Distribution list

            - The Director (Commercial), Gridco, Bhubaneswar

            - The Director (Operation), OHPC, Bhubaneswar

            - The CGM (O & M), OPTCL, Bhubaneswar

            - The CGM (Const.), OPTCL, Bhubaneswar

            - The CGM, (RT&C), OPTCL, Bhubaneswar

            - The C.G.M (PP), GRIDCO, Bhubaneswar

            - The CGM (IT), OPTCL, Bhubaneswar

            - The Sr. G.M (C.P), OPTCL, Bhubaneswar

            - The Sr. G.M (TP&C), OPTCL, Bhubaneswar

            - The Sr. G.M. (CPC), OPTCL, Bhubaneswar

            - The Sr. G.M.(O&M), Zone-I, Narendrapur

            - The Sr. G.M.(O&M), Zone-II, Meramundali

            - The Member Secy., (GCC), OPTCL, Bhubaneswar

            - The C.E.O., CESU, Bhubaneswar

            - The M.D.,WESCO, Burla

            - The M.D., NESCO, Balasore

            - The MD., SOUTHCO, Berhampur

            - The G.M. (Telecom), OPTCL, Bhubaneswar

            - The Vice President (O), IMFA, Choudwar

            - The D.G.M (Electrical), IbTPS, OPGC, Banharpali

            - The G.M. (O &M), CPP, NALCO, Angul

            - The DGM (O & M), NTPC (TTPS), Talcher

            - The G.M, HINDALCO, Hirakud

            - The D.G.M (Power Distribution), RSP, Rourkela

            - The D.G.M. (Elect.), JINDAL Stainless Ltd, Duburi

            - The G.M, Vedanta Aluminium Ltd., Jharsuguda

            - The G.M.(Elect.), Bhushan Steel & Power Ltd, Budhipadar

            - The Sr. G.M. (Elect.), Bhusan Steel Limited, Meramundali

            - The S.E, Machhakund

## Odisha Power Transmission Corporation Ltd. Bhubaneswar.

Minutes of 83rd PSOC meeting held on 24.02.2015 at PTC, Chandaka

List of participants is at Annexure.

Sr. G.M (Power System) welcomed all the participants to the 83rd Power System Operational Coordination meeting and highlighted the system performance during the month of January’2015 and overall power scenario of the State. He also emphasized on the drawal by all the Discoms during the month.

The meeting was chaired by Director (Commercial), GRIDCO.

D.G.M. (SS) took the agenda items for discussion.

The review proceeded as follows:

PART A: CONFIRMATION OF MINUTES

A.1: Confirmation of minutes of 82nd PSOC meeting held on 20.01.2015

The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2014/423(30), dated 16.02.2015 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting

Minutes of 82nd PSOC meeting was confirmed since no comments were received.

PART B : SYSTEM PERFORMANCE

B1: Review of Grid Performance for the month of January’2015.

## (A)  Frequency

It was noticed that, during the month, 51.40% of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 47.90 % during the month of December’14. The maximum and minimum System frequency during the month of January’15 was 50.56 Hz & 49.56 Hz respectively.

## (B)  Grid demand

Grid demand for the month of January’15 was reviewed. The energy consumption during the month was 1919 MU. The maximum System demand of 3464 MW occurred on 23.01.2015 at 20:00 Hrs and minimum demand of 1787 MW occurred on 02.01.2015 at 03:00 Hrs.

Deliberation in the meeting

It is observed that energy consumption during the month of January’ 15 was decreased by 18 MU, while the peak demand during the month has decreased by 51 MW from that of December’14. The energy consumption during the month has been decreased by 90 MU in comparison to December’13. The energy consumption was decreased due to shutdown of transmission elements for annual maintenance.

(C)  Voltage Profile of important Sub Stations in OPTCL System.

The Voltage profile at different 220 kV buses in OPTCL system during the month of January’15 was reviewed. It is noticed that Bidanasi and Jayanagar 220 kV buses have experienced a maximum voltage of 253.62 kV and 251.20 kV respectively, while minimum Voltage of 198.83 kV was experienced at Meramundali 220 kV bus.

Deliberation in the meeting

Sr. G.M (PS) stated that issue of persisting high voltage at Jayanagar has been raised in the OCC meeting of ERPC. CMD, OPTCL has also written a letter to ED, POSOCO in this issue. Over Voltage at Bidanasi, and low Voltages at Meramundali need to be investigated by checking the CVTs of these S/Ss. CGM (O&M) stated that replacement of CVT at Bidanasi is scheduled to be done by 28th February’15.

[Action: CGM (O&M)]

(D) Energy Generation / import during the month of January’15

Energy generation and exchange during the month of January’15 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 1919.21 MU.

(E) Drawal of Machhakund Power

The drawal of Machhakund power during the month of Januaty’15 was 29.081 MU against AP drawal of 29.899 MU

In the last meeting it was decided to expedite the bus modification work at Jayanagar S/S and to establish direct communication between Machhakund and SLDC through PLCC and modification of 33 kV network by Southco for enhancing Machhakund drawal.

Deliberation in the meeting

SLDC stated that Jaynagar sub-station is not responding to SLDC’s direction for diversion of Akhusingh & Mohana load to Machhakund system especially during off peak hours as a result of which the State is unable to optimize the drawal from Machhakund. Necessary instruction need to be issued to Jayanagar S/S by Sr. G.M (O&M), Zone-I. Sr. GM (O&M), Zone-I stated that bus modification work at Jayanagar S/S is will be taken up after commissioning of Auto at Jayanagar. G.M (Telecom) stated that installation of OPGW equipments at Machhakund and Jayanagar by POWERGRID is expected to be completed by June 2015. After which, Remote Subscriber (RS) phone provision can be made from Jayanagar S/S. Southco stated that around 1.5 MW load has been extended to Akusingh Grid by linking 33/11kv Substation Kumbhar Dhamuni.  Other linking lines as suitable are being taken up.

[Action:-G.M (Telecom) / Sr.GM (O&M)-I / SOUTHCO]

- Under Frequency Relay operation in OPTCL System during the month of January’15.

There is no UF Relay operation occurred during the month of Januay’15 as the frequency had never gone beyond 48.5 Hz.

(G) DISCOM Drawal during the month of January’15

The schedule and actual energy drawal by Discoms for the month of January’15 was reviewed.

Deliberation in the meeting

It was noticed that CESU and WESCO have overdrawn substantially to the tune of 55.7 MU and 32.97 MU respectively, while SOUTHCO have overdrawn 6.15 MU during the month. NESCO has almost maintained their drawal in accordance with the schedule. CESU stated that the drawal data displayed at SLDC is not correct, which leads wrong prediction of day-ahead drawal.  It was decided that SLDC shall monitor the overdraw of DISCOMs and do the needful for compliance of the drawal schedule. The data displayed shall be checked by the Discom representatives and Telecom officers at SLDC.

[Action: All Discoms, SLDC, Telecom]

PART C – issues of 106th OCC meeting of ERPC

C1: Performance of UFR.

It was decided in the 105th OCC meeting of ERPC that constituents should check the UFR enunciation & PT fuse and thereby certify on monthly basis that UFRs are in service.

Further, it was decided to monitor the quantum of load connected to the UFR and constituents are to submit, on quarterly basis, maximum and average load quantum of each feeder with UFRs connected.

Deliberations in the meeting.

Sr. G.M (PS) stated that CGM (O&M) may instruct the Grid S/Ss where UFR has been installed to check and certify the operations and connected load to the UF Relay on monthly basis. G.M (O&M) stated that all the S/Ss have been instructed to certify the operation of UF Relays and connected load in each month.

C2: DR, EL, PLCC and Reactor status installed in Eastern Region.

Member Secretary ERPC intimated that updated status of DR & EL and PLCC are available in ERPC website & requested to check the list & intimate by 26.02.2015 in case of modification / correction.

In the last meeting, CGM (O&M) stated that Event Loggers have already installed. After arrival of Service engineer of M/s Alstom, these ELs shall be commissioned.

Deliberations in the meeting.

G.M (Telecom) stated that the status of PLCC has already been intimated to ERPC. CGM (O&M) stated that commissioning of EL at Bidanasi has been done. Commissioning of EL at 11 Nos. of S/Ss shall be completed by March 2015. Data from 400 kV Mendhasal and Meramundali S/Ss can be retrieved from the numerical relays. OHPC stated that EL at Indravati PH is functioning and need to be synchronized with GPS. It was decided that OHPC may take action for installation of EL at their Balimela, Rengali and Upper Kolab PHs.

C3: Augmentation of 3rd ICT at 400kV Jeypore s/s.

It was deliberated by SLDC, OPTCL that augmentation of Jeypore sub-station capacity is not required at this juncture.

Members may note.

C4: Status of 80MVAR Line reactor of 400kV Meramundali-Angul at Meramundali

In the last OCC meeting it was deliberated that OPTCL has completed all works. Powergrid may commission the relay.

Deliberations in the meeting.

C.G.M (O&M) stated that the reactor has been charged after commissioning of the Relay by OPTCL, since POWERGRID did not turn up for commissioning of the relay.

C5: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG) S/s

400/220 kV, 2X 315 MVA S/S at Bolangir has been established by Powergrid as part of  ISTS system & the following 220 kV interconnecting lines was envisaged to be established by OPTCL:

CGM (Construction) stated that 220 kV Bolangir-Bolangir (PG) line, which is a part of 220 kV Bolangir–Kesinga D/C line with one ckt LILO at Bolangir(PG) may be delayed due to land dispute issue raised by IDCO. The schedule of commissioning of the line is as follows:

- LILO of OPTCL’s Burla-Bolangir line (One ckt) at Bolangir (PG): March 2015

- 220 kV Bolangir –Kesinga D/C line with one ckt LILO at Bolangir(PG): March’15

Deliberations in the meeting.

C.G.M (O&M) stated that the status of item (i) remains same. Construction representative stated that status of item (ii) is uncertain due to allotted IDCO land dispute issue by a party.

C6: Status of “Third Party Protection Audit”

It was deliberated in the OCC that work order has been placed to CPRI, Bangalore for conducting protection audit at Meramundali, Budhipadar, Theruvali & Jaynagar sub-stations.

It was deliberated in the 105th OCC meeting of ERPC that the checklist for carrying out 2nd Third Party Protection Audit is available in ERPC website. Constituents were advised to send their views for modifications required, if any, positively by mid-week of February, 15. It was decided that on the updated checklist the 2nd third party protection audit for eastern region will be tentatively started from April, 2015 as per road map to be finalized in 106th /107th OCC meeting.

Deliberations in the meeting.

G.M (O&M) stated that the list as mentioned is not available in ERPC site. OPTCL shall take action only after seeing the list of S/Ss.

C7: High voltage problem at 400kV Jeypore-OPTCL Substation—OPTCL

In the last meeting it was decided that OHPC shall conduct harmonic study in coordination with OPTCL. Gridco shall send a proposal to CEA Standing Committee for elimination of back to back DC. OPTCL shall examine for filing Petition before the CERC for not maintaining the bus Voltage at Jeypore (PG) by POWERGRID, as per CEA standard.

In the 105th OCC meeting of ERPC, Powergrid-Odisha projects informed that, earlier it was envisaged to replace the 63 MVAR bus reactor with a 125 MVAR reactor at 400kV Jeypore S/s. Now it has been revised to keep both (63 MVAR & 125 MVAR) bus reactors. Total scheme including space, foundation and switching equipment is getting revised. The expected date of commissioning of new 125 MVAR reactor is May, 2015.

OCC of ERPC opined that high voltage will be regulated as and when 125 MVAR reactor at Jeypore S/s is commissioned.

Further, CMD, OPTCL has expressed concern for persistence high voltage at Jaynagar, Meramandali & Mendhasal buses, which is the impact of over voltage in CTU system and requested CEO, POSOCO & ED, NLDC to expedite installation of 125MVAr reactor at Jeypore PG sub-station.

The reactive power injection by M/s JSPL & M/s BSL at Meramundali bus may also be a reason for high voltage which is to be monitored by SLDC on real time basis.

Deliberations in the meeting.

It was decided that SLDC shall monitor the VAr injection by M/s JSPL and M/s BSL on real time basis. OHPC stated that tender has already been floated for PQA required for harmonic study at Upper Kolab PH.

[Action: SLDC / OHPC]

C8: Pollution mapping for Eastern Region

In the last meeting CGM (O&M) stated that OPTCL shall provide insulators to Southco and WESCO for hanging at the locations of their respective control area. The Discoms may expedite the work and report to OPTCL.

In the 105th OCC meeting of ERPC, Powergrid informed that the Instrument Kits for measurement related to Pollution Mapping were already dispatched to the constituents.

Deliberations in the meeting.

CGM (O&M) stated that major numbers of locations belongs to SOUTHCO. SOUTHCO is not taking initiative for hanging of insulators, even after OPTCL agreed to provide insulators. SOUTHCO may expedite the matter and complete all locations before next PSOC meeting.

[Action: SOUTHCO]

C9: Certification through BIS as per IS 18001:2007 to all generating/transmission units.

In the last meeting CGM (O&M) stated that BIS has not responded yet. However, BIS will be reminded again.

Deliberations in the meeting.

CGM (O&M) was requested to remind BIS again.

[Action: CGM (O&M)]

C10: Mock Black start exercises in Eastern Region–ERLDC

The mock black start exercise for Upper Indravati HEP was carried out on 10th February 2015.

Deliberations in the meeting.

SLDC stated that mock black start exercise for Rengali PH shall be taken up during the month of March’15

[Action: OHPC/SLDC]

PART-D – Operational Issues

D1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of January’15 was reviewed. Maximum 27 numbers of such messages were issued to CESU followed by 5 Nos. to WESCO, 2 Nos to NESCO and 1 No. to SOUTHCO.

Deliberations in the meeting.

SLDC stated that CESU and WESCO were not responded SLDC instruction regarding compliance of drawal scheduled, resulting substantial quantum of over drawal during the month. It was decided that SLDC shall take necessary action to make the Discoms to comply their respective drawal schedule.

[ Action : SLDC / DISCOMS]

D2: Availability of data of real time power flow of feeders covered under Under-frequency Load shedding scheme (UFLS) and lower relief expected to obtained in real time system operation

In the last meeting G.M. (Telecom) stated that purchase order has already been placed with M/s Industrial Control and Drives. Work shall be started soon after receipt of MFM and associated accessories.

Deliberations in the meeting.

GM (Telcom.) stated that the performance BG submitted by the Firm “M/s Industrial Control” was not in line with OPTCL requirement. The firm has been asked to comply with.

[Action: GM (Telecom)]

D3: Reporting of Sequence of Events (SoE)

In the last meeting G.M (Telecom) stated that Relays (CMR) have already been installed for interfacing status of tie-breaker with the RTU for display in SCADA system, but field inputs are not available presently at the control panel of Meramundali. No action has been taken by E&MR at Meramundali. In the 18th SCADA O&M meeting ERLDC stated that most of the SoE are wrong & OPTCL assured to rectify the same by 15th February’ 15.

Deliberations in the meeting.

GM (Telcom) stated that E&MR wing have installed separate TB for CMR. Telecom shall install CMR by 2nd week of March’15. SLDC stated that the garbage data need to be blocked.

[Action: GM (Telecom)]

D4: Repeated damage of Lightning Arrester at Meramundali Sub-station.

It is observed that LA installed at Meramundali sub-station are being damaged frequently causing tripping of important transmission elements which needs to be investigated.

Deliberations in the meeting.

GM (O&M) stated that due to persistence high Voltage, the L.As at Meramundali are getting stressed. The magnitude of 3rd harmonic at Meramundali and Mendhasal are ok. The old LAs need to be replaced.

[Action: CGM (O&M)]

D5: Reporting of major incidents.

It is noticed that Grid S/Ss and Generating stations are not reporting the details of tripping and Relay indication soon after occurrence of a major disturbance. Rather, they are reporting after a lot of persuasions by SLDC and after considerable lapses of time. Further the main relay indications are not being mentioned in most of the tripping.  It is also noticed that sometimes fabricated reports are being received from generating stations as well as grid S/Ss. In absence of Disturbance Recorder (DR) in major grid S/Ss, the incidents cannot be analyzed correctly. This leads to put SLDC and O&M in an embarrassing condition in the PCC sub-committee meeting of ERPC as well as giving a scope to ERLDC to raise the issue before the CERC. Even though this issue was raised earlier in the house, the quality of reporting is yet to be improved.

Deliberations in the meeting.

GM (O&M) stated that Electromagnetic Relays at Narendrapur and Bhanjanagar S/Ss and need to be replaced. E&MR wing of respective circles are requested to create awareness between the Shift Engineers for study the relay indications for proper reporting.

[Action: CGM (O&M)]

D6: Prolonged outage of transmission elements and tentative revival dates

| Sl. No | Name of transmission element | Reason of outage | Probable date of revival |
| --- | --- | --- | --- |
| 1 | 220 kV Jayanagar-Theruvali ckt-III Breaker | Breaker defunct. | Breaker received. March 2015 |
| 2 | 220/132 kV, 100 MVA Auto-II at Duburi | After inspection by repairer, date can be ascertained | Can be ascertained after inspection. |
| 3 | 220/132 kV, 100 MVA Auto-II at Joda | -do- | -do- |
| 4 | 220/132 kV, 100 MVA Auto-I at Jaynagar | Replacement of 100 MVA Auto by 160 MVA under progress. | Charged on 20.02.2015 |
| 5 | 220/132 kV, 100 MVA Auto at Bolangir (new) | Replacement of 100 MVA Auto by 160 MVA under progress. | 5th March 2015 |

[Action : CGM (O&M)]

D7: Communication issues

- Installation of communication equipment by CGPs / Industries.

The status of data communication from CGPs as deliberated in the last meeting is as follows

| Sl. No | Name of CGP | Present status |
| --- | --- | --- |
| 1 | M/s Sri Ganesh Metalicks Ltd. | PLCC / SCADA not established. M/S Sri Ganesh proposed for communication through wireless communication mode. They have been permitted for testing. No progress thereafter. |
| 2 | M/s IFFCO, Paradeep | Work has been awarded to M/s Bharat Kumar Sahoo. Outdoor commissioning work is expected to be completed by a week time. Requisition for line shutdown has made for 24th & 25th February’15 for the purpose. |
| 3 | M/s MSP Mettalicks | PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited. |
| 4 | M/s NINL, Duburi | M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. |
| 5 | M/s Adhunik Metallics | PLCC & RTU installed. Database has prepared by OPTCL. Commissioning of RTU is yet to be done. |
| 6 | M/s Rohit Ferrotech | PLCC established and inspection by Telecom Engineers completed. Data base has already been prepared by OPTCL. |
| 7 | M/s VAL, Jharsuguda | No isolator status is available. MW/ MVAR not available for Sterlite 1/2 line, station transformer / Smelter. CBs of Bus coupler data, Bus-1 kV/Hz are not available. As per MOM between OPTCL & Sesa Sterlite, Jharsuguda dtd 22.09.2014, provision for telemetry data will be extended within 6 months.(March,2015) |

All the CGPs have agreed to establish data communication system by March 2015 in the meeting held on 27th November 2014.

[Action : G.M (Telecom)]

- Availability of Tap position of 400kV ICTs at Mendhasal.

Tap position data for Mendhasal ICTs are not available for display through SCADA. ERLDC raised this issue in 105th OCC meeting of ERPC.

In the last meeting, G.M (Telecom) stated that, they have prepared a modified ckt for input to transducer “TPC-2001” for acquiring / display of OLTC status and successfully tested. The PCB has been designed and ordered placed. The PCB is expected to be received within 15 days.

Deliberations in the meeting.

GM (Telecom) stated that PCB for ICT –II has already been installed and working. PCB for ICT-I will be installed after availing of line shutdown.

[Action : G.M (Telecom)]

D8: DISCOM Issues

SOUTHCO:

- The dashboard of DSOCC is displaying only for few minutes at a time and going to Server error for long time in all over the day.

- Due to non availability of correct dashboard data, the day-ahead requirement cannot be presumed in realistic value, owing to that the ABT operation should be discontinued during the time of non availability / availability of wrong data.

- The energy drawl reading of 132 kV traction end meter should be considered for all commercial purposes and billing.

- Machakund power of around 1.5 MW has been extended from Akusingi Grid to 33/11kv Substation Kumbhar Dhamuni by linking 33kv feeders of Southco and other linking lines as suitable are being taken up.

- Replacement of failed power transformer at Jayanagar Grid S/S.

- Normalizing and feeding power from Ganjam Grid substation with 3 nos of 33 kV  bays for feeding power to Southco area as the area load has been drawn from Chhatrapur grid which creates interruption of more times due to long distance .

Deliberations in the meeting.

- IT representative stated that the technology adopted by M/s Addsoft for displaying Dashboard data is found to be erroneous. IT has developed one internal application for display of Dashboard data, which was programmed to be demonstrated after the meeting.

- Gridco stated that Southco may take action for installation of appropriate class of accuracy CT / PT and meters, so that the billing at traction points can be examined.

- Jayanagar transformer has already replaced.

- Ganjam Grid S/S is expected to be made functional by December 2015.

[Action: SOUTHCO / CGM (O&M)/ IT]

WESCO:

- The Solar units import is yet to be deducted from WESCO’s bills.

- The block wise statement as provided in SLDC site may be provided in EXCEL format instead of PDF format. For safety reason the data may be provided both in PDF and EXCEL format.

- For last four months hardly for 10 days full 96 block data is available on ABT DASHBOARD.

- The past adjustment of export to Pallahara (export to CESU) is to be made from WESCO's bill up to November-2014.

- There is always a mismatch between the drawl data shown in ABT DASHBOARD at WESCO and the drawl shown at SLDC DASHBOARD

Deliberations in the meeting.

- Gridco shall  convene a meeting with all Discoms for resolving solar plant import issue.

- Erroneous display of dash board data has already deliberated at Southco deliberation.

- Adjustment of Pallahara drawal is under process.

[Action: GRIDCO/All Discoms/ IT]

CESU:

- Commissioning of Satasankha, Athagarh, New Gondia 132/33kVsub-stations and Atri & Samaghara 220/132/33kV Sub-stations.

- Up-gradation of conductor size to cater Khurda load from Bidanasi

- Provision of additional 33kV feeder bay at Nadia Gurudi & Rengali grid

- Up-gradation of Hind Metaliks, Rengali, Chainpal, Kalarangi & Boinda grid sub-stations.

- Metering issues at Barkote grid sub-station.

- Replacement of 33kV CTS at Chandaka, Ransinghpur & Mancheswar grid sub-station.

- Additional bay Chandaka, Ransinghpur, Mancheswar, Cuttack, Bidanasi, RAWMET, AARTI, Meramundali & Paradeep grid sub-station.

Deliberations in the meeting.

CESU may discuss the issues with OPTCL separately as already decided in the last meeting.

[Action: CESU]

NESCO:

- Display of Dashboard data of NESCO as proposed format submitted in the 79th PSOC meeting.

- Long time server error problem to be sorted out.

- Anandapur Grid needs up-gradation from 2x12.5 MVA to 2x20 MVA.

- Up-gradation of Barbil Grid 2x12.5 MVA to 2x20 MVA.

- Power supply to Chandikhol Grid may be fed from Duburi Grid instead of Paradeep which is causing low voltage.

Deliberations in the meeting.

- Dashboard problem has already been deliberated at above.

- NESCO may take action for diversion of some of the area loads from Barbil feeder to Joda S/S and Anandpur to Jajpur S/S to relieve over loading of Barbil and Anandpur S/Ss.

[ Action: NESCO / IT]

PART E: OPERATIONAL PLANNING

E1:  Commissioning status of New Transmission elements.

As deliberated in the meeting the status of commissioning of new transmission elements is as follows:

| Sl. No | Details of transmission element | Present Status |
| --- | --- | --- |
| 1 | Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line | Work has already been started. Expected to be completed by June 2015. |
| 2 | Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt | Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal for which work order / PO issued. (October-2015) |
| 3 | Commissioning of 400 kV Ib-Meramundali D/C line. | 400kV SSEL-Meramundali line has been idle charged from SSEL end. Due to theft of conductor line could not be charged. Expected to be charged by end of March’2015. |
| 4 | Commissioning of 400 kV Duburi-Meramundali D/C line. | Work is in progress after disposal of Case. Expected by the end of March 2015. |
| 5 | Commissioning of 220 kV Bidanasi-Cuttack line | Work in progress and expected to be completed by June 2015. |
| 6 | Commissioning of 220/132 kV Cuttack S/S | Work in progress and expected to be completed by June 2015. |
| 7 | Commissioning of 132 kV Baripada (PG)-Jaleswar line | Work has already been started, which will be completed by December 2015. |
| 8 | Commissioning of 220/132 kV Kesinga S/S | Work under progress. Expected by September 2015. |
| 9 | Connectivity to Keonjhar PG | Proposal is mooted to be placed in the BoD meeting for connecting the proposed 220 / 33 kV Keonjhar S/S and with Turumunga S/S through 2 Nos. 220 kV ckts each.. |
| 10 | LILO of 220 kV Burla - Bolangir line (one ckt) at Bolangir(PG) | Work awarded. Expected to be completed by March, 2015 |
| 11 | 220 kV Bolangir –Kesinga D/C line and LILO of one ckt at Bolangir(PG). | 220kV Bolangir – Kesinga D/C line is under construction. It is proposed to connect Bolangir (PG) through LILO arrangement of one ckt. (may be delayed due to land dispute with IDCO) |

[Action: CGM (Construction)]

Status of Discom’s action plan for power drawal from the S/Ss expected to be commissioned in near future.

| Sl. No | Name of the sub-station | Probable month of commissioning | Name of DISCOM | Action taken by Discoms |
| --- | --- | --- | --- | --- |
| 1 | 132/33kV, 2x20 MVA Banki | January’15 | CESU | 33 kV feeder work completed. |
| 2 | 132/33kV, 2x20 MVA Konark | Mar’15 | CESU | Line existing |
| 3 | 132/33kV, 2x20 MVA Samuka beach | Mar’15 | CESU | L&T has taken up |
| 4 | 132/33kV, 2x20 MVA Khajuriakota | June’15 | CESU |  |
| 5 | 132/33kV, 2x40 MVA Sarasmal | March’15 | WESCO |  |
| 6 | 132/33kV, 2x40 MVA Kalunga | March’15 | WESCO |  |
| 7 | 220/33kV, 2x20 MVA Banei | Dec’15 | WESCO |  |
| 8 | 132/33kV, 2x20 MVA Boud | January’15 | SOUTHCO | 33 kV Boudh feeder completed. Purunapatna feeder under progress |
| 9 | 132/33kV, 2x12.5 MVA Dabugaon | March’15 | SOUTHCO | 33 kV Dabugaon and Papadahandi feeder completed |
| 10 | 132/33kV, 2x12.5 MVA Umerkote | Mar’15 | SOUTHCO | Requisition for funds placed |
| 11 | 132/33kV, 2x20 MVA Nawapara | January’15 | WESCO | 33 kV feeder work completed. |
| 12 | 132/33kV, 2x20 MVA Padmapur | June’15 | WESCO |  |
| 13 | 132/33kV, 2x20 MVA Udala | Dec-15 | NESCO | Line existing |
| 14 | 132/33kV, 2x20 MVA Somanathpur | March’15 | NESCO |  |

As decided in the last meeting, CESU stated that action is being taken for construction of 33/0.4 kV S/S at Mendhasal to avail power supply for Mendhasal area.

[Action: All Discoms]

E2: Installation of Energy Metering at Hydro / Traction & Solar projects.

In the last meeting it was deliberated that installation of meters at all hydro stations except Indravati HEP and traction S/Ss except Bamara, Bhalulata and Chandiposi traction S/Ss have been completed. OHPC was agreed to provide the required assistance to M/s Secure Meters for installation of meters at Indravati PH. Discoms are requested to ask railway authority for change of CT / PT and identify the space for meter installation.

Deliberations in the meeting

OHPC stated that ABT compliance energy meters have installed at all OHPC stations except Indravati and was agreed to provide the required assistance to M/s Secure Meters for installation of meters at Indravati PH. At present billing is done from the Apex meter installed at Balimela PH only. Discoms are requested to ask railway authority for change of CT / PT and identify the space for meter installation. It was decided that, from 1st March OPTCL shall take meter reading from those meters. Installation of meters at Indravati shall be completed prior to 1st March.

[Action: OHPC / OPTCL /WESCO]

E3: Metering issue of TTPS.

In the last meeting Director (Commercial) stated that a CGM (PP) had visited TTPS to discuss the issue. The matter shall be resolved soon.

Deliberations in the meeting.

Director (Commercial) stated that 1st round discussion has been done. The issue will be sorted out soon.

[Action GRIDCO / TTPS]

E4: Construction of 220 kV Tarkera-RSP 2nd DC line.

In the last meeting, CGM (Const.) stated that a decision can be taken only after conducting system study.

Deliberations in the meeting.

CGM (O&M) stated that a system study is required for construction of 220 kV 2nd DC line for providing additional quantum of power to RSP. CGM (Construction) shall write a letter to CGM (O&M) for system study.

[Action; CGM (O&M) / CGM (Const.)]

E5: Shifting of 33 kV line from Balasore Grid S/S yard to facilitate separation of Tfr and Balasore Alloy bays.

In the last meeting, CGM (O&M) stated that since the work is urgent in nature, NESCO should take it very seriously and complete the shifting early. All Discoms are requested for shifting of 33 kV feeders if any from the Switchyard area of Grid S/Ss within three months.

Deliberations in the meeting.

NESCO stated that estimate for shifting of 33 kV line from Balasore Switchyard is under process. CGM (O&M) stated that NESCO has to expedite the work, as it is very much delayed.

[Action: NESCO]

E6: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

It was deliberated in the last meeting, CGM (IT) stated that the data received through AMR is not the real time data, as such cannot be used for monitoring. However, these data can be utilized for day-ahead demand estimation purpose. The real time drawal by DISCOMS shall be made available from SCADA as per the format finalized to the DISCOMs.

Deliberations in the meeting.

IT representative stated that a demo will be presented to all Discoms after the meeting regarding display of Dash board data.

[Action : IT / All Discoms]

E7: Major Events in the month of January’15

The following sub-stations have been energized:

- 132/33kV, 2 X 20 MVA Boudh Sub-station with one tfr. Charged on 28.01.2015.

- 132/33kV, 2 X 20 MVA Banki Sub-station with one tfr. Charged on 29.01.2015.

Members may note

E8: Important Grid Incidences during the month of January’15.

Important incidents occurred during the month of January’15 were reviewed.

Deliberations in the meeting

SLDC stated that grid S/Ss are not furnishing the reports after occurring of disturbances. Rather, they are submitting reports after lapses of 1 or 2 days. Due to non-receipt of report from the field, SLDC is not able to furnish final report to ERLDC within the scheduled time. CGM (O&M) may instruct all the GMs in charge of EHT (O&M) to monitor the reporting issue.

[Action: C.G.M. (O&M) ]

E9: Outage of major transmission Elements during the month of January’15. (above 10 hrs).

Outage of major transmission elements above 10 hours during the month of January’15 was reviewed.

Deliberations in the meeting

There are only three outages due to conductor snapping, jumper snapping ant tower collapse.

[Action: C.G.M. (O&M) ]

E10: Review of Outage Program of State Generators / Transmission elements for the month of February & March’15:

Tentative Outage programme for State Generators for the month of Feb & Mar’15 are as follows:

| Sl. | Station | Unit | Period | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Burla | # 1 # 6 # 7 | 01.04.15 to 30.07.15 17.02.14 to continue 25.02.15 to 13.03.15 | Capital Maintenance Programming for R, M & U Annual Maintenance |
| 2 | Chiplima | #3 | 15.02.14 to continue | Programming for R & M |
| 3 | Balimela | # 1 # 5 | 31.01.13 to continue 10.02.15 to 09.03.15 | Programming for R, M & U Annual Maintenance |
| 4 | Rengali | # 1 # 2 | 15.03.15 to 31.03.15 15.03.15 to 31.03.15 | Governor Rectification Governor Rectification |
| 5 | Upper Kolab | # 1 | 01.04.15 to 28.09.15 | Capital Maintenance |
| 6 | Upper Indravati | # 1 # 2 | 28.03.15 to 22.04.15 24.04.15 to 18.05.15 | Annual Maintenance Annual Maintenance |

OHPC stated that during March and April 2015 Burla generation may be enhanced to utilize the water as power channel maintenance work shall be taken up from the month of May onwards.

E11: Generation Program for the month of March’15.

Generation schedule for the month of March’15 furnished by OHPC are given below.

| Name of Hydro Gen. Station | Generation Programme (MW) | Reservoir Level as on 01.02.14 | Reservoir Level as on 01.02.15 | MDDL | High Flood Reservoir Level |
| --- | --- | --- | --- | --- | --- |
|  | March’15 |  |  |  |  |
| HPS, Burla | 40+30 | 625.67ft | 622.47ft | 590 ft. | 630 ft. |
| Balimela | 80 | 1505.90ft ft | 1505.40ft | 1440 ft. | 1516 ft. |
| Rengali | 40 | 122.17mt 1.78mt mtr mt | 120.70mt mt | 109.72mtr mtr mtr. | 123.5 mtr. |
| U.Kolab | 80 | 855.13mt mt | 855.79mt | 844 mtr mtmtr. | 858 mtr. |
| U.Indravati | 300 | 641.30mt mt | 639.09mt mt | 625mtr mtr mtr. | 642 mtr |
| MKD (O/D) | 30 | 2743.50ft ft | 2740.20ft ft | 2685 ft. | 2750 ft. |
| TOTAL | 600 |  |  |  |  |

##### E12: Issues raised by Ib TPS

##### Bus-bar protection at Budhipadar sub-station.

##### Islanding scheme of IbTPS

Deliberations in the meeting.

CGM (O&M) stated that the busbar panel installed at Budhipadar S/S could not be commissioned due to defects noticed in the relays. The panel can be commissioned after replacement of the defective Relay by M/S SIEMENS.

##### Action is being taken as per the discussion in the meeting for functioning of islanding scheme.

PART F: OTHER ISSUES

F1.  Date and Venue of the next (84th) PSOC meeting:

The date and venue of 84th PSOC meeting shall be intimated to all the Members.

ANNEXURE