Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

# Agenda

for

90th Power System Operational Coordination Meeting

## Date: 17.10.2015

### Venue: PTC, Chandaka

Odisha Power Transmission Corporation Ltd. Bhubaneswar.

Agenda for 90th PSOC Meeting to be held on 17.10.2015 at PTC, Chandaka

A1: Confirmation of the minutes of the 89th PSOC Meeting held on 29.08.2015

The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2015/3440(30), dated 10.09.2015 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART B: GRID PERFORMANCE

Review of Grid Performance for the month of August’15 & September’15.

- Frequency:

Hourly frequency variation for the month of August’15 & September’15.

| Month | % of time frequency remained |
| --- | --- |
|  | <49.00 | 49.00-49.70 | 49.70-49.90 | 49.90-50.05 | >50.05 |
| July’15 | 0.00 | 0.09 | 8.22 | 66.01 | 25.69 |
| Aug’15 | 0.00 | 0.14 | 11.04 | 66.58 | 22.23 |
| Sept’15 | 0.00 | 0.38 | 24.55 | 61.04 | 14.03 |

Maximum & Minimum frequency during the month of August’15 & September’15.

| Month | Freq (Hz) | Date | Time |
| --- | --- | --- | --- |
| July’15 | Maximum – 50.23 | 26.07.15 | 06:00 Hrs |
|  | Minimum – 49.65 | 13.07.15 | 14:30 Hrs |
| August’15 | Maximum – 50.19 | 23.08.15 | 17:00 Hrs |
|  | Minimum – 49.60 | 03.08.15 | 19:15 Hrs |
| September’15 | Maximum – 50.35 | 20.09.15 | 16:03 Hrs |
|  | Minimum – 49.54 | 03.09.15 | 19:12 Hrs |

- Grid Demand for the month of August’15 & September’15.

| Month | Demand | Maximum Consumption | Maximum Demand | Minimum Demand |
| --- | --- | --- | --- | --- |
|  | MU | Avg. (MW) | MU | Date | MW | Date | Time | MW | Date | Time |
| July’15 | 2337 | 3141 | 79.59 | 05.06.15 | 3994 | 04.07.15 | 21:00 | 2431 | 25.07.15 | 16:00 |
| Aug’15 | 2422 | 3256 | 82.25 | 09.08.15 | 3992 | 06.08.15 | 20:00 | 2558 | 14.08.15 | 15:00 |
| Aug’14* | 2162 | 2906 | 73.47 | 25.08.14 | 3551 | 29.08.14 | 21:00 | 2146 | 05.08.14 | 03:00 |
| Sept’15 | 2258 | 3137 | 79.52 | 04.09.15 | 3849 | 09.09.15 | 22:00 | 2388 | 20.09.15 | 14:00 |
| Sept’14 | 2179 | 3026 | 76.10 | 26.09.14 | 3720 | 26.09.14 | 21:00 | 2395 | 06.09.14 | 04:00 |

Members may please discuss.

- Voltage Profile of 220 kV Buses in OPTCL system for the month of:

- August’15

| Sl. No | S/s Name | Maximum | Minimum |
| --- | --- | --- | --- |
|  |  | kV | Day | Time | kV | Day | Time |
| 1 | Jayanagar | 244.27 | 19 | 13:30 | 222.33 | 21 | 7:30 |
| 2 | Theruvali | 239.77 | 27 | 13:45 | 212.57 | 21 | 8:45 |
| 3 | Bhanjanagar | 233.24 | 01 | 01:15 | 218.58 | 20 | 19:15 |
| 4 | Chandaka | 230.88 | 19 | 16:15 | 209.34 | 14 | 19:30 |
| 5 | Narendrapur | 223.66 | 27 | 13:30 | 183.36 | 20 | 20:45 |
| 6 | Joda | 239.24 | 1 | 05:45 | 222.70 | 22 | 10:30 |
| 7 | Tarkera | 237.98 | 30 | 07:00 | 213.56 | 06 | 17:30 |
| 8 | Bhadrak | 234.22 | 18 | 07:45 | 195.31 | 20 | 19:45 |
| 9 | Paradeep | 227.76 | 01 | 15:00 | 195.25 | 14 | 19:00 |
| 10 | Budhipadar | 232.03 | 28 | 14:00 | 222.79 | 01 | 20:15 |
| 11 | Duburi(O) | 233.07 | 01 | 05:00 | 211.42 | 14 | 19:00 |
| 12 | Duburi (N) | 225.68 | 19 | 11:15 | 203.91 | 14 | 19:15 |
| 13 | Balasore | 231.51 | 01 | 06:30 | 201.78 | 26 | 20:15 |
| 14 | Meramundali | 227.41 | 01 | 06:45 | 215.92 | 14 | 21:00 |
| 15 | Bidanasi | 229.84 | 19 | 16:30 | 213.44 | 27 | 18:45 |
| 16 | Katapalli | 231.68 | 12 | 13:45 | 214.94 | 01 | 20:30 |
| 17 | Nayagarh | 230.41 | 19 | 16:15 | 212.98 | 14 | 19:45 |
| 18 | Mendhasal | 230.99 | 08 | 07:30 | 210.21 | 14 | 19:45 |
| 19 | Bolangir | 234.22 | 12 | 13:15 | 201.95 | 01 | 20:15 |
| 20 | Barkote | 234.97 | 03 | 05:45 | 224.76 | 25 | 16:45 |
| 21 | Laxmipur | 241.33 | 27 | 13:45 | 218.87 | 21 | 08:45 |

The maximum voltage of 244.27 kV occurred at Jaynagar 220 kV bus while Narendrapur, Bhadrak and Paradeep 220 kV bus have experienced the minimum Voltage of 183.36 kV, 195.31 kV and 195.25 kV respectively.

- September’15

| Sl. No | S/s Name | Maximum | Minimum |
| --- | --- | --- | --- |
|  |  | kV | Day | Time | kV | Day | Time |
| 1 | Jayanagar | 251.43 | 20 | 05:45 | 223.37 | 14 | 17:00 |
| 2 | Theruvali | 238.73 | 20 | 07:00 | 208.65 | 25 | 8:15 |
| 3 | Bhanjanagar | 237.34 | 15 | 11:30 | 213.96 | 25 | 18:30 |
| 4 | Chandaka | 231.11 | 5 | 16:45 | 208.53 | 10 | 14:15 |
| 5 | Narendrapur | 223.43 | 26 | 17:45 | 183.36 | 1 | 18:45 |
| 6 | Joda | 237.77 | 20 | 10:00 | 223.42 | 30 | 19:15 |
| 7 | Tarkera | 232.95 | 01 | 06:00 | 222.45 | 30 | 18:45 |
| 8 | Bhadrak | 233.70 | 30 | 06:45 | 194.62 | 30 | 23:45 |
| 9 | Paradeep | 228.28 | 09 | 06:00 | 188.21 | 04 | 18:45 |
| 10 | Budhipadar | 232.90 | 17 | 14:00 | 224.35 | 30 | 18:30 |
| 11 | Duburi(O) | 235.09 | 22 | 16:15 | 216.10 | 08 | 21:00 |
| 12 | Duburi (N) | 232.55 | 22 | 16:15 | 213.73 | 08 | 20:45 |
| 13 | Balasore | 231.86 | 20 | 10:00 | 198.37 | 30 | 20:15 |
| 14 | Meramundali | 229.26 | 22 | 11:45 | 217.71 | 04 | 14:30 |
| 15 | Bidanasi | 232.38 | 22 | 10:15 | 214.88 | 09 | 18:30 |
| 16 | Katapalli | 233.24 | 17 | 14:15 | 216.15 | 10 | 20:15 |
| 17 | Nayagarh | 236.65 | 15 | 11:30 | 211.30 | 24 | 19:00 |
| 18 | Mendhasal | 229.49 | 05 | 16:45 | 209.92 | 10 | 14:15 |
| 19 | Bolangir | 235.73 | 14 | 22:15 | 202.18 | 09 | 18:30 |
| 20 | Barkote | 235.44 | 20 | 06:45 | 185.21 | 11 | 12:30 |
| 21 | Laxmipur | 246.87 | 20 | 07:00 | 219.85 | 14 | 18:30 |

The maximum voltage of 251.43 kV occurred at Jaynagar 220 kV bus while Narendrapur, Barkote and Paradeep 220 kV bus have experienced the minimum Voltage of 183.36 kV, 185.21 kV and 188.21 kV respectively.

Members may discuss.

- Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of September’15

- Energy Generation / Import during the month of August’15 & Sept’15

AUGUST’15

| Source of Power | Energy (MU) |
| --- | --- |
| Thermal (TTPS+IB) | 473.06 |
| OHPC Stations including Machhkund share | 656.45 |
| IPP & CGP Support | 681.53 |
| ISGS drawal | 611.28 |
| TOTAL | 2422.32 |

SEPTEMBER’15

| Source of Power | Energy (MU) |
| --- | --- |
| Thermal (TTPS+IB) | 463.32 |
| OHPC Stations including Machhkund share | 496.85 |
| IPP & CGP Support | 777.44 |
| ISGS drawal | 520.91 |
| TOTAL | 2258.52 |

- Drawal of Machhakund Power

The drawal of Machhakund power during the month of August’15 & September’15 were as detailed:

| Month | Total Generation (MU) | Odisha Drawal (MU) | AP Drawal (MU) |
| --- | --- | --- | --- |
| April’15 | 60.537 | 26.706 | 31.114 |
| May’15 | 38.508 | 17.300 | 19.478 |
| June’15 | 24.556 | 8.927 | 14.345 |
| July’15 | 52.6518 | 24.036 | 26.266 |
| August’15 | 60.393 | 29.393 | 28.749 |
| September’15 | 43.426 | 18.045 | 23.316 |

In the last meeting, it was decided that Jayanagar S/S shall explore the drawal during off peak period by providing matching load. It was also decided that OHPC shall convene a meeting between Machhakund authority, Gridco, OPTCL and SLDC. Southco shall expedite the construction of 33 kV line to connect Gumuda with Akhusing S/S.

Sr. G.M (PS) shall place the requisition for providing RVDU at Jayanagar control room for display of Machhakund drawal.

OHPC / SLDC/ Southco Utility may deliberate.

- DISCOM Drawal up to the month of September’15

| Name of DISCOM | Month | Approved Energy Drawal Prorated for the month (MU) | Scheduled Energy (MU) | Actual Energy Drawal ( MU) | Open Access Import Schedule (MU) | Net Energy Drawal ( MU) | Overdraw (MU) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 | 2 | 3 | 4 | 5=(3-4) | 6=(5-2) |
| CESU | April’15 | 721.644 | 676.468 | 700.852 | 3.892 | 696.96 | 20.492 |
|  | May’15 | 745.699 | 741.683 | 803.331 | 4.582 | 798.749 | 57.066 |
|  | June’15 | 721.644 | 680.782 | 731.303 | 4.094 | 727.209 | 46.427 |
|  | July’15 | 745.699 | 682.482 | 747.814 | 4.552 | 743.262 | 60.78 |
|  | Aug’15 | 745.699 | 730.38 | 787.091 | 1.844 | 785.247 | 54.867 |
|  | Sept’15 | 745.699 | 668.276 | 716.483 | 1.247 | 715.236 | 46.960 |
| WESCO | April’15 | 604.11 | 569.419 | 692.842 | 124.592 | 568.25 | -1.169 |
|  | May’15 | 624.247 | 608.011 | 742.524 | 132.217 | 610.307 | 2.296 |
|  | June’15 | 604.11 | 571.331 | 677.972 | 107.811 | 570.161 | -1.17 |
|  | July’15 | 624.247 | 550.147 | 716.622 | 102.587 | 614.035 | 63.888 |
|  | Aug’15 | 624.247 | 571.706 | 700.166 | 107.046 | 593.12 | 21.414 |
|  | Sept’15 | 624.247 | 530.990 | 668.478 | 96.912 | 571.566 | 40.576 |
| NESCO | April’15 | 431.507 | 412.235 | 432.73 | 17.888 | 414.842 | 2.607 |
|  | May’15 | 445.890 | 452.964 | 475.162 | 19.32 | 455.842 | 2.878 |
|  | June’15 | 431.507 | 428.938 | 458.649 | 23.262 | 435.387 | 6.449 |
|  | July’15 | 445.890 | 429.905 | 462.235 | 29.387 | 432.848 | 2.943 |
|  | Aug’15 | 445.890 | 460.083 | 495.915 | 31.255 | 464.66 | 4.57702 |
|  | Sept’15 | 445.890 | 417.330 | 486.661 | 38.715 | 447.946 | 30.616 |
| SOUTHCO | April’15 | 281.096 | 275.391 | 264.684 | 0 | 264.684 | -10.707 |
|  | May’15 | 290.466 | 277.641 | 285.102 | 0 | 285.102 | 7.461 |
|  | June’15 | 281.096 | 253.054 | 263.675 | 0 | 263.675 | 10.621 |
|  | July’15 | 290.466 | 282.015 | 285.292 | 0 | 285.292 | 3.277 |
|  | Aug’15 | 290.466 | 285.264 | 290.409 | 0 | 290.409 | 5.145 |
|  | Sept’15 | 290.466 | 252.453 | 257.882 | 0 | 257.882 | 5.429 |

The above figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali.

Members may please discuss.

- Under Frequency Relay operation in OPTCL System during the month of August & September’15.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of August’15 & September’15.

Members may note

PART C – Issues raised in 114th OCC meeting of ERPC scheduled to be held on 16.10.15

C.1: Handing over of 2 nos 132 kV bays at 400/220/132 kV Kuchei (Baripada) Grid S/s in Odisha.

As discussed in the Standing Committee meeting held in New Delhi on 08.02.2012, OPTCL has been allotted 4 nos. 132 kV bay at Kuchei Grid S/s in Odisha. During site visit by OPTCL for connection of 2 nos.132kV feeders from Kuchei –Jaleswar line, there is not sufficient space for termination. It was noticed that 2 nos. equipped 132kV bay meant for Jharkhand is available at Kuchei S/s lying un-utilised and is learnt that the same bays shall not be used in near future. It was also informed that JUVNL is yet to construct 132kV line that will be connected with these 2 nos. bay. Since these 2 nos. bay cannot be used by Jharkhand and the guarantee period of equipment / materials will expire, it is better OPTCL, can immediately use these bays for its line, which is going to be completed within next 3 to 4 months.

During 110th OCC meeting at Kolkata, this issue of allotment of bays was discussed and it was opined that consent of JUVNL, may be accorded for handing over the 2 nos. 132kV bays to OPTCL. In view of this, JUSNL is requested to communicate their consent for sparing the 2 nos. bays meant for JUVNL to OPTCL for better utilization of the existing equipments in the bay within its guarantee period.

O&M / SLDC may update.

C.2: Furnishing of data for Electricity Generation Targets for the year 2016-17

You are aware that the annual exercise of assessment and finalization of the generation targets and the planned maintenance schedules of the generating units for the year 2016-17 is being initiated by CEA. Although the generation performance of the various stations and their planned & unscheduled outages are regularly monitored in CEA but it is felt that a more realistic projection of month-wise generation in the coming year could be made by the respective Station Authorities.

While monitoring the generation performance during the current financial year, it has been observed that power utilities are facing the problem of loss of generation due to no / low schedules and losses accounted on other technical and commercial egresses. Accordingly, it is requested that the following inputs may kindly be submitted to this office as per the enclosed

Annexure:

i) (Annex- I (point no. 1 to 5)) The unit-wise proposed generation during 2016-17 (monthly and yearly) along with anticipated generation during 2015-16, the anticipated loss of generation on account of various constraints (e.g. Grid Constraints/ Low schedules/ Reserve shutdown /high fuel cost) may be accounted and furnish with necessary details. The details of units like boiler/ turbine make, date of commissioning etc may also be furnished.

ii) (Annex –I (point no. 6)) Utilities who have their Power Purchase Agreement (PPA) with various Discoms, Trader, states etc. and the details may be furnished in MW for Long and Medium term Agreement for assessing the expected generation for next year.

iii) (Annex- I (point no 7 (a) and (b)) The details of coal linkages from coal agencies and availability of gas/ liquid fuel.

iv) (Annex – I (point no. 8)) Unit wise cost of generation and rate of sale of power.

v) (Annex- II) Detailed unit-wise schedule of Planned Maintenance (approved by the respective Regional Power Committees) and R&M to be carried out during 2016-17 may also be furnished.

The information may please be furnished electronically at the email address

targetopmcea@gmail.com, kiran.meena@nic.in with a copy to ERPC (e-mail: mserpcpower@nic.in) latest by 31st October, 2015.

For any inconvenience in submission of data you may contact Mrs. Kiran Meena, Assistant Director, CEA, Ph- 011-26732684, Mob.08588831051 or write to the following address:

Chief Engineer (OPM Division), Room No.604 (N), Central Electricity Authority, Sewa Bhawan,

R.K. Puram, New Delhi-110066

Ph. 011-26105026 (Telefax)

For your convenience the input formats are also being made available at CEA website

http://www.cea.nic.in in Whats New/ Flash News and ERPC website www.erpc.gov.in.

All Generators & CGPs to comply.

C.3: Preparation of Load Generation Balance Report (LGBR) of ER for 2016-17

As per the IEGC under Clause 5.7.4 of Principal Regulations, first amendment in 2012 under Sub-Regulation (a), (b), (c) and (d) states that

a) “The RPC Secretariat shall be primarily responsible for finalization of the Annual Load Generation Balance Report (LGBR) and the annual outage plan for the following financial year by 31st December of each year. The LGBR shall be prepared by the respective RPC Secretariat for Peak as well as Off-peak scenarios”.

b) “Each SLDC shall submit LGBR for its control area, for Peak as well as Off-Peak scenario, by 31st October for the next financial year, to respective RPC Secretariat”.

c) “RPC Secretariat shall then come out with draft LGBR and draft outage plan for the next financial year by 30th November of each year for the regional grid taking ….”

d) “The outage plan shall be finalized in consultation with NLDC and RLDCs. The final LGBR after considering comments/observations of the stakeholders shall be prepared by RPC Secretariat by 31st December of each year. The……”So, the planning of maintenance of generating units of various generating companies of the region as well as outage of transmission system on annual basis in respect of Eastern Region for the year 2016-17 is to be finalised by 31st December, 2015. To facilitate the preparation of LGBR of Eastern Region by ERPC Secretariat within the above schedule period, the following data/ information for the year 2016-17 in respect of the constituents/ generators of Eastern

Region is required:

State and Central Sector Generators/ IPPs/CPPs

i)   The unit wise and station wise monthly energy generation proposed from existing units during 2016-17 (thermal/hydro/RES).

ii)  Annual maintenance programme for each of the generating units (thermal and hydro both).

iii) Generating units under R&M/ long outage indicating date of outage and reasons of outage and expected date of return (thermal and hydro both).

iv)  Partial and forced outage figures (in %) of generating units for the last 3 years.

v)   Month wise peak demand (MW) – restricted and unrestricted peak demand.

vi)  Month wise energy requirement (in MU).

vii) Schedule of commissioning of new generating units during 2016-17 and unit-wise monthly generation programme (in MU).

viii) Allocation of power from new generating units.

CTU / STU / Powerlinks / ENICL

Month wise annual planned outage of transmission systems (Transmission lines 220kV and above /ICTs/ Reactors/ other elements).

It is therefore requested to please send the above information (as applicable) on or before 31.10.2015 for compilation of data and preparation of LGBR of ER for the year 2016-17.

Information should be submitted in the form of soft copy through email (mail ID: rpc.erpc@gov.in / mserpc-power@nic.in).

Members may submit the data for LGBR by 31.10.2015.

SLDC / O&M / SGS / IPPs / CGPs may update the status.

C.4: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA.

NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

Members may discuss.

C.5: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.

In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In 85th OCC NTPC informed that, NTPC-Farakka has been certified with IS 18001. Other constituents including OHPC requested to interact with BIS with intimation to ERPC and get certified as per CEA direction. The matter is getting reviewed by highest authorities with top priority.

In 88th OCC NTPC informed that, all NTPC stations in Eastern Region are certified with IS 18001.

NHPC informed that, Teesta is also certified with IS 18001. After that, OHPC and CESC informed that their stations are certified with IS18001.

In 104th OCC, WBPDCL informed that Bandel TPS is certified with IS 18001.

OPTCL vide letter No.TB-SO-MISC-9/2010/1914 dated 20.12.2014 had proposed to go for IS 18001:2007 certification as per direction of CEA.

O&M may deliberate the status

C.6: Restricted Governor Mode of Operation.

The latest status of units of ER under RGMO is available at ERPC website (http://www.erpc.gov.in/) under Operation>Important data.

In 108th OCC, ERLDC informed that the RGMO/FGMO response of the generators needs monitoring on continuous basis.

OCC advised ERLDC to intimate the event of sudden drop in frequency to the generators and requested all generators to provide the RGMO/FGMO response data to ERLDC during the said incidents.

In 110th OCC, ERLDC informed that there was a generation loss of 1100MW at 19:25hrs on 16th June, 2015 and subsequent response of most of the generators were not satisfactory. FRC calculation for Eastern Region was circulated.

OCC advised all the generators to go through and place the response for this event in next OCC meeting.

ERLDC requested all the constituents to send the generator response.

CERC in the RoP dated 14.07.15 in Petition No. 84/MP/2015 filed by NRLDC has directed as under:

“10. The Commission also directed SLDCs to approach their respective SERCs to initiate appropriate action under the Act against the State generating stations which have not provided adequate primary response during both grid events reported by the petitioner.”

All Generators may deliberate.

C.7: Information regarding commissioning of new transmission element

1.125 MVAr B/R at Indravati (PG) was charged for the first time at 16:05 hrs of 01/08/15.

2. LILO of 220kV Ramchandrapur-Joda up to dead end tower at Chaibasa (JUSNL) was charged for the first time at 19:44hrs of 10/08/15.

3.400kV Baripada-New Duburi and 400kV New Duburi-Mendhasal were charged for the first time at 19:01hrs and 20:11hrs of 17/08/15 respectively. Also 80 MVAr BR at New Duburi was charged at 21:07hrs of 17/08/15.

4. 400kV Meramundali-New Duburi-II was charged for the first time at 13:15hrs of 11/09/15.

5. 315 MVA ICT-I and II at New Duburi were charged for the first time on no load at 21:02hrs and 21:18hrs of 28/08/15 respectively. Finally 315 MVA ICT-I and II at New Duburi were loaded at 14:24hrs and 15:37hrs of 29/08/15 respectively.

6. Indbharat Unit-I of 350 MW was synchronized for the first time at 17:03hrs of 11/09/15.

7. Barh Unit-V of 660 MW was synchronized for the first time at 11:19hrs of 17/09/15.

Members may note

C.8: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.

In 110th OCC, OPTCL updated the completion schedule of inter-connecting system as follows:

| Sl. No. | Name of the transmission line | Completion schedule |
| --- | --- | --- |
| 1. | 2 X 315MVA 400/220kV Bolangir S/s |
| a. | LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir S/S. | Severe ROW problem, December’2015 |
| b. | LILO of one circuit of Katapalli-Sadeipalli 220 kV D/C line at Bolangir S/S. | End of October’2015 |
| 2. | 400/220 kV Keonjhar S/S. |
| a. | Keonjhar (PG)-Keonjhar (OPTCL) 220 kV D/C line | Yet to be awarded |
| b. | Keonjhar (PG)-Turumunga (OPTCL) 220 kV D/C Line. | Yet to be awarded |
| 3. | 400/220 kV Pandiabil Grid S/s |
| a. | Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line | It will take 1 year for completion. |
| b. | LILO of one circuit of Atri-Puri (Samangara) 220 kV D/C line at Pandiabil (PG) | Work will be taken up after charging of Pandiabili (PG) Grid. |

CGM (Const) / CGM (O&M) may please update the status.

C.9: Third Party Protection Audit

Status of 1st Third Party Protection Audit:

The compliance status of 1st Third Party Protection Audit observations is as follows:

| Name of Constituents | Observations | Total Complied | % of Compliance |
| --- | --- | --- | --- |
| Odisha | 59 | 39 | 45.76 |

As deliberated in the OCC, OPTCL have complied 39 Nos observations out of total 49. The balance 10 nos belong to OHPC and OPGC. OHPC stated that they have complied their observations.

OPTCL/ OPGC / OHPC may please deliberate.

C.10: Antitheft charging of lines from Meramundali end --ERLDC

At 11:43hrs of 22/09/15, SLG (i.e Y-N) fault occurred on 400kV Meramundali- IBTPS-I (idle charged from Meramundali) but the breaker did not open at Meramundali and consequently LBB protection operated at Meramundali Bus-II leading to tripping of 400kV Meramundali-N.Duburi-II, 400kV and 400/220kV ICT-II at Meramundali (tripped from LV side). It may be noted that in the previous PCC/OCC meetings it was discussed and confirmed that 400kV Meramundali- IBTPS D/C line would not be idle charged from Meramundali end due to similar protection issues. Also, it may be noted that as per directives from Electrical Inspectorate Division, CEA, New Delhi, regarding tapping of lines 66kV and above class, provisions of sub regulation(6) of regulation 44 are to be strictly complied with and such matters need to be taken up with the Chief Electrical inspector.

ERLDC/OPTCL may update.

C.11: Availability of only one 220kV Main Bus in Joda Substation of OPTCL

It has been observed that at Joda S/s only one 220kV Main Bus is available. The other Main Bus is in place but cannot be utilised due to problem in isolators and hence shifting over of feeders to the other Main Bus cannot be done. Consequently, in case of any shutdown requirements for the Bus side isolators or if the Main Bus has to be taken under outage, all the 220kV lines have to be opened from Joda end. As an instance, for rectification of red hot and continuous sparking for R phase isolator clamp(Bus side) for 220kV Joda-Jindal feeder, the 220kV Bus had to be given shutdown on 13/09/15, and all 220kV outgoing feeders from Joda were required to be opened.

Considering importance of Joda Substation and to enhance reliability of the Grid it is felt that the remaining isolators may be re-commissioned to enable bringing the other 220kV Main Bus and the 220kV Transfer Bus into service.

113th OCC, it was advised OPTCL to look into the issue.

OPTCL agreed to send their views.

CGM (O&M) may please update.

C.12: Mock Black start exercises in Eastern Region – ERLDC

| Sl. No. | Name of Hydro Station | Schedule (1st) | Tentative Date | Schedule (2nd) |
| --- | --- | --- | --- | --- |
| 1 | U.Kolab | Last week of May, 2015 | Done on 16/07/2015 | Last Week of January, 16 |
| 2 | Rengali | 2nd week of June 2015 | Done on 13/10/2015 | Last week of November, 15 |
| 3 | U. Indravati | 3rd week of June 2015 | Done on 16/07/2015 | 2nd week of February 2016 |
| 4 | Balimela | 1st week of November,15 |  | 1st week of March 2016 |
| 5 | Burla |  |  |  |

A procedure for conducting mock black start exercise for Burla PH need to be developed by SLDC in coordination with OHPC.

SLDC / O&M / OHPC may deliberate.

C.13: Restoration of SCADA data

Updated latest status is circulated in the meeting. During deliberations in 99th OCC it was pointed out by most of the constituents that SCADA problem in many locations are due to behind the schedule progress of work on the part of CTU/PGCIL. OCC advised Powergrid / CTU to expedite and restore at least the priority RTUs by 31st July, 2014.

Updated status as updated in SCADA meeting which was held on 28th January’15 is circulated in the meeting.

The status as updated in the SCADA meeting is as given below:

- List of additional elements/feeders whose data is not available – station under ULDC project:

| Sl no | Name of Utility | KV | Name of station | Reason for non-reporting | Latest status |
| --- | --- | --- | --- | --- | --- |
| 1 | OPTCL | 220 | Vedanta (9x135 MW) | No status points are available. | No isolator status is available. MW/ MVAR not available for Sterlite 1/2 line, station transformer / Smelter. CBs of Bus coupler not available. Bus-1 KV/ HZ not available. Problem still not resolved |

iv) The updated status of telemetry of OPTCL Sub-Stations under ULDC project is project as given below:

| S/n | Name of RTU Locations | Latest status |
| --- | --- | --- |
| 1 | Nalco | OPTCL informed that RTU is reporting but intermittent since it was not configured properly. The issue was already taken up with Nalco and it will be resolved soon. OPTCL has resolved the issue. Some Unit generation polarity will be resolved by Feb 2015. Problem still not resolved |

v) RTU telemetry provided but data are intermittent / new element not wired.

| SL No | Name of station/ Utility | Reason for non reporting | Latest status |
| --- | --- | --- | --- |
| II | JSPL (Meramundali - 400) | Most of the data not available. | OPTCL informed that they are taking matter with JSPL. Problem still not resolved |

In the last meeting Vedanta Limited stated that materials are expected to be received from ABB by August and completion of work is expected by Sept’15.

OPTCL stated that they have resolved the issue. Reversal of CT polarity for two Nos. of units has to be done by NALCO. GCC may write to NALCO in this regard.

It was decided that O&M may not issue Technical clearance for open access transaction in favour of the CGPs till compliance of data communication.

Sr. G.M. (Telecom.) / GCC / OPTCL / NALCO / Vedanta / JSPL may deliberate.

C.14: Status of commissioning of generating station and transmission elements

New transmission elements:

| Sl No. | Name of Element | Expected date |
| --- | --- | --- |
| 7 | LILO of Baripada-Mendhasal D/C at New Duburi | August’2015 |
| 11 | 400 kV Meramundali-Dubri D/C | August’2015 |
| 12 | 400 kV IB-Meramundali D/C | October’ 2015 |
| 14 | 220 kV Bidansai-Cuttack D/C | March’2016 |

It was deliberated that 400 kV Meramundali-Dubri ckt-II charged on 11.09.2015.

C.G.M. (Const.) may deliberate.

PART-D – Operational Issues

D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of August’15:

| Sl. No | Name of Discom | No. of message issued | Over drawal (MU) |
| --- | --- | --- | --- |
| 1 | CESU | 18 | 54.867 |
| 2 | WESCO | 21 | 21.414 |
| 3 | NESCO | 6 | 4.577 |
| 4 | SOUTHCO | 6 | 5.145 |
|  | Total | 51 | 86.003 |

September’15

| Sl. No | Name of Discom | No. of message issued | Over drawal (MU) |
| --- | --- | --- | --- |
| 1 | CESU | 47 | 46.960 |
| 2 | WESCO | 55 | 40.576 |
| 3 | NESCO | 57 | 30.616 |
| 4 | SOUTHCO | 39 | 5.429 |
|  | Total | 198 | 123.581 |

It is noticed that CESU & WESCO had overdrawn a substantial quantum of power while Southco & NESCO had also overdrawn during the month of August . During the month of September all the Discoms have over drawn substantial quantum of power.  It was also noticed that CESU was continuously overdrawing since last six months. As stated by CESU, that they are predicting the drawal from the SCADA data.

In the last meeting it was decided that SLDC shall take all steps to display CESU’s real time drawal more accurately. The S/Ss not integrated with SCADA may be incorporated manually in the drawal display of CESU and compare with the actual to ascertain its accuracy.

SLDC/ Discoms may please deliberate.

D.2: Availability of data of real time power flow of feeders covered under Under-frequency Load shedding scheme (UFLS) and lower relief expected to obtained in real time system operation

In the last meeting Sr. G.M (Telecom) stated that MFMs have already been installed at the following S/Ss.

- Khurda			2. Bhanjanagar		3. Jayanagar		4. Theruvali

- Boinda			6. Chainpal			7. Dhenkanal		8. Balasore

9. Bhadrak		10. Jajpur Road		11. Bargarh		12. Bhadrak

13. Bolangir		14. Bolangir (New)		15. Rourkela		16. Sambalpur

Integration will be done soon after joint testing with EMR.

Sr. G.M. (Telecom) / OPTCL may please update the status.

D.3: Revival of Station Transformer for Station Auxiliary supply at Balimela HEP.

It was suggested to keep minimum number of ckts in service while of low generation at Balimela to reduce Var injection. Also it was suggested to avoid keeping two units in synchronization with minimum generation (10 MW each) to meet the auxiliary requirement in contingency conditions, even though DG set is available.

Although it was agreed in the last meeting by OHPC to keep one unit of Balimela synchronized and one No. 220 kV ckt during low generation period as per SLDC direction, it is noticed that BHEP is not complying the same.

In the last meeting it was suggested that, OHPC may install new pumps with high suction head to lift the technical water requirement. It was decided that OHPC may write to Water Resources Dept. for early repair of the barrage to prevent the leakage. OHPC may not waste water, which is a pricey item in the present scarcity scenario. OHPC stated that SLDC is instructing to keep two nos. of Upper Kolab units to keep synchronized. It was decided that SLDC should not instruct to keep units with minimum generation unless the situation warranted

Also new pump sets need to be installed at Burla PH for dewatering purpose.

SLDC / OHPC may deliberate.

D.4: Prolonged outage of transmission elements and tentative revival dates

The tentative revival dates of transmission elements are updated in the last meeting are as follows:

| Sl.No | Name of transmission element | Reason of outage | Probable date of revival |
| --- | --- | --- | --- |
| 1 | 220kV Jayanagar-Theruvali ckt-III breaker | Breaker defunct | September 2015 |
| 2 | 220/132 kV, 100 MVA Auto-II at Duburi | After inspection by repairer, date can be ascertained | Spares received. Work will be taken up after rainy season. |
| 3 | 220/132 kV, 100 MVA Auto-I, Bhadarak |  | September’ 2015 |

C.G.M. (O&M) may please update the status.

D.5: Communication issues

- Installation of communication equipment by CGPs / Industries.

The status of data communication from CGPs as deliberated in the last meeting is as follows

| Sl. No | Name of CGP | Present status |
| --- | --- | --- |
| 1 | M/s IFFCO, Paradeep | Outdoor commissioning work completed. RTU was locally tested. After replacement of the faulty CVT data will be integrated. |
| 2 | M/s MSP Mettalicks | PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited. |
| 3 | M/s NINL, Duburi | M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. |
| 4 | M/s Adhunik Metalliks | Work order placed with ABB for supply of RTU. |
| 5 | M/s Rohit Ferrotech | PLCC established and inspection by Telecom Engineers completed. Data base has already been prepared by OPTCL. |
| 6 | M/s VAL, Jharsuguda | No isolator status is available. MW/ MVAR not available for Sterlite 1&2 line, station transformer / Smelter. CBs of Bus coupler data, Bus-1 kV/Hz are not available. As per MOM between OPTCL & Sesa Sterlite, Jharsuguda dtd 22.09.2014, provision for telemetry data will be extended within 6 months (March, 2015). The CGP is not responding. VAL intimated that data shall be made available in all respect by July, 2015. No progress of work. |

It was decided in the last meeting that Member Secretary GCC shall write to the defaulting CGPs for compliance of data communication provisions. OPTCL, while issuing Technical clearance shall consider the provisions also.

GCC / O&M / Sr. G.M. (Telecom.) may please deliberate.

- Availability of Tap position of 400kV ICTs at Meramundali.

It is noticed that tap position of Meramundali ICTS are not available for SCADA display.

In the last meeting Sr. G .M (Telecom) stated that the work has been completed and shall be made available after joint testing with EMR by September’15.

Sr. G.M. (Telecom) may update.

- Availability of data at SLDC.

The data for

- Auto loading of 220/132 kV, 100 MVA Mendhasal S/S.

- Power flow through 132 kV Paradeep- Jagatsinghpur ckt.

In the last meeting Sr. G .M (Telecom) stated that the work has been completed and shall be made available after joint testing with EMR by September’15.

Sr. G.M. (Telecom) may please deliberate.

- Interruption of SCADA.

It is noticed that there is frequent interruption of SCADA System, resulting problem in real time operation. Action may be taken to avoid such frequent interruption of SCADA.

In the last meeting, Sr. G.M (Telecom) stated that Powergrid link between Rourkela-Kaniha is being used for data transfer. The link is not healthy due to heavy fibre loss. Powergrid have proposed to upgrade the existing SDH equipment to STM16. Work order has already been awarded.

Sr. G.M. (Telecom) may please update the status.

- Integration of new element.

M/s SSL-SEZ became a consumer of WESCO Utility with effect from 20.03.2015 and importing power through intra State open access from its CGP at Jharsuguda as well as from other utility. The drawal of SSL-SEZ needs to be integrated to SCADA to ascertain WESCO Utility drawal and State demand on real time basis. Since the SSL is reporting to ERLDC, Sr. G.M (Telecom) may write to ERLDC for integration of SSL-SEZ drawal in to the SCADA.

At present generation data of SSL-IPP connected with State Transmission System is being received through ERLDC. But most of the times the data become suspected. SEZ drawal date is yet to be received. However, the calculated figure is being displayed. Sr. G.M (Telcom) may write to SSL to transmit uninterrupted date of IPP generation as well as integrate SEZ drawal to ERLDC.

In the last meeting, Sr. G.M (Telecom) stated that M/S SSL is yet to respond. It was decided that SLDC and OPTCL, while issuing Technical clearance shall consider the provisions also.

Sr. G.M. (Telecom) / SLDC may please update.

D.6: Display of dashboard data.

On receipt of feedback from Dist. Utilities, IT representatives have made a demo at SLDC in presence of all Discoms, Telecom and SLDC, wherein some modifications were suggested. However, the dashboard display is functioning satisfactorily.

The status of lease line of all Discoms as deliberated in the meeting are as detailed.

| Sl. No | Dist. Utility | Status of leased line | Remarks |
| --- | --- | --- | --- |
| 1 | CESU | Already connected. RVDU commissioned | Data display available |
| 2 | WESCO | Required amount deposited with BSNL | Expected by 15th of Sept’15 |
| 3 | NESCO | Already connected. RVDU commissioned | Data display available |
| 4 | SOUTHCO | Already connected. RVDU commissioned | Data display available |

In the last meeting CGM (IT) stated that, IT representative had visited all four Discoms and found that the newly developed Dashboard is functioning satisfactorily. NESCO, WESCO and SOUTHCO have also issued certificate in this line. CESU stated that the Dashboard is functioning satisfactorily except some missing data.  It was decided that the Dash board shall be kept in parallel with RDVU for three months.

CGM (IT) / Sr. G.M (Telecom) / SLDC / All Dist. Utilities may please update the status.

D.7: Web based drawal / generation scheduling.

SLDC is going to implement web based drawal / generation scheduling for Dist. Utilities and State generating stations including IPPs and CGPs soon. A demo has been organized on 29.07.15.

In the last meeting, CGM (IT) stated that, web based generation scheduling module for State generating stations has been already been developed by IT wing. Modules for Discom and CGP / IPP shall be made available before the next PSOC meeting. After approval by the stake holders the same shall be go live from September’15. All Users were requested to forward their respective schedule in the prescribed format.

In the last meeting CGM (IT) stated that web based scheduling modules have already been done. SLDC may write all State generators, IPPs and CGPs to nominate their representative to attend one day demonstration cum training programme at SLDC for web base scheduling. The date of the training may be finalized in coordination with CGM (IT).

CGM (IT) / Discoms / OHPC / NTPC / OPGC / CGPs & SLDC may update the status.

D.8: Replacement of Battery bank at SLDC data centre.

It is noticed that the existing battery bank at SLDC data centre have become defunct and unable to supply back up in case of power failure. SLDC data centre experienced severe problem from 19.09.15 to 21.09.15 due to cable fault causing interruption of power. The DG set has to run continuously during the above period to provide power supply to the data centre. This issue has already been brought to the notice of IT wing of OPTCL, entrusted for maintenance of the Data Centre.

CGM (IT) / SLDC may please deliberate.

D.9: Tripping of feeders at Meramundali & Duburi Sub-station.

It is noticed that all 220kV feeders emanating from Meramundali & Duburi grid sub-station at 04:59 Hrs on 18.09.15 on LBB indication. As per the report received, D/P relay of 220kV Meramundali-Duburi ckt.-I operated at both the ends, but the breaker did not operate at either end resulting tripping of all 220kV feeders. Since, the above sub-stations are vital in OPTCL system, healthiness of protection system is a prime requirement from grid security point of view.

CGM (O&M) / CGM (Const.) / SLDC may please deliberate.

D.10: Non-compliance of Grid Code provision by Meramundali sub-station.

On 22.09.15, 400kV Meramundali - New Duburi  ckt tripped which was subsequently charged at Meramundali in absence of charging code from ERLDC through SLDC. ERLDC has issued a message to SLDC in this regard. It is also learnt that even New Duburi sub-station was not intimated prior to charging of the line.

D.11: DISCOM Issues

SOUTHCO:

- Data in RVDU are not being updated except 4 to 5 interception points. Schedule revision, SOUTHCO total Block period are not being updated with all other points.

- Due to implementation of Load restriction on account of huge power shortage during the current month, the actual drawal may be treated as schedule and waive out of deviation charges.

CESU

- Mismatch of displayed and actual drawal given in the bill lead to inaccurate drawal prediction on day-ahead basis.

- RVDU installed at CESU H.O. is not functioning very often.

NESCO

- Arrangement of 33 KV Bay and control unit at 132/33 KV Anandapur Grid Sub-station to avail power supply in 33KV feeder connecting to the newly constructed 33/11KV Structure at Chhenapadi and Rekutia under ODSSP.

- Extension of 33KV Bay at Baripada 132/33KV Grid Sub-station for dedicated 33 KV feeder of Medical College at Rangamatia.

CGM (IT) / Sr. G.M. (Telecom.) / CGM(O&M) / Gridco may please deliberate.

PART E: OPERATIONAL PLANNING

E.1:  Commissioning status of New Transmission elements.

The status of commissioning of new transmission elements is as follows:

| Sl. No | Transmission element details | Present Status |
| --- | --- | --- |
| 1 | Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line | Work has already been started. Expected to be completed by March 2016. |
| 2 | Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt | Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal, which is under progress. |
| 3 | Commissioning of 400 kV Ib-Meramundali D/C line. | 400kV SSEL-Meramundali line has been idle charged from SSEL end. Due to theft of conductor line could not be charged. Expected to be charged by end of Nov’2015. |
| 4 | Commissioning of 400 kV Duburi-Meramundali D/C line. | One ckt charged. |
| 5 | Commissioning of 220 kV Bidanasi-Cuttack line | Work in progress and expected to be completed by March 2016. |
| 6 | Commissioning of 220/132 kV Cuttack S/S | Work in progress and expected to be completed by October 2015. |
| 7 | Commissioning of 132 kV Baripada (PG)-Jaleswar line | Work has already been started, which will be completed by December 2015. Availability of bay at Baripada PG is uncertain. |
| 8 | Commissioning of 220/132 kV Kesinga S/S | Work under progress. Expected by September 2016. |
| 9 | Connectivity to Keonjhar PG | Proposal is mooted to be placed in the BoD meeting for connecting the proposed 220 / 33 kV Keonjhar S/S and with Turumunga S/S through 2 Nos. 220 kV ckts each. |
| 10 | LILO of 220 kV Burla - Bolangir line (one ckt) at Bolangir(PG) | Work has been started. Expected to be completed by October, 2015 |
| 11 | 220 kV Bolangir –Kesinga D/C line and LILO of one ckt at Bolangir(PG). | 220kV Bolangir - Kesinga D/C line is under construction. It is proposed to connect Bolangir (PG) through LILO arrangement of one ckt. Land dispute is yet to be resolved. |

Status of Discom’s action plan for power drawal from the S/Ss expected to be commissioned in near future.

| Sl. No | Name of the sub-station | Probable month of commissioning | Name of DISCOM | Action taken by Discoms |
| --- | --- | --- | --- | --- |
| 1 | 132/33kV, 2x20 MVA Khajuriakota | December’15 | CESU | By July’15 |
| 2 | 132/33kV, 2x40 MVA Kalunga | Commissioned | WESCO Utility |  |
| 3 | 220/33kV, 2x20 MVA Banei | Dec’15 | WESCO Utility |  |
| 4 | 132/33kV, 2x20 MVA Padmapur | Dec’15 | WESCO Utility |  |
| 5 | 132/33kV, 2x20 MVA Udala | Dec-15 | NESCO Utility | Line existing |
| 6 | 132/33kV, 2x20 MVA Somanathpur | Sept’15 | NESCO Utility | 33 kV feeder existing. |

CESU stated that action is being taken for construction of 33/0.4 kV S/S at Mendhasal to avail power supply for Mendhasal area.

All DISCOMS may update the status / CGM(O&M) & CGM(Const.) may please deliberate.

E.2: Installation of Energy Metering at Hydro / Traction & Solar projects.

In the last meeting OHPC stated that meters installed at Upper Kolab and Upper Indravati are yet to be tested. After completion of testing, Gridco shall consider the Secure meters for billing purpose. O&M may take action for testing of these energy meters early.

WESCO shall take follow up action with Railway authority for replacement of CT & PT and meter panel at the traction points and intimate the progress in the next meeting.

GRIDCO / OHPC / WESCO may please deliberate.

E.3: TTPS Issue.

Implementation of Feeder Metering

- STL team had been to TTPS for testing of feeder meters. TTPS authority had asked them for testing of other meters instead of these meters. It is construed that TTPS is deliberately avoiding implementation of feeder metering.  Further OPTCL has agreed to spare a set of PT and CT of required accuracy for installation at TTPS-Duburi 132 kV feeder. TTPS is delaying to place requisition for the same. Members expressed their concern for such activity. It was decided that Director (Com) shall take up the matter with the higher authority of NTPC.

- It is noticed that TTPS has replaced the energy meters (used for billing purpose) without prior intimation to SLDC / GRIDCO. The reason and circumstances under which the meters need replacement may be deliberated.

GRIDCO / OPTCL/ TTPS may please deliberate.

E.4: Major Events in the month of August & September’15

132/33 kV, 20 MVA Auto at Lapanga 440/220/132 kV S/S charged on 11.08.2015.

132/33 kV, 1x40 MVA Kalunga S/S charged on 07.09.2015

E.5: Important Grid Incidences during the month of August’15 and September’15.

Important incident occurred during the month of August’15 are as detailed.

On 30.08.2015 at 06:38hrs all the 220 kV feeders emanating from Tarkera tripped at remote end. All the 220 kV feeders emanating from Rengali tripped except 220 kV Tarkera Ckt-II. Total power failure to 220kV Bus observed at Tarkera and Rengali S/S. On investigation it was found that earth wire of 220 kV Tarkera-Rengali DC line snapped between Loc.No-539 to 540.

Important incident occurred during the month of September’15 are as detailed.

On 18.09.15 at 04:59 hrs, at Meramundali S/S, 400 kV New Duburi ckt-II tripped on ‘Y’ ph to E/F, Zone-1, Dist-37.2 km. 220 kV Meramundali-Duburi ckt-I relay operated at Meramundali was D/P, Zone-1, Dist-55 %, Dist-60.21 km but breaker did not operate. 220 kV bus bar protection operated and all breaker of Bus-I & II tripped on LBB.

On 22.09.15 at 11:43 hrs, at Meramundali S/S, 400 kV IbTPS-I   D/P, ‘Y’ ph to E/F, dist-126.8 km relay operated but the breaker did not operate. So, 400 kV New Duburi Ckt-II, Angul-I tripped on LBB at Meramundali S/S tripped making 400 kV bus-II dead. At the same time 220 kV side ICT-II tripped.

Members may discuss

E.6: Reporting of major Incidents

It is noticed that, very often the reports in respect of major incident received from the field S/Ss are not in proper order and not containing the relay indications and sequence with justification. At times the report is being received after considerable lapses of time, even after 2-3 days, which lead to embarrassing situation in the protection coordination sub-committee meeting of ERPC

In the last meeting, it was decided that the preliminary report shall be sent by the respective DGMs within 24 hours of occurrence of the incident to SLDC. The final report shall be sent to SLDC after due analysis by the concern E&MR Divisions, which is yet to be implemented.

Members may discuss.

E.7: Reporting of transmission element outage

It is noticed that in the event of planned / forced outage of transmission elements Grid S/Ss are not reporting the details such as relay indication, outage and restoration timing and work done indicating (Loc. No & phase) to SLDC Sou-motu. The above details are not being received even after a lot of persuasion from SLDC. Sometimes it takes months time to get the information. All GM, EHT (O&M) Circles may be advised to instruct all Grid S/Ss to forward the information to SLDC immediately after occurrence through email.

O&M may deliberate.

E.8: Outage of major transmission Elements during the month of August’15 & September’15. (above 10 hrs).

Outage of major transmission elements above 10 hours during the month of August’15 is as detailed.

| Sl No | Transmission lines | Tripping Dt/time | Restoration Dt/time | Reason |
| --- | --- | --- | --- | --- |
| 1 | 220 kV Tarkera-RSP Ckt-II | 03.08.15 00:09 | 03.08.15 17:41 | ‘R’ ph jumper snapped at Loc. No-27 |
| 2 | 220 kV New Duburi-JSL Ckt-I | 07.08.15 15:06 | 08.08.15 16:37 | ‘R’ ph LA burst at New Duburi S/S. |
| 3 | 220 kV Joda-Ramchandrapur Ckt | 11.08.15 17:59 | 12.08.15 12:10 | Problem at Ramchandrapur end. |
| 4 | 132 kV Theruvali-IMFA Ckt | 16.08.15 22:13 | 17.08.15 14:57 | ‘Y’ ph LA drop jumper snapped at IMFA end. |

Major outages are due jumper snapping.

Outage of major transmission elements above 10 hrs during the month of Sept’15 is as detailed.

| Sl No | Transmission lines | Tripping Dt/time | RestorationDt/time | Reason |
| --- | --- | --- | --- | --- |
| 1 | 220 kV TTPS-Kaniha Ckt | 05.09.15 13:39 | 12.09.15 15:08 | Breaker problem at TTPS end. |
| 2 | 132 kV Kendrapara-ParadeepCkt-II | 09.09.15 20:00 | 10.09.15 09:34 | ‘B’ ph jumper snapped at Loc. No-294 |
| 3 | 220 kV Balimela-JaynagarCkt-I | 13.09.15 14:13 | 14.09.15 15:45 | At Loc. No-1637 top conductor string insulator touched ‘B’ ph cross arm |
| 4 | 132 kV Berahmpur-DigapohandiCkt | 14.09.15 21:03 | 15.09.15 13:35 | ‘R’ ph jumper snapped near to Berahmpur grid. |
| 5 | 220 KV Meramundali-BhanjanagarCkt-II | 15.09.15 13:35 | 16.09.15 19:6 | Tree branches touched the line at Loc. NO-462 |
| 6 | 400 kV Meramundali-New DuburiCkt-II | 18.09.15 04:59 | 20.09.15 17:30 | ‘Y’ ph jumper snapped at Loc.No-23 |
| 7 | 132 kV Theruvali-RaygadaCkt | 19.09.15 11:38 | 22.09.15 20:40 | ‘R’ ph conductor snapped at Theruvali gantry. |
| 8 | 132 kV Tarkera-RSP Ckt-II | 19.09.15 16:50 | 21.09.15 18:30 | ‘Y’ ph LA burst at Tarkera S/S |
| 9 | 220 kV Joda-RamchandrapurCkt | 21.09.15 09:45 | 22.09.15 01:50 | Line fault from Ramchandrapur end. |
| 10 | 400 kV Meramundali-IbTPSCkt-I | 22.09.15 20:27 | 23.09.15 20:20 | ‘R’ ph LA burst at Meramundali S/S |

Major outages are due jumper snapping.

C.G.M. (O&M) may please deliberate.

E.9:  Review of Outage Program of State Generators / Transmission elements for the month of October’2015:

Tentative Outage programme for State Generators for the month of October’2015 are as follows:

| Sl. | Station | Unit | Period | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Burla | # 1 # 3 # 6 | 18.04.15 to 25.09.15 10.09.15 to 28.09.15 17.02.14 to continue | Capital Maintenance Guide vane problem Programming for R, M & U |
| 2 | Chiplima | #3 | 15.02.14 to continue | Programming for R & M |
| 3 | Balimela | # 1 # 3 # 7 | 31.01.13 to continue 26.06.15 to 31.10.15 10.07.15 to 31.10.15 | Programming for R & M Excitation problem Excitation problem |
| 4 | Upper Kolab | # 1 | 29.07.15 to 31.01.16 | Capital Maintenance |
| 5 | TTPS | # 3 # 6 | 25.09.15 to 09.10.15 25.10.15 to 28.11.15 | Boiler license renewal Capital Maintenance |
| 6 | IbTPS | # 1 # 2 | 05.01.16 to 08.02.16 05.04.16 to 25.04.16 | Annual Maintenance Annual Maintenance |

SLDC proposed to defer the shutdown programme of #6 TTPS and #1 & #2 of IbTPS due to power scenario in the State.

OHPC / TTPS / IbTPS / SLDC may deliberate.

E.10: Generation Program for the month of October’15.

Generation schedule for the month of October’15 furnished by OHPC are given below.

| Name of Hydro Gen. Station | Generation Programme (MW) | Reservoir Level as on 15.10.14 | Reservoir Level as on 15.10.15 | MDDL | High Flood Reservoir Level |
| --- | --- | --- | --- | --- | --- |
|  | Oct’15 (1st fortnight) | Oct’15 (2nd fortnight) |  |  |  |  |
| HPS, Burla | 80+40 | 120+40 | 625.06ft | 629.67ft | 590 ft. | 630 ft. |
| Balimela | 90 | 100 | 1512.50ft | 1501.70ft | 1440 ft. | 1516 ft. |
| Rengali | 60 | 20 | 122.01mt 1.78mt mtr mt | 119.28mt mt | 109.72mtr | 123.5 mtr. |
| U.Kolab | 80 | 100 | 856.49mt mt | 856.34mt | 844 mtr | 858 mtr. |
| U. Indravati | 220 | 270 | 640.71mt | 636.00mt mt | 625mtr | 642 mtr |
| MKD (O/D) | 30 | 30 | 2748.50ft | 2748.30ft | 2685 ft. | 2750 ft. |
| TOTAL | 600 | 680 |  |  |  |  |

OHPC may update.

E.11: Agenda by RSP (SAIL), Rourkela.

- Review of relay settings of TG grid to RSP 220kV feeders

- Drawal clearance during shutdown of 60MW unit-1 of NSPCL from 01.10.15 to 20.10.15.

- Clearance for construction of two 220kV bays at Tarkera grid sub-station and construction of 220kV D/C line.

RSP and O&M may please deliberate

E.12: Agenda by HINDALCO, Hirakud

Frequent tripping of 132kV Burla-Hindalco and Burla-FRP feeders causing unreliability supply. 33 trippings during April-15 to August15.

HINDALCO and O&M may please deliberate.

E.13: Anticipated power generation and demand for the month of November’2015.

| Sl. No | Discom | Average | Peak |
| --- | --- | --- | --- |
| 1 | CESU | 1000 | 1300 |
| 2 | WESCO | 980 | 1220 |
| 3 | NESCO | 680 | 850 |
| 4 | SOUTHCO | 360 | 480 |
| 5 | Total | 3020 | 3900 |
|  | Demand including Loss | 3150 | 4000 |
| Availability |  |  |
|  | Hydro | 600 | 1300 |
|  | State Thermal | 750 | 760 |
|  | IPP share | 650 | 750 |
|  | ISGS share | 900 | 950 |
|  | CGP support (OA) | 150 | 200 |
| 6 | Total availability | 3050 | 3960 |
| 7 | Surplus / Deficit | -100 | -40 |

PART F: OTHER ISSUES

F.1: Training Programme on “Power Distribution Regulations & Automation” proposed to be conducted by National Power Training Institute (NPTI), Bengaluru for DISCOM executives.

NPTI, Bengaluru has proposed a five days training programme on “Power Distribution Regulations & Automation” for DISCOM executives at Bengaluru. The details of programme & courses to be covered have been forwarded to all DISCOMs by NPTI. The DISCOMs may contact & suggest for any item to be included and avail the opportunity of the said programme.

All DISCOMs may please deliberate.

F.2:  Date and Venue of the next (91st) PSOC meeting.