Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

# Agenda

for

92nd Power System Operational Coordination Meeting

## Date: 29.12.2015

### Venue: PTC, Chandaka

Odisha Power Transmission Corporation Ltd. Bhubaneswar.

Agenda for 92nd PSOC Meeting to be held on 29.12.2015 at PTC, Chandaka

Item no. 1: Confirmation of the minutes of the 91st PSOC Meeting held on 28.11.2015

The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2015/4402(41), dated 15.12.2015 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)

B   : Grid Performance for the month of November’2015

C.1: Status of PLCC system installed in Eastern Region

C.2: Third Party Protection Audit

C.3: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

C.4: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.

C.5: Pollution mapping for Eastern Region

C.6: Nodal coordinators for web based scheduling software

C.7: Dynamic data of Generator Models required in PSSE for Simulations -ERLDC

C.8: Information regarding commissioning of new transmission element

C.9: Mock Black start exercises in Eastern Region – ERLDC

C.10: Restricted Governor Mode of Operation.

C.11: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s

C.12: Restoration of SCADA data

D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Availability of data of real time power flow of feeders covered under Under-frequency Load shedding scheme (UFLS) and lower relief expected to obtained in real time system operation

D.3: High Voltage at 400 kV Meramundali & Duburi S/S.

D.4: Revival of Station Transformer for Station Auxiliary supply at Balimela HEP.

D.5: Prolonged outage of transmission elements and tentative revival dates

D.6: Communication issues

D.8: Display of dashboard data.

D.9: Web based drawal / generation scheduling.

D.10: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.11: DISCOM Issues

E.1:  Commissioning status of New Transmission elements.

E.2: Installation of Energy Metering at Hydro / Traction & Solar projects.

E.3: TTPS Issue.

E.4: Major Events in the month of November’15

E.5: Important Grid Incidences during the month of November’15.

E.6: Outage of major transmission Elements during the month of November’15. (above 10 hrs).

E.7: Review of Outage Program of State Generators for the month of January’2016.

E.8: Generation Program for the month of January’16.

E.10: RSP (SAIL), Rourkela Issue.

E11:  Operating procedure for Odisha System.

E.12: Anticipated power generation and demand for the month of December’2015.

PART B: GRID PERFORMANCE

Review of Grid Performance for the month of November’15.

- Frequency:

Hourly frequency variation for the month of November’15.

| Month | % of time frequency remained |
| --- | --- |
|  | <49.00 | 49.00-49.70 | 49.70-49.90 | 49.90-50.05 | >50.05 |
| Sept’15 | 0.00 | 0.38 | 24.55 | 61.04 | 14.03 |
| Oct’15 | 0.00 | 0.03 | 11.64 | 66.83 | 21.51 |
| Nov’15 | 0.00 | 0.03 | 10.21 | 64.82 | 24.94 |

Maximum & Minimum frequency during the month of November’15.

| Month | Freq (Hz) | Date | Time |
| --- | --- | --- | --- |
| October’15 | Maximum – 50.21 | 28.10.15 | 13:00 Hrs |
|  | Minimum – 49.71 | 17.10.15 | 18:15 Hrs |
| November’15 | Maximum – 50.19 | 15.11.15 | 21:45 Hrs |
|  | Minimum – 49.72 | 06.11.15 | 06:30 Hrs |

- Grid Demand for the month of November’15.

| Month | Demand | Maximum Consumption | Maximum Demand | Minimum Demand |
| --- | --- | --- | --- | --- |
|  | MU | Avg. (MW) | MU | Date | MW | Date | Time | MW | Date | Time |
| Oct’15 | 2363 | 3177 | 79.64 | 19.10.15 | 4157 | 16.10.15 | 19:00 | 2435 | 13.10.15 | 14:00 |
| Nov’15 | 2084 | 2895 | 75.36 | 05.11.15 | 3968 | 05.11.15 | 20:00 | 2097 | 14.11.15 | 15:00 |
| Nov’14 | 1972 | 2739 | 69.92 | 04.11.14 | 3630 | 12.11.14 | 20:00 | 2000 | 20.11.14 | 14:00 |

Members may please discuss.

- Voltage Profile of 220 kV Buses in OPTCL system for the month of: November’15

| Sl. No | S/s Name | Maximum | Minimum |
| --- | --- | --- | --- |
|  |  | kV | Day | Time | kV | Day | Time |
| 1 | Jayanagar | 246.75 | 17 | 23:00 | 226.60 | 3 | 13:45 |
| 2 | Theruvali | 237.00 | 26 | 02:30 | 211.94 | 11 | 18:30 |
| 3 | Bhanjanagar | 238.84 | 20 | 02:45 | 222.00 | 14 | 18:30 |
| 4 | Chandaka | 235.49 | 20 | 02:45 | 216.15 | 06 | 18:30 |
| 5 | Narendrapur | 219.68 | 17 | 23:45 | 182.55 | 24 | 17:30 |
| 6 | Joda | 240.68 | 28 | 03:00 | 224.12 | 03 | 18:15 |
| 7 | Tarkera | 236.24 | 12 | 02:15 | 227.93 | 14 | 18:45 |
| 8 | Bhadrak | 239.48 | 30 | 03:45 | 218.52 | 02 | 17:30 |
| 9 | Paradeep | 236.42 | 16 | 04:45 | 211.25 | 03 | 18:00 |
| 10 | Budhipadar | 235.55 | 30 | 22:45 | 219.73 | 05 | 08:30 |
| 11 | Duburi(O) | 240.86 | 30 | 03:30 | 223.37 | 13 | 18:30 |
| 12 | Duburi (N) | 228.16 | 30 | 03:30 | 211.65 | 02 | 17:45 |
| 13 | Balasore | 237.63 | 20 | 03:00 | 217.42 | 02 | 17:45 |
| 14 | Meramundali | 232.61 | 20 | 03:30 | 220.00 | 18 | 17:30 |
| 15 | Bidanasi | 236.65 | 20 | 03:45 | 220.77 | 06 | 17:45 |
| 16 | Katapalli | 236.42 | 29 | 09:45 | 214.71 | 04 | 19:00 |
| 17 | Nayagarh | 235.49 | 23 | 00:15 | 218.12 | 18 | 17:45 |
| 18 | Mendhasal | 235.44 | 20 | 02:45 | 217.42 | 06 | 18:30 |
| 19 | Bolangir | 244.44 | 10 | 16:45 | 200.28 | 04 | 18:45 |
| 20 | Barkote | 238.21 | 30 | 03:45 | 230.41 | 02 | 18:00 |
| 21 | Laxmipur | 243.69 | 18 | 00:15 | 223.72 | 03 | 14:45 |

The maximum Voltage of 246.75 kV occurred at Jaynagar 220 kV bus while Narendrapur, bus 220 kV bus have experienced the minimum Voltage of 182.55 kV.

Members may discuss.

- Energy Generation / Import during the month of November’15

| Source of Power | Energy (MU) |
| --- | --- |
| Thermal (TTPS+IB) | 525.30 |
| OHPC Stations including Machhkund share | 237.03 |
| IPP & CGP Support | 643.60 |
| ISGS drawal | 678.43 |
| TOTAL | 2084.37 |

- Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of Nov-15

- DISCOM Drawal up to the month of November’15

| Name of DISCOM | Month | Approved Energy Drawal Prorated for the month (MU) | Scheduled Energy (MU) | Actual Energy Drawal ( MU) | Open Access Import Schedule (MU) | Net Energy Drawal ( MU) | Overdraw (MU) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 | 2 | 3 | 4 | 5=(3-4) | 6=(5-2) |
| CESU | April’15 | 721.644 | 676.468 | 700.852 | 3.892 | 696.96 | 20.492 |
|  | May’15 | 745.699 | 741.683 | 803.331 | 4.582 | 798.749 | 57.066 |
|  | June’15 | 721.644 | 680.782 | 731.303 | 4.094 | 727.209 | 46.427 |
|  | July’15 | 745.699 | 682.482 | 747.814 | 4.552 | 743.262 | 60.78 |
|  | Aug’15 | 745.699 | 730.38 | 787.091 | 1.844 | 785.247 | 54.867 |
|  | Sept’15 | 721.644 | 668.276 | 716.483 | 1.247 | 715.236 | 46.96 |
|  | Oct’15 | 745.699 | 729.776 | 733.265 | 3.606 | 729.659 | -0.117 |
|  | Nov’15 | 721.644 | 607.136 | 636.447 | 4.449 | 631.998 | 24.862 |
| WESCO | April’15 | 604.11 | 569.419 | 692.842 | 124.592 | 568.25 | -1.169 |
|  | May’15 | 624.247 | 608.011 | 742.524 | 132.217 | 610.307 | 2.296 |
|  | June’15 | 604.11 | 571.331 | 677.972 | 107.811 | 570.161 | -1.17 |
|  | July’15 | 624.247 | 550.147 | 716.622 | 102.587 | 614.035 | 63.888 |
|  | Aug’15 | 624.247 | 571.706 | 700.166 | 107.046 | 593.12 | 21.414 |
|  | Sept’15 | 604.11 | 530.99 | 668.478 | 96.912 | 571.566 | 40.576 |
|  | Oct’15 | 624.247 | 550.739 | 732.87 | 124.713 | 608.157 | 57.418 |
|  | Nov’15 | 604.11 | 524.758 | 655.613 | 116.562 | 539.051 | 14.293 |
| NESCO | April’15 | 431.507 | 412.235 | 432.73 | 17.888 | 414.842 | 2.607 |
|  | May’15 | 445.890 | 452.964 | 475.162 | 19.32 | 455.842 | 2.878 |
|  | June’15 | 431.507 | 428.938 | 458.649 | 23.262 | 435.387 | 6.449 |
|  | July’15 | 445.890 | 429.905 | 462.235 | 29.387 | 432.848 | 2.943 |
|  | Aug’15 | 445.890 | 460.083 | 495.915 | 31.255 | 464.66 | 4.57702 |
|  | Sept’15 | 431.507 | 417.33 | 486.661 | 38.715 | 447.946 | 30.616 |
|  | Oct’15 | 445.890 | 449.492 | 493.603 | 41.506 | 452.097 | 2.605 |
|  | Nov’15 | 431.507 | 380.024 | 443.309 | 68.066 | 375.243 | -4.781 |
| SOUTHCO | April’15 | 281.096 | 275.391 | 264.684 | 0 | 264.684 | -10.707 |
|  | May’15 | 290.466 | 277.641 | 285.102 | 0 | 285.102 | 7.461 |
|  | June’15 | 281.096 | 253.054 | 263.675 | 0 | 263.675 | 10.621 |
|  | July’15 | 290.466 | 282.015 | 285.292 | 0 | 285.292 | 3.277 |
|  | Aug’15 | 290.466 | 285.264 | 290.409 | 0 | 290.409 | 5.145 |
|  | Sept’15 | 281.096 | 252.453 | 257.882 | 0 | 257.882 | 5.429 |
|  | Oct’15 | 290.466 | 279.951 | 281.598 | 0 | 281.598 | 1.647 |
|  | Nov’15 | 281.096 | 254.482 | 260.385 | 0 | 260.385 | 5.903 |

The above figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali.

Members may please discuss.

- Drawal of Machhakund Power

The drawal of Machhakund power up to the month of November’15 are as detailed:

| Month | Total Generation (MU) | Odisha Drawal (MU) | AP Drawal (MU) |
| --- | --- | --- | --- |
| April’15 | 60.537 | 26.706 | 31.114 |
| May’15 | 38.508 | 17.300 | 19.478 |
| June’15 | 24.556 | 8.927 | 14.345 |
| July’15 | 52.6518 | 24.036 | 26.266 |
| August’15 | 60.393 | 29.393 | 28.749 |
| September’15 | 43.426 | 18.045 | 23.316 |
| October’15 | 54.825 | 25.288 | 27.537 |
| November’15 | 52.776 | 23.079 | 27.339 |

Earlier, it was decided that Jayanagar S/S shall explore the drawal during off peak period by providing matching load.

In the last meeting, Sr. GM (Telecom) stated that providing of RVDU shall be taken up with M/s Chemtrol. SLDC shall place requisition for providing a RVDU at Jayanagar control room. Southco stated that construction of 33 kV Gumuda-Akhusing feeder is expected to be completed by March 2015.

Sr. G.M (O&M) -I stated that it is proposed for extending power supply to Rayagada Rly traction S/S from Rayagada S/S. Normally Rayagada is on Machhakund system. There may be frequent interruption of  Rly. Supply with the changeover of Rayagada sub-station from Machhakund to BTH system. Moreover, traction load has adverse impact on Machhakund units for which the traction feeder has already been disconnected from Machhakund PH.  It was decided to examine for connecting the proposed Rayagada Rly traction S/S feeder with Theruvali Grid S/S.

SLDC/ CGM (Const) / Southco Utility may deliberate.

- Under Frequency Relay operation in OPTCL System during the month of November’15.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of November’15.

Members may note

PART C – Issues raised in 116th OCC meeting of ERPC held on 23.12.15

C.1: Status of PLCC system installed in Eastern Region

In 30th TCC/ERPC, Powergrid agreed to restore the PLCC system at both ends (its own end as well as the constituent end) of a line wherein the other ends are not operational for some reasons or others as one time job.

In the last meeting Sr. G.M (Telecom) stated that since most of the links are covered under optical fibre project, except 220 kV Budhipadar-Korba, 132 kV Joda-Kenduposi, Indravati-Indravati-PG and Rengali switchyard-Rengali (PG), PLCC is required only for Budhipadar-Korba and Joda-Kenduposi lines. Indravati & Rengali will be done through OPGW. CGM (O&M) shall intimate POWERGRID accordingly.

In 115th OCC, ERPC advised POWERGRID to discuss the matter with OPTCL.

C.G.M (O&M) / Sr. G.M. (Telecom.)  may deliberate.

C.2: Third Party Protection Audit

Status of 1st Third Party Protection Audit:

The compliance status of 1st Third Party Protection Audit observations is as follows:

| Name of Constituents | Observations | Total Complied | % of Compliance |
| --- | --- | --- | --- |
| Odisha | 59 | 38 | 64.41 |

As deliberated in the OCC, OPTCL have complied 39 Nos observations out of total 49. The balance 10 nos belong to OHPC and OPGC. OHPC stated that they have complied their observations.

Member Secretary suggested to apply for PSDF for compliance of the observations.

In the last meeting C. G.M (O&M) stated that OPTCL shall apply for 2nd phase PSDF for compliance of the observations.

OPTCL/ OPGC / OHPC may please deliberate.

C.3: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA.

NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In 113th OCC, Member Secretary informed that during interaction with consultants of Grid Study Committee, NLDC agreed that they will plan for conducting workshops on crisis management plan for Cyber Security and few workshops will also be held in Eastern Region.

In the last PSOC meeting, it was decided that CGM (IT) shall examine and prepare a Crisis Management Plan for countering the cyber attacks for OPTCL. Sr. G.M. (PS) has written a letter to CGM(IT) in this regard.

CGM (IT) may deliberate.

C.4: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.

In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In 85th OCC NTPC informed that, NTPC-Farakka has been certified with IS 18001. Other constituents including OHPC requested to interact with BIS with intimation to ERPC and get certified as per CEA direction. The matter is getting reviewed by highest authorities with top priority.

In 88th OCC NTPC informed that, all NTPC stations in Eastern Region are certified with IS 18001.

NHPC informed that, Teesta is also certified with IS 18001. After that, OHPC and CESC informed that their stations are certified with IS18001.

In 104th OCC, WBPDCL informed that Bandel TPS is certified with IS 18001.

OPTCL vide letter No.TB-SO-MISC-9/2010/1914 dated 20.12.2014 had proposed to go for IS 18001:2007 certification as per direction of CEA.

In the last meeting CGM (O&M) stated that BIS is not responding for certification. SLDC may be get clarified from ERPC whether ISO or BIS is required.

SLDC may deliberate the status.

C.5: Pollution mapping for Eastern Region

The Pollution Mapping work in ER was started with on-site measurement of ESDD and NSDD.

The latest available status is as follows:

| Utility | Scope | Installed Locations | Number of locations where 1st set of Measurements Completed |
| --- | --- | --- | --- |
| OPTCL | 164 | 102 | 99 |

OCC advised all constituents to complete the 1st set of measurements and send to Powergrid/ CPRI. Powergrid vide mail dated 5th November, 2015 requested to complete the 2nd set of measurements by end of Novemebr, 2015, as it is already passed 4 months after completion of 1st set of measurements for the most of the locations.

Powergrid also requested to provide probable pollution sources and direction details near the site with specific details e.g. type of pollution sources (factories, Brick Kiln, Agricultural pollutant, Saline pollutant from sea coast), direction form site, distance from site etc.

In the last meeting CGM (O&M) stated that only Discom locations are left due to non-availability of testing kit. Since CPRI is not responding for supply of more kits, the existing kits will be diverted to Discom locations after completion of measurement for O&M locations.

CGM (O&M) may update.

C.6: Nodal coordinators for web based scheduling software

Presently, development of the web-based scheduling software is at an advanced stage and testing of the same is required before the final commissioning. It is hence requested that nodal persons may be identified for being associated with the testing and commissioning phase of the software.

Constituents nominate the Nodal Officer. In the 115th OCC meeting SLDC has intimated the name of persons for co-ordination as Nodal Officer.

SLDC may deliberate.

C.7: Dynamic data of Generator Models required in PSSE for Simulations -- ERLDC

To carry out proper simulation studies in PSSE, actual generator parameters are required as incomplete or incorrect modeling of generator may not give valid simulation result. Hence all the generating companies are requested to furnish data for generator, exciter, governor, PSS of their all generating units in the format.

In 114th OCC, the house was informed that the formats are available at ERPC website.(www.erpc.gov.in)

OCC advised all the generating utilities to submit the relevant information as per the format.

All generating utilities agreed to submit. Till date, the data received only from Khahalgaon & Barh, NTPC, NHPC Teesta-V and GMR.

In 115th OCC, all the other generating utilities were advised to submit the data latest by 15th Dec’15.

In the last meeting, it was decided that OHPC, OPGC and TTPS shall forward their Email Id to ERPC directly.

OHPC/ OPGC/TTPS/CGPs may deliberate.

Item no. C.8: Information regarding commissioning of new transmission element

125MVAR B/R at Jeypore was charged for the first time at 21:36hrs of 30/11/15.

C.9: Mock Black start exercises in Eastern Region – ERLDC

| Sl. No. | Name of Hydro Station | Schedule (1st) | Tentative Date | Schedule (2nd) |
| --- | --- | --- | --- | --- |
| 1 | U.Kolab | Last week of May, 2015 | Done on 16/07/2015 | Last Week of January, 16 |
| 2 | Rengali | 2nd week of June 2015 | Done on 13/10/2015 | January, 16 |
| 3 | U. Indravati | 3rd week of June 2015 | Done on 16/07/2015 | 2nd week of February 2016 |
| 4 | Balimela | 1st week of November,15 | Done on 24/11/2015 | 1st week of March 2016 |
| 5 | Burla |  |  | January 2016 |

A procedure for conducting mock black start exercise for Burla PH need to be developed by SLDC in coordination with OHPC & OPTCL.

SLDC / O&M / OHPC may deliberate.

C.10: Restricted Governor Mode of Operation.

The latest status of units of ER under RGMO is available at ERPC website (http://www.erpc.gov.in/) under Operation>Important data.

In 108th OCC, ERLDC informed that the RGMO/FGMO response of the generators needs monitoring on continuous basis.

OCC advised ERLDC to intimate the event of sudden drop in frequency to the generators and requested all generators to provide the RGMO/FGMO response data to ERLDC during the said incidents.

ERLDC informed that on 12.10.2015 there was sudden load loss of 900 MW in NR and they observed 0.11 Hz change in the grid frequency.

As per the data of ERLDC they have received the RGMO/FGMO response only from Burla, Kahalgaon, Teesta-V and SSL generators. The response of other generators are not satisfactory.

In the OCC meeting, reports received from OPGC & Chiplima PH have been handed over to ERLDC.

In the OCC meeting, it was decided that hydro units of 10MW capacity & thermal units of 200MW capacity shall intimate the response of governor to ERLDC.

ERLDC intimated that a new web group was formed for sharing governor response of various generator in ER. The url of the group is https://in.groups.yahoo.com/neo/groups/er_gov_respons/info

ERLDC requested to send email ids (preferably Yahoo mail ids) of the Generators where invitation will be sent. Governor response for the event of 12-11-2015 at 23:05 hrs based on ERLDC SCADA data is already posted in the group.

CERC in the RoP dated 14.07.15 in Petition No. 84/MP/2015 filed by NRLDC has directed as under:

“10. The Commission also directed SLDCs to approach their respective SERCs to initiate appropriate action under the Act against the State generating stations which have not provided adequate primary response during both grid events reported by the petitioner.”

All Generators may deliberate.

C.11: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.

In 115th OCC, OPTCL updated the completion schedule of inter-connecting system as follows:

| Sl. No. | Name of the transmission line | Completion schedule |
| --- | --- | --- |
| 1. | 2 X 315MVA 400/220kV Bolangir S/s |
| a. | LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir S/S. | 5 out of 14 completed. Severe ROW problem, March’2016 |
| b. | LILO of one circuit of Katapalli-Sadeipalli 220 kV D/C line at Bolangir S/S. | One tower left due to forest clearance. End of March’16 |
| 2. | 400/220 kV Keonjhar S/S. |
| a. | Keonjhar (PG)-Keonjhar (OPTCL) 220 kV D/C line | Tender opening 18 Nov 2015 |
| b. | Keonjhar (PG)-Turumunga (OPTCL) 220 kV D/C Line. | Yet to be awarded |
| 3. | 400/220 kV Pandiabil Grid S/s |
| a. | Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line | It will take 1 year for completion. |
| b. | LILO of one circuit of Atri-Puri (Samangara) 220 kV D/C line at Pandiabil (PG) | May, 2016 |

CGM (Const) / CGM (O&M) may please update the status.

C.12: Restoration of SCADA data

Updated latest status is circulated in the meeting. During deliberations in 99th OCC it was pointed out by most of the constituents that SCADA problem in many locations are due to behind the schedule progress of work on the part of CTU/PGCIL. OCC advised Powergrid / CTU to expedite and restore at least the priority RTUs by 31st July, 2014.

Updated status as updated in SCADA meeting which was held on 28th January’15 is circulated in the meeting.

The status as updated in the SCADA meeting is as given below:

- List of additional elements/feeders whose data is not available – station under ULDC project:

| Sl no | Name of Utility | KV | Name of station | Reason for non-reporting | Latest status |
| --- | --- | --- | --- | --- | --- |
| 1 | OPTCL | 220 | Vedanta (9x135 MW) | No status points are available. | No isolator status is available. MW/ MVAR not available for Sterlite 1/2 line, station transformer / Smelter. CBs of Bus coupler not available. Bus-1 KV/ HZ not available. Problem still not resolved |

iv) The updated status of telemetry of OPTCL Sub-Stations under ULDC project is project as given below:

| S/n | Name of RTU Locations | Latest status |
| --- | --- | --- |
| 1 | Nalco | OPTCL informed that RTU is reporting but intermittent since it was not configured properly. The issue was already taken up with Nalco and it will be resolved soon. OPTCL has resolved the issue. Some Unit generation polarity will be resolved by Feb 2015. Problem still not resolved |

v) RTU telemetry provided but data are intermittent / new element not wired.

| SL No | Name of station/ Utility | Reason for non reporting | Latest status |
| --- | --- | --- | --- |
| II | JSPL (Meramundali - 400) | Most of the data not available. | OPTCL informed that they are taking matter with JSPL. Problem still not resolved |

In the last meeting, Sr. G.M (Telecom) suggested that Vedanta Ltd may explore for alternate Vender for rectification of problem at their CGP.

Sr. G.M. (Telecom.) / GCC / OPTCL / NALCO / Vedanta / JSPL may deliberate.

PART-D – Operational Issues

D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of November’15:

| Sl. No | Name of Discom | No. of message issued | Over drawal (MU) |
| --- | --- | --- | --- |
| 1 | CESU | 27 | 24.862 |
| 2 | WESCO | 24 | 14.293 |
| 3 | NESCO | 6 | -4.781 |
| 4 | SOUTHCO | 4 | 5.903 |
|  | Total | 61 | 40.277 |

It is noticed that CESU & WESCO had overdrawn a substantial quantum of power to the tune of 24.8 & 14.2 MU respectively.

SLDC/ Discoms may please deliberate.

D.2: Availability of data of real time power flow of feeders covered under Under-frequency Load shedding scheme (UFLS) and lower relief expected to obtained in real time system operation

In the last meeting, Sr. G.M (Telecom) stated that data availability for all feeders have been completed except three Nos. of S/Ss namely Boinda, Dhenkanal and Kendrapara, for which the CT / PT output is required. It was decided that all the remaining S/Ss may be completed before the next meeting in coordination with the respective EMR wing, as the matter has been considerably delayed.

Sr. G.M. (Telecom) / OPTCL may please update the status.

D.3. High Voltage at 400 kV Meramundali & Duburi S/S_ Reactive Power Injection by OPTCL

Persistent high Voltage is being observed at Meramundali & Duburi 400 kV buses. Since these buses are the inter State exchange points, Reactive power injection penalty is being charged to Gridco. It is learnt that one no of 50 MVAr line reactor at Meramundali is not functioning. O&M may take action for rectification of the same early. It may also be examined for installation of 2nd reactor at Duburi to arrest the high Voltage. Further Powergrid may be requested to shift the line reactor of the 400 kV Baripada- New Duburi-Mendhasal ckt from Mendhasal to New Duburi.

In the last meeting, it was suggested that defunct line reactor at Meramundali may be brought into service early and Powergrid may be requested to enhance the capacity of reactor at New Duburi.

O&M may update the status.

D.4: Revival of Station Transformer for Station Auxiliary supply at Balimela HEP.

It was suggested in earlier meetings for revival of station supply for Balimela HEP from Balimela Grid S/S.

In the last meeting, OHPC stated that revival of station supply from Balimele 220/33 kV S/S will be done by end of January’ 2016.

OHPC may update.

D.5: Prolonged outage of transmission elements and tentative revival dates

The tentative revival dates of transmission elements are updated in the last meeting are as follows:

| Sl.No | Name of transmission element | Reason of outage | Probable date of revival |
| --- | --- | --- | --- |
| 1 | 220kV Jayanagar-Theruvali ckt-III breaker | Breaker already erected but not commissioned. Isolator problem | December 2015 |
| 2 | 220/132 kV, 100 MVA Auto-II at Duburi |  | Spares received. Work will be started soon. |
| 3 | 220/132 kV, 100 MVA Auto-I, Bhadarak |  | Filtration under process. Expected by Dec’15 |

C.G.M. (O&M) may please update the status.

D.6: Communication issues

- Installation of communication equipment by CGPs / Industries.

The status of data communication from CGPs as deliberated in the last meeting is as follows

| Sl. No | Name of CGP | Present status |
| --- | --- | --- |
| 1 | M/s IFFCO, Paradeep | Outdoor commissioning work completed. RTU was locally tested. After replacement of the faulty CVT data will be integrated. |
| 2 | M/s MSP Mettalicks | PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited. |
| 3 | M/s NINL, Duburi | M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. |
| 4 | M/s Adhunik Metalliks | Work order placed with ABB for supply of RTU. |
| 5 | M/s Rohit Ferrotech | PLCC established and inspection by Telecom Engineers completed. Data base has already been prepared by OPTCL. |
| 6 | M/s Vedanta Ltd. (IPP), Jharsuguda | Generators data remains Suspect most of the times. |

OPTCL may also approach OERC in this regard.

GCC / O&M / Sr. G.M. (Telecom.) may please deliberate.

- Interruption of SCADA.

It is noticed that there is frequent interruption of SCADA System, resulting problem in real time operation. Action may be taken to avoid such frequent interruption of SCADA.

In the last meeting, Sr. G.M (Telecom) stated that Powergrid link between Rourkela-Kaniha is being used for data transfer. The link is not healthy due to heavy fibre loss. Powergrid have proposed to upgrade the existing SDH equipment to STM16. Work order has already been awarded.

Sr. G.M. (Telecom) stated that Powergrid will complete the work by 1st week of December’2015

Sr. G.M. (Telecom) may please update the status.

D.7. Islanding Scheme of Ib TPS

The islanding scheme for IbTPS has already been commissioned but not functioning due to non- incorporate the trip commands to the breakers at Budhipadar from the Islanding Relay. This has already been discussed in the 81st PSOC meeting, wherein Telecom wing of OPTCL assured to complete the optical fibre link, provided IbTPs allow for working in their premises. Ib TPS had also agreed to allow them. The link is yet to be completed yet.

In the last meeting, Sr. G.M. (Telecom) stated that all works have been completed. It was decided that Sr. G.M (Telecom) shall intimate the same to Ib TPS and mark a copy to ERPC.

Sr. G.M. (Telecom) / Ib TPS may please update the status.

D.8: Display of dashboard data.

The status of lease line of all Discoms as deliberated in the meeting are as detailed.

| Sl. No | Dist. Utility | Status of leased line | Remarks |
| --- | --- | --- | --- |
| 1 | CESU | Already connected. RVDU commissioned | Data display available |
| 2 | WESCO | Already connected. RVDU commissioned | Data display available |
| 3 | NESCO | Already connected. RVDU commissioned | Data display available |
| 4 | SOUTHCO | Already connected. RVDU commissioned | Data display available |

It was reported by Discoms that the data of RVDU and Dashboard data are not matching. Also the RVDU data are remaining in hanging conditions. It was decided in the last meeting that Telecom and IT may collect feedback from Discoms and rectify the problems.

CGM (IT) / Sr. G.M (Telecom) / SLDC / All Dist. Utilities may please update the status.

D.9: Web based drawal / generation scheduling.

SLDC is going to implement web based drawal / generation scheduling for Dist. Utilities and State generating stations including IPPs and CGPs soon. A demo has been organized on 29.07.15.

In the last meeting, CGM (IT) stated that, web based generation scheduling module for State generating stations has been already been developed by IT wing. Modules for Discom and CGP / IPP shall be made available before the next PSOC meeting. After approval by the stake holders the same shall be go live from September’15. All Users were requested to forward their respective schedule in the prescribed format.

In the last meeting IT representative deliberated that SLDC shall finalize the date for one day demonstration cum training programme at SLDC for web base scheduling. SLDC has written a letter to IT to make a demonstration at SLDC prior to finalization of the training programe.

CGM (IT) / SLDC may deliberate.

D.10: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

The work for Automatic Meter Reading (AMR) for all the interface points is in progress. Whether these data will be received on real time basis so that these can be incorporated in the dashboard for monitoring of net drawal by Discoms.

CGM (IT) may deliberate.

D.11: DISCOM Issues

CESU

A.In the last meeting, it was decided that CESU shall approach O&M through a meeting to resolve bilateral issues. The discussion in the meeting may be placed in the next PSOC meeting.

B.

- Non-acceptance of downward revision by SLDC in case of Technical minimum generation, if accepted after 4 block periods,

- Replacement of fixed data by variable data in SLDC dashboard,

- Display of Khurda drawal data in case of power drawal from Mendhasal,

- Installation of 2nd 20MVA transformer at Mendhasal to meet full load of Jatani,

- Up-gradation of conductor size of Narendrapur-Khurda ckt.

- Low voltage problem at Khurda sub-station,

- Minimization of interruption of traction supply within CESU area.

- Provision of three nos. of 33kV bays at Paradeep sub-station, replacement of 33kV CT of 600/1 ratio by 800/1 of Tirtol feeder at Paradeep sub-station, Change of CT ratio for 132kV Gorakhnath traction ckt.

CGM (IT) / Sr. G.M. (Telecom.) / CGM (O&M) / CESU may please deliberate.

PART E: OPERATIONAL PLANNING

E.1: Handing over of 2 nos 132 kV bays at 400/220/132kV Kuchei (Baripada) Grid S/s in Odisha.

As agreed by JUSNL to spare 2 Nos of 132 kV bays at Baripada (PG) for use of OPTCL, in the last meeting it was decided that CGM (Const) to explore for connectivity of OPTCL S/Ss with the bays.

CGM (Const.) may deliberate.

E.2:  Commissioning status of New Transmission elements.

The status of commissioning of new transmission elements is as follows:

| Sl. No | Transmission element details | Present Status |
| --- | --- | --- |
| 1 | Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line | Work has already been started. Expected to be completed by March 2016. |
| 2 | Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt | Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal, which is under progress. |
| 3 | Commissioning of 400 kV Ib-Meramundali D/C line. | 400kV Ib-Lapanga-Meramundali ckt-1 will be charged by 15th December’2015. 2nd ckt is expected to be charged by March’2016. |
| 4 | Commissioning of 220 kV Bidanasi-Cuttack line | Work in progress and expected to be completed by March 2016. |
| 5 | Commissioning of 220/132 kV Cuttack S/S | Work in progress and expected to be completed by December 2015. |
| 6 | Commissioning of 132 kV Baripada (PG)-Jaleswar line | Work has already been started, which will be completed by December 2015. |
| 7 | Commissioning of 220/132 kV Kesinga S/S | Work under progress. Expected by September 2016. |
| 8 | Connectivity to Keonjhar PG | Proposal is mooted to be placed in the BoD meeting for connecting the proposed 220 / 33 kV Keonjhar S/S and with Turumunga S/S through 2 Nos. 220 kV ckts each. |
| 9 | LILO of 220 kV Burla - Bolangir line (one ckt) at Bolangir(PG) | Work has been started. Expected to be completed by December, 2015 |
| 10 | 220 kV Bolangir –Kesinga D/C line and LILO of one ckt at Bolangir(PG). | 220kV Bolangir - Kesinga D/C line is under construction. It is proposed to connect Bolangir (PG) through LILO arrangement of one ckt. Land dispute is yet to be resolved. |

Status of Discom’s action plan for power drawal from the S/Ss expected to be commissioned in near future.

| Sl. No | Name of the sub-station | Probable month of commissioning | Name of DISCOM | Action taken by Discoms |
| --- | --- | --- | --- | --- |
| 1 | 132/33kV, 2x20 MVA Khajuriakota | December’15 | CESU | By July’15 |
| 2 | 132/33kV, 2x40 MVA Kalunga | Charged on 03.11.15 | WESCO Utility |  |
| 3 | 220/33kV, 2x20 MVA Banei | Dec’15 | WESCO Utility |  |
| 4 | 132/33kV, 2x20 MVA Padmapur | Dec’15 | WESCO Utility |  |
| 5 | 132/33kV, 2x20 MVA Udala | Dec-15 | NESCO Utility | Line existing |
| 6 | 132/33kV, 2x20 MVA Somanathpur | Sept’15 | NESCO Utility | 33 kV feeder existing. |

CESU stated that action is being taken for construction of 33/0.4 kV S/S at Mendhasal to avail power supply for Mendhasal area.

In the last meeting, it was suggested that WESCO shall explore the work for diversion of 11kV line at Sarsmal (Jharsuguda) and connecting 33 kV feeders with Lapanga Grid.

The progress in this regard may be placed in the next meeting.

All DISCOMS may update the status / CGM(O&M) & CGM(Const.) may please deliberate.

E.3: Energy Metering at Hydro stations.

In the last meeting, OHPC stated that billing for all the OHPC stations except Upper Kolab is being done from the newly installed energy meters. The energy meters at Upper Kolab are showing problem, which may be rectified soon.

GRIDCO / OHPC / O&M may please deliberate.

E.4: TTPS Issue.

Implementation of Feeder Metering

In the last meeting TTPS deliberated that all the meters were tested & calibrated by the STL on 09.10.2015. The 132kV CTs for TTPS-Duburi-1 have been replaced. Further, as per the PPA dated 08.03.1995, the energy meters are to be installed at GT end. Since the meter locations will be shifted to feeders, the corresponding clause in the PPA is required to be amended. Accordingly, the proposal has been sent to the competent authority of NTPC for approval.

As per the decision by Gridco the feeder metering has been implemented with effect from 1st October. SLDC has prepared the Deviation charge bill considering the feeder meter data for the month of October.

TTPS in their letter No.045/GGM/TTPS, Dated. 20.11.2015 addressed to CGM (PP) Gridco pointed out that, as per clause 7(1), 1st proviso of CEA (Installation and operation of Energy meters) Regulation, 2006 as amended in 2010 “ for existing stations the location of Main, Check and Standby meters shall not be changed unless permitted by the Authority”.

In the present case, for the first time, energy meters have been installed at the interface points, which should have been installed earlier, without changing the position of the existing meters. As such the regulation as mentioned by TTPS is not applicable. However the existing meters will be treated as standby meters.

In the last meeting, TTPS stated that they have written to CEA for clearance to the feeder meter installation, in view of which the metering may be considered from 1st November’ 2015. Director (Commerce) stated that installation of feeder meters will be informed to CEA by Gridco and NTPC.

It is noticed that there are considerable time delay to the tune of 0.5 - 8 hours between the Generator meter & feeders resulting wide mismatch of both the meter data, which calls for time synchronization.

GRIDCO / OPTCL/ TTPS / SLDC may please deliberate.

E.5: Major Events in the month of November’15

04.11.2015: 132/33 kV, 1 X 40 MVA Kalugaon S/S charged.

07.11.2015: 132/33 kV, 12.5 MVA Transformer No.-3 at Paralakhemundi S/S charged.

13.11.2015: 132/33 kV, 20 MVA Transformer No.-1 at Konark S/S charged.

26.11.2015: 132/33 kV, 12.5 MVA Transformer No.-3 at Kamakshyanagar S/S charged.

27.11.2015: 132kV Rajgangpur-OISL ckt. charged.

E.6: Important Grid Incidences during the month of November’15.

Important Grid Incidences during the month of November’15.

On 16.11.2015 at 08:00 hrs 220 kV TTPS-Joda Ckt-I & II tripped pulling out  #5 & # 6 along with  both Autos at TTPS. All 220 kV feeders emanating from TTPS also pulled out.

E.7: Outage of major transmission Elements during the month of Novemober’15. (above 10 hrs).

Outage of major transmission elements above 10 hours during the month of Nov-15 is as detailed.

| Sl No | Transmission lines | Tripping Dt/time | Restoration Dt/time | Reason |
| --- | --- | --- | --- | --- |
| 1 | 132 kV Narendrapur-Khurda Ckt | 06.11.15 17:54 | 07.11.15 16:42 | ‘B’ ph jumper snapped at Loc. No-70. |
| 2 | 132 kV TTPS-Jabamayee Ckt | 13.11.15 17:20 | 14.11.15 13:26 | ‘Y’ ph jumper snapped at Loc. No-121 |

Major outages are due to jumper snapping.

C.G.M. (O&M) may please deliberate.

E.8:  Review of Outage Program of State Generators / Transmission elements for the month of December’2015:

Tentative Outage programme for State Generators for the month of November’2015 are as follows:

| Sl. | Station | Unit | Period | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Burla | # 2 # 4 # 6 | 15.01.16 to 15.06.16 25.01.16 to 24.02.16 17.02.14 to continue | Capital Maintenance Annual Maintenance Programming for R, M & U |
| 2 | Chiplima | #2 #3 | 16.12.15 to 04.01.16 15.02.14 to continue | Annual Maintenance Programming for R & M |
| 3 | Balimela | # 1 # 2 # 6 | 31.01.13 to continue 16.12.15 to 10.01.16 16.01.16 to 10.02.16 | TGB problem and started R,M & U Annual maintenance Annual maintenance |
| 4 | Upper Kolab | # 1 | 29.07.15 to 31.01.16 | Capital Maintenance |
| 5 | Rengali | # 5 | 02.01.16 to 31.01.16 | Annual maintenance |
| 6 | Upper Indravati | # 3 | 23.11.15 to 30.04.16 | Capital Maintenance |

OHPC / SLDC may deliberate.

E.9: Generation Program for the month of January’16.

Generation schedule for the month of January’16 furnished by OHPC are given below.

| Name of Hydro Gen. Station | Generation Programme (MW) | Reservoir Level as on 15.11.14 | Reservoir Level as on 15.11.15 | MDDL | High Flood Reservoir Level |
| --- | --- | --- | --- | --- | --- |
|  | Jan’16 (1st fortnight) | Jan’16 (2nd fortnight) |  |  |  |  |
| HPS, Burla | 40+30 | 40+30 | 629.31ft | 625.56ft | 590 ft. | 630 ft. |
| Balimela | 80 | 80 | 1514.40ft | 1500.60ft | 1440 ft. | 1516 ft. |
| Rengali | 25 | 25 | 122.02mt 1.78mt mtr mt | 118.94mt mt | 109.72mtr | 123.5 mtr. |
| U.Kolab | 100 | 100 | 856.90mt mt | 855.87mt | 844 mtr | 858 mtr. |
| U. Indravati | 90 | 90 | 640.43mt | 634.86mt mt | 625mtr | 642 mtr |
| MKD (O/D) | 30 | 30 | 2748.50ft | 2747.25ft | 2685 ft. | 2750 ft. |
| TOTAL | 395 | 395 |  |  |  |  |

Members may discuss.

E.10: RSP (SAIL), Rourkela Issue.

- Review of relay settings of Tarkera grid to RSP 220kV feeders

- Clearance for construction of two 220kV bays at Tarkera grid sub-station and construction of 220kV D/C line.

In the last meeting, CGM (O&M) stated that WESCO has not intimated the proposal regarding enhancement of contract demand RSP. Field inspection report for feasibility of 220 kV bay at Tarkera is yet to be received.

RSP / O&M / WESCO may please deliberate

E.11:  Operating procedure for Odisha System.

As per provision in the Regulation 5.1(4) of Odisha  Grid Code, the draft Operating Procedure for Odisha System has been prepared and uploaded in the SLDC site (path: Document    information). Members are requested and forward their comments / suggestions to SLDC before 15th December2015. No comments has been received from Members except OHPC. The final Operating Procedure shall be placed in the next meeting.

Members may discuss

E.12: Anticipated power generation and demand for the month of January’2016.

| Sl. No | Discom | Average | Peak |
| --- | --- | --- | --- |
| 1 | CESU | 750 | 1100 |
| 2 | WESCO | 850 | 1000 |
| 3 | NESCO | 600 | 800 |
| 4 | SOUTHCO | 350 | 500 |
| 5 | Total | 2550 | 3400 |
|  | Demand including Loss | 2700 | 3600 |
| Availability |  |  |
|  | Hydro | 395 | 1050 |
|  | State Thermal | 750 | 750 |
|  | IPP, small hydro &RE | 750 | 750 |
|  | ISGS share | 900 | 900 |
|  | CGP support (OA) | 100 | 150 |
| 6 | Total availability | 2905 | 3600 |
| 7 | Surplus / Deficit | 205 | 0 |

PART F: OTHER ISSUES

F.1:  Date and Venue of the next (93rd) PSOC meeting.