Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

# Agenda

for

139th Power System Operational Co-ordination Meeting

## Date: 22.11.2019

### Venue: Power Training Center, Chandaka, Bhubaneswar

Odisha Power Transmission Corporation Ltd. Bhubaneswar.

Agenda for 139th PSOC Meeting to be held on 22.11.2019 at OPTCL Power Training Center, Chandaka, Bhubaneswar

- Confirmation of the minutes of the 138th PSOC Meeting held on 25.10.2019

The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2019/3606 (49) dated 08.11.2019 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there are no comments, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)

B   :  Grid Performance for the month of October’2019

C.1: Status of projects funded under PSDF scheme

C.2: Implementation of Automatic Demand Management Scheme.

C.3: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s

C.4: Bypassing arrangement of LILO of 400kV Lines at Angul

C.5: Update on status of telemetry

C.6: Mock Black start exercises in Eastern Region

C.7: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC.

C.8: Implementation of Automatic Generation Control in Eastern Region--ERLDC

C.9: Submission of data in MERIT Order portal--CEA

C.10: Data for preparation Load Generation Balance Report (LGBR) of ER for the year 2020-21

C.11: Monitoring of Next Six-Month New Element Integration in OCC and Its Update on Monthly Basis --ERLDC

C.12: Auxiliary  power consumption by Powergrid  Substations--GRIDCO

C.13: Review of the PSS Tuning of Generators in Eastern Region --ERLDC

C.14: Long term outage of transmission elements

C.15: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.

D.3: Data communication from newly commissioned RE sources connected at 132 kV- SLDC

D.4: Despatch Scheduling for RE Generation.

D.5: Information regarding RE Sources for RPO Compliance monitoring.

D.6: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.7: Collection of tie-line meter data

D.8: Repair of OPGW, Groung wire and doubling of jumpers & summation meters for 220 kV RSP DC lines. – RSP Agenda

E.1: Commissioning status of New Transmission elements.

E.2: HT metering at DISCOM interface points.-SLDC.

E.3: Major Events in the month of October’19

E.4: Important grid incidences during the month of October’19.

E.5: Outage of major transmission Elements during the month October’19. (above 10 hrs).

E.6: Prolonged outage of Transmission elements

E.7: Review of Outage Program of State Generators for the month of December’2019

E.8: Generation Program for the month of December’2019.

E.9: Anticipated power generation and demand for the month of December’2019.

F.1: Date and Venue of the next (140th) PSOC meeting.

PART B: GRID PERFORMANCE

B. Review of Grid Performance for the month of October’19.

- Frequency:

Hourly frequency variation for the month of October’19.

| Month | % of time frequency remained | Average |
| --- | --- | --- |
|  | <49.00 | 49.00-49.70 | 49.70-49.90 | 49.90-50.05 | >50.05 |  |
| Aug’19 | 0.00 | 0.10 | 7.29 | 71.69 | 20.92 | 49.99 |
| Sept’19 | 0.00 | 0.08 | 4.56 | 74.71 | 20.64 | 50.00 |
| Oct’19 | 0.00 | 0.00 | 2.97 | 75.24 | 21.79 | 50.00 |

Maximum & Minimum frequency during the month of Sept’19 & Oct’19.

| Month | Freq (Hz) | Date | Time |
| --- | --- | --- | --- |
| Sept’19 | Maximum –50.20 | 29.09.19 | 13:30 Hrs |
|  | Minimum – 49.70 | 18.09.19 | 18:30 Hrs |
| Oct’19 | Maximum –50.18 | 26.10.19 | 13:00 Hrs |
|  | Minimum – 49.74 | 24.10.19 | 07:00 Hrs |

- Grid Demand up to the month of October’19

| Month | Max. Consumption | Demand | Maximum Demand | Minimum Demand |
| --- | --- | --- | --- | --- |
|  | MU | Date | MU | Avg. (MW) | MW | Date | Time | MW | Date | Time |
| Apr’19 | 113.14 | 05.04.19 | 2786 | 3869 | 5151 | 04.04.19 | 20:00 | 2689 | 20.04.19 | 05:00 |
| May’19 | 102.99 | 19.05.19 | 2638 | 3545 | 4635 | 18.05.19 | 24:00 | 1720 | 03.05.19 | 18:00 |
| June’19 | 105.24 | 11.06.19 | 2653 | 3684 | 4790 | 11.06.19 | 23:00 | 2556 | 13.06.19 | 06:00 |
| July’19 | 106.80 | 15.07.19 | 2744 | 3688 | 4899 | 15.07.19 | 21:00 | 2640 | 02.07.19 | 04:00 |
| Aug’19 | 105.41 | 21.08.19 | 2924 | 3930 | 4901 | 16.08.19 | 21:00 | 3161 | 08.08.19 | 05:00 |
| Sept’19 | 107.91 | 19.09.19 | 2780 | 3862 | 4969 | 18.09.19 | 20:00 | 2982 | 30.09.19 | 05:00 |
| Oct’19 | 89.89 | 12.10.19 | 2519 | 3386 | 4385 | 20.10.19 | 19:00 | 2430 | 25.10.19 | 03:00 |
| Oct’18 | 116.85 | 05.10.18 | 3147 | 4230 | 5270 | 02.10.18 | 19:00 | 3033 | 12.10.18 | 07:00 |

- Voltage Profile of 220 kV Buses in OPTCL system for the month of: October’19

| SUBSTATION | MAX VOLTAGE (KV) | DATE | TIME | MIN VOLTAGE (KV) | DATE | TIME |
| --- | --- | --- | --- | --- | --- | --- |
| Atri | 228.92 | 24-10-2019 | 14:00 | 223.38 | 04-10-2019 | 20:15 |
| Balasore | 233.71 | 25-10-2019 | 02:15 | 218.93 | 03-10-2019 | 18:30 |
| Barkote | 231.17 | 24-10-2019 | 14:00 | 225.63 | 09-10-2019 | 11:30 |
| Bargarh | 228.80 | 22-10-2019 | 14:30 | 215.93 | 10-10-2019 | 09:00 |
| Bhadrak | 230.48 | 24-10-2019 | 15:15 | 214.89 | 03-10-2019 | 18:30 |
| Bhanjanagar | 236.25 | 24-10-2019 | 04:15 | 221.07 | 03-10-2019 | 18:45 |
| Bidanasi | 234.92 | 25-10-2019 | 04:00 | 222.40 | 03-10-2019 | 18:00 |
| Bolangir | 237.23 | 25-10-2019 | 05:00 | 218.70 | 16-10-2019 | 16:15 |
| Budhipadar | 231.52 | 08-10-2019 | 14:15 | 226.32 | 18-10-2019 | 17:45 |
| Chandaka | 232.79 | 24-10-2019 | 04:15 | 215.24 | 03-10-2019 | 18:30 |
| Cuttack | 233.31 | 24-10-2019 | 04:15 | 215.06 | 03-10-2019 | 18:30 |
| Duburi Old | 231.34 | 25-10-2019 | 02:15 | 221.76 | 04-10-2019 | 18:45 |
| Duburi New | 239.66 | 25-10-2019 | 02:15 | 229.50 | 04-10-2019 | 18:45 |
| Jayanagar | 239.60 | 26-10-2019 | 04:15 | 231.17 | 15-10-2019 | 18:15 |
| Joda | 235.10 | 06-10-2019 | 15:00 | 223.61 | 04-10-2019 | 19:45 |
| Katapalli | 229.03 | 25-10-2019 | 04:45 | 222.34 | 19-10-2019 | 16:00 |
| Lapanga | 232.56 | 08-10-2019 | 14:00 | 228.11 | 08-10-2019 | 19:30 |
| Laxmipur | 239.83 | 01-10-2019 | 14:15 | 228.40 | 03-10-2019 | 18:45 |
| Mendhasal | 236.14 | 24-10-2019 | 04:15 | 219.39 | 03-10-2019 | 18:45 |
| Meramundali | 227.76 | 25-10-2019 | 04:00 | 205.71 | 03-10-2019 | 11:45 |
| Narendrapur | 234.64 | 25-10-2019 | 14:30 | 215.29 | 03-10-2019 | 18:45 |
| Nayagarh | 235.62 | 24-10-2019 | 04:15 | 203.92 | 03-10-2019 | 12:30 |
| Paradeep | 231.11 | 24-10-2019 | 06:15 | 209.17 | 06-10-2019 | 13:45 |
| Tarkera | 224.42 | 02-10-2019 | 15:15 | 218.58 | 02-10-2019 | 19:15 |
| Theruvali | 237.75 | 23-10-2019 | 11:15 | 224.36 | 01-10-2019 | 18:45 |
| Rengali | 228.92 | 24-10-2019 | 14:00 | 223.38 | 04-10-2019 | 20:15 |

The maximum Voltage of 239.83 kV occurred at Laxmipur 220 kV bus., while Nayagarh 220 kV bus has experienced the minimum Voltage of 203.92 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Mendhasal, Meramundali and New Duburi bus during the month of Oct’2019 are indicated in System performance presentation.

Members may discuss.

- Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of Oct– 2019.

- DISCOM Drawal up to the month of October’19

| Name of DISCOM | Month | Approved Energy Drawal Prorated for the month (MU) | Scheduled Energy (MU) | Actual Energy Drawal ( MU) | Open Access Import Schedule (MU) | Net Energy Drawal ( MU) | Overdraw (MU) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 | 2 | 3 | 4 | 5=(3-4) | 6=(5-2) |
| CESU | Apr’19 | 798 | 760.542 | 857.404 | 18.345 | 839.059 | 78.517 |
|  | May’19 | 770.33 | 664.438 | 689.035 | 16.166 | 672.869 | 8.431 |
|  | June’19 | 798 | 758.651 | 793.853 | 17.431 | 776.422 | 17.771 |
|  | July’19 | 770.33 | 778.505 | 798.994 | 15.847 | 783.147 | 4.642 |
|  | Aug’19 | 770.33 | 745.852 | 785.057 | 14.196 | 770.861 | 25.009 |
|  | Sept’19 | 798 | 766.486 | 755.33 | 15.336 | 739.994 | -26.492 |
|  | Oct’19 | 770.33 | 739.392 | 740.459 | 16.154 | 724.305 | -15.087 |
| WESCO | Apr’19 | 635 | 649.188 | 856.374 | 149.999 | 706.375 | 57.187 |
|  | May’19 | 604.71 | 703.036 | 841.28 | 100.32 | 740.96 | 37.924 |
|  | June’19 | 635 | 656.64 | 789.792 | 110.175 | 679.617 | 22.977 |
|  | July’19 | 604.71 | 670.083 | 835.876 | 143.639 | 692.237 | 22.154 |
|  | Aug’19 | 604.71 | 637.41 | 1043.79 | 423.111 | 620.682 | -16.728 |
|  | Sept’19 | 635 | 650.296 | 908.15 | 281.184 | 626.966 | -23.33 |
|  | Oct’19 | 604.71 | 605.866 | 678.503 | 71.157 | 607.346 | 1.48 |
| NESCO | Apr’19 | 517 | 478.905 | 600.692 | 99.608 | 501.084 | 22.179 |
|  | May’19 | 521.48 | 508.934 | 629.852 | 89.858 | 539.994 | 31.06 |
|  | June’19 | 517 | 490.244 | 607.403 | 105.15 | 502.253 | 12.009 |
|  | July’19 | 521.48 | 532.112 | 660.208 | 131.831 | 528.377 | -3.735 |
|  | Aug’19 | 521.48 | 493.554 | 627.779 | 128.157 | 499.622 | 6.068 |
|  | Sept’19 | 517 | 451.669 | 557.042 | 99.737 | 457.305 | 5.636 |
|  | Oct’19 | 521.48 | 446.652 | 556.344 | 105.563 | 450.781 | 4.129 |
| SOUTHCO | Apr’19 | 331 | 303.576 | 334.361 | 0 | 334.361 | 30.785 |
|  | May’19 | 310.85 | 320.055 | 336.003 | 0 | 336.003 | 15.048 |
|  | June’19 | 331 | 318.393 | 324.819 | 0.116 | 324.703 | 6.31 |
|  | July’19 | 310.85 | 315.891 | 305.83 | 0.061 | 305.769 | -10.122 |
|  | Aug’19 | 310.85 | 291.711 | 296.609 | 0 | 296.609 | 4.898 |
|  | Sept’19 | 331 | 298.482 | 290.17 | 0.007 | 290.163 | -8.319 |
|  | Oct’19 | 310.85 | 285.153 | 283.453 | 0.263 | 283.19 | -1.963 |

The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali.

Members may please discuss.

- Energy Generation / Import up to the month of October’19

Figures in MU

| Month | Thermal (TTPS+IbTPS) | OHPC & MKD | CGP Support | IPP Inj. | RE | ISGS | Total |
| --- | --- | --- | --- | --- | --- | --- | --- |
| April’19 | 588.681 | 538.473 | 308.480 | 263.019 | 29.852 | 1057.035 | 2785.540 |
| May’19 | 608.185 | 571.561 | 290.845 | 203.850 | 46.247 | 916.949 | 2637.637 |
| June’19 | 581.856 | 414.962 | 329.321 | 212.683 | 47.362 | 1066.419 | 2652.603 |
| July’19 | 566.902 | 407.505 | 363.839 | 198.433 | 46.030 | 1171.210 | 2753.919 |
| Aug’19 | 359.551 | 836.840 | 345.534 | 56.723 | 46.535 | 1278.578 | 2923.761 |
| Sept’19 | 828.709 | 808.759 | 328.938 | 75.013 | 44.608 | 694.453 | 2780.479 |
| Oct’19 | 931.846 | 815.124 | 201.462 | 170.221 | 43.395 | 357.406 | 2519.453 |
| Total | 4465.728 | 4393.224 | 2168.420 | 1179.942 | 304.029 | 6542.050 | 19053.392 |

- Drawal of Machhakund Power

The drawal of Machhakund power up to the month of October’19 are as detailed:

| Month | Total Generation | Odisha Drawl | AP Drawl |
| --- | --- | --- | --- |
|  | MU | Avg (MW) | MU | Avg (MW) | MU | Avg (MW) |
| Apr’19 | 53.168 | 73.84 | 24.896 | 34.58 | 26.401 | 36.67 |
| May’19 | 60.577 | 81.42 | 26.811 | 36.04 | 31.821 | 42.77 |
| June’19 | 52.203 | 72.50 | 22.395 | 31.10 | 30.840 | 42.84 |
| July’19 | 59.779 | 80.35 | 26.579 | 35.73 | 31.116 | 41.82 |
| Aug’19 | 53.318 | 71.66 | 24.773 | 33.30 | 27.139 | 36.48 |
| Sept’19 | 52.348 | 72.706 | 23.869 | 33.151 | 26.276 | 36.494 |
| Oct’19 | 51.532 | 69.263 | 23.229 | 31.222 | 25.936 | 34.860 |
| Total | 382.925 |  | 172.552 |  | 199.529 |  |

In the 136th PSOC meeting Southco stated that Dasmantpur feeder in expected to be charged today i.e on 21.08.2019.

Sr.GM (O&M), Zone –I suggested to explore the following link lines for providing adequate matching load in Machhakund system.

- Connecting Patangi S/S or Proposed Lamtaput S/S with Podagada S/S through 132 kV link.

- Providing Sunabeda S/S area load in Machhakund system

- Modification of Jayanagar S/S to accommodate Jayanagar load

In the 137th PSOC meeting, SOUTHCO stated that 33 kV Dasmantpur feeder did not stand after charging. Insulators are being changed by the contractor. Sr. GM (Const) stated that 132 kV Patangi-Podagada line is under construction and expected by March’2010. He also suggested to utilize 132 kV NALCO-Sunabeda line to feed Sunabeda area load from Machhakund system by bus splitting.

In the 138th PSOC meeting, SOUTHCO stated that insulator changing of Dasmantpur feeder is under progress. It was suggested that GRIDCO may convene a meeting with PMU for early restoration of the feeder, so that, more matching load can be provided in Machhakund system.

GRIDCO / O&M/SLDC/SOUTHCO may deliberate.

- Under Frequency Relay operation in OPTCL System during the month of October’19.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of October’19.

- Status of Open Access applications up to the month of October’2019

The status of different types of Open Access applications received and disposed by SLDC is as tabled.

| Sl. No | Month | No of Applications received | No of Applications Disposed | No of App. Rejected | MU |
| --- | --- | --- | --- | --- | --- |
|  |  | Intra-State | Inter-State | Total | Intra-State | Inter-State | Total |  |  |
|  |  |  | Bilateral | PXI |  |  | Bilateral | PXI |  |  |  |
|  |  |  | ST | MT/ LT |  |  |  | ST | MT/ LT |  |  |  |  |
| 1 | April’19 | 48 | 100 | 0 | 24 | 172 | 48 | 100 | 0 | 24 | 172 | 0 | 522.98 |
| 2 | May’19 | 21 | 92 | 0 | 29 | 142 | 21 | 92 | 0 | 29 | 142 | 0 | 487.30 |
| 3 | June’19 | 49 | 106 | 0 | 32 | 187 | 49 | 106 | 0 | 32 | 187 | 0 | 641.01 |
| 4 | July’19 | 94 | 60 | 0 | 28 | 182 | 94 | 60 | 0 | 28 | 182 | 0 | 726.36 |
| 5 | Aug’19 | 114 | 132 | 0 | 38 | 284 | 110 | 132 | 0 | 38 | 284 | 4 | 904.48 |
| 6 | Sept’19 | 66 | 122 | 0 | 58 | 246 | 66 | 122 | 0 | 58 | 246 | 1 | 576.64 |
| 7 | Oct’19 | 42 | 43 | 0 | 34 | 119 | 42 | 43 | 0 | 34 | 119 | 0 | 360.33 |
|  | Total | 392 | 612 | 0 | 209 | 1213 | 392 | 612 | 0 | 209 | 1213 | 5 | 4219.10 |

PART C – Issues discussed in the 163rd OCC meeting of ERPC on 15.11.2019

C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:

| Sl No | Name of Constituent | Name of Project | Date of approval from PSDF | Target Date of Completion | PSDF grant Approved (in Rs.) | Amount Drawn till date (in Rs.) | Status as updated in 129th meeting |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 4 | OPTCL | Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies. | 11.05.15 | 31.03.20 | 162.5 Cr. Total expenditure may not exceed Rs. 68 Cr. | 38.09Cr. Received Rs. 8.00 Cr on 28.03.19 | Work almost completed. |
| 7 |  | Implementation of OPGW based reliable communication at 132kV and above substations | 15.11.2017 |  | 51.22 Cr | 2.56 Cr received as 10 % DPR. Claimed for 20 %. | Order placed. Expected by Nov’19. Inspection under process. |
| 13 | OHPC | Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations |  | U.Kolab- March 19 Balimela- Feb 2019 U.Indravati-Jan 19 Burla-Nov18 Chiplima Dec 2018 | 22.35 Cr. | 2.674 Cr | Placed work order for Balimela. PO for other units amounting Rs. 12.79 Crs placed. Order under process. |
| Projects under process of approval: |
|  | OPTCL | Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal, Meramundali & New Duburi for VAR control & stabilisation of system voltage | 27-07-18 |  | 31.94 Cr Ested. Cost. Approved amount 30.26 Cr. Grant amount 27.23 Cr. | Rs.2.72 Cr received as 10% of DPR. Retendering under process. | Agreement signed and sent to NLDC for signature. Retendering under process. |
| Projects recently submitted: |
|  | OPTCL | Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha | 22-12-17 Date of submission |  | 3.26 Cr Estt cost. 2.93 Cr recommended by Appraisal committee. |  | CERC approval received. Tendering under process. |
|  | OPTCL | Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep). | 12.03.2018 Date of submission |  | 41.1 Cr Estt cost | 10% of DPR to be asked. | Project approved. Tender to be floated after revision of specification. Agreement will be sent to NLDC after signature of Govt. |

CGM (Const)/CGM (O&M) / OHPC may deliberate

C.2: Implementation of Automatic Demand Management Scheme

The latest status along with proposed logic as follows:

| Sl. No | State /Utility | Logic for ADMS operation | Implementation status/target | Proposed logic (if different from under implementation logic |
| --- | --- | --- | --- | --- |
| 1 | Odisha | 1. System Frequency < 49.9 Hz 2. Odisha over-drawl > 150 MW 3. DISCOM over-drawl > (40 MW) | 10 Months Sent for PSDF approval | Logic 2 and 3 is AND or OR, in case it is AND then ADMS may not operate when DISCOMs are in schedule but GRIDCO is over drawing due to less generation at State embedded generators. |

In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.

In the 123rd PSOC meeting SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval.

In the 133rd PSOC meeting a committee was constituted with representatives of DISCOM, Telecom, IT & SLDC.

A meeting of the Committee was held on Dt. 06.07.2019. SLDC made a presentation on the logic and methodology to be adopted for the ADMS. The technical specifications prepared by SLDC were shared among the concern wings of OPTCL for their views. The specification will be finalized on receipt of the same. The DISCOMs were requested to update the list of feeders and group considering the present network configuration. On finalization of the above, the tendering process will be taken up by CPC wing of OPTCL as already approved by CMD, OPTCL.

The Technical & Commercial specification have been approved by the committee and forwarded to CPC for processing the Tender.

In the 137th PSOC meeting, it was suggested by CGM (Telecom) that BoQ & SoQ in different formats need to be matched and technical sanction shall be made by SLDC and forwarded to CPC for necessary action.

In the 138th PSOC meeting SLDC stated that technical sanction has been done and forwarded to CPC for tendering.

SLDC may deliberate

C.3: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.

In 138th PSOC meeting the status has been updated as follows:

| Sl. | Name of the transmission line | Completion schedule |
| --- | --- | --- |
| 1. | 2 X 315MVA 400/220kV Bolangir S/s |
| a. | LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S. | Construction of 220 kV Sadeipali- Kesinga line has started. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by March’20. |
| 2. | 400/220 kV Keonjhar S/S. |
| a. | Keonjhar (PG)-Keonjhar (220/33 kV) & 220 kV D/C line | 220 kV S.C line and Keonjhar S/S (220/33 kV), 2x20 MVA charged on 31.12.2018. 2nd ckt; charged on 03.08.2019. |
| b. | Keonjhar (PG)-Turumunga (220/132 kV) & 220 kV D/C Line. | By 2021. Order placed. |
| 3. | 400/220 kV Pandiabil Grid S/s |
| a. | Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C | December’2019 |

C.GM (Cont) / CGM (Telecom) may update.

C.4: Bypassing arrangement of LILO of 400kV Lines at Angul

LILO of Meramundali-Bolangir/Jeypore 400 kV S/C line and LILO of one Ckt of Talcher-Meramundali 400 kV D/C line has been done at Angul 765/400kV Sub-station. The bypass arrangement for these circuits is under implementation at Angul by Powergrid.

In 158th OCC, Powergrid informed that bypass arrangement would be completed by August 2019. OPTCL informed that 2nd circuit of 400 kV Meramundali-Mendhasal line would be commissioned

by 1st week of August 2019.

OPTCL informed that 2nd circuit of 400kV Meramundali-Mendhasal line would be commissioned by end of August 2019.

As per POWERGRID email dated 16th September, the anticipated date for commissioning of the LILO by-pass arrangements at Angul SS is by end of Oct’2019.

OCC advised POWERGRID to take urgent steps for commissioning of the bypass arrangement. Delay in implementation of the arrangement is causing loss of operational flexibility besides subjecting the grid to the risk of high fault current.

In the 137th PSOC meeting, DGM (Const) stated that 3rd ICT at Mendhasal in under testing. O&M stated that tree clearance has already been completed. After commissioning of the ICT, 400 kV Mendhasal-Meramundali 2nd ckt will be charged.

Const. wing stated that a committee has been formed to examine the oil sample test result for charging of the 3rd ICT at Mendhasal. A decision shall be taken after receiving the views of the Committee.

Powergrid informed that the bypassing arrangement would be completed by November’2019

O&M may update.

C.5: Update on status of telemetry

CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action. Major issues are given below:

xxxxxxx

Issues relating OPTCL Network:

Narsingpur data:

In the 132nd PSOC meeting CGM (Telecom) stated that survey work for Meramundali-Bhanjanagar line is under process. OPGW will be reached at site after completion of survey and preparation of drum schedule.

In the 134th meeting CGM (Telecom) stated that delivery of OPGW has already been started.

In the 135th PSOC meeting DGM (Telecom) stated that replacement of earth wire by OPGW in 220 kV Bhanjanagar-Meramundali is expected by December’2019

NALCO data: DGM (Telecom) stated that the vender list and rate will be provided to NALCO for placement of order by them.

In the 137th PSOC meeting, NALCO stated that the estimate has already been received from OPTCL (Telecom). Approval from higher authority in under process.

Telecom / NALCO may deliberate the status

C.6: Mock Black start exercises in Eastern Region – ERLDC

Schedule and tentative date for conducting mock black start exercise in OHPC stations is as tabled.

| Sl. | Name of Hydro Station | Schedule | Tentative Date | Schedule | Tentative Date |
| --- | --- | --- | --- | --- | --- |
|  |  | Test-I |  | Test-II |  |
| 1 | Upper Kolab | Last week of May-2019 | Done on 19th July19 | Last week of January 2020 |  |
| 3 | Rengali | 2nd week of June 2019 | Done on June’19 | Last week of November 2019 |  |
| 4 | U.Indravati | 3rd week of June 2019 | Done on June’19 | 2nd week of February 2020 |  |
| 6 | Balimela | 3rd week of October 2019 | Done on 17th July19 | 1st week of March 2020 | Dec’2019 |
| 9 | Burla | Last week of June 2019 | Done on 20th July’ 2019 | Last week of February 2020 | Dec’2019 |

In the 136th PSOC meeting, SLDC stated that while conducting mock Black start exercise for Upper Kolab and Upper Indravati HEPs Muniguda Traction feeder is getting interrupted. In view of the above, feeding of Muniguda Traction S/S from Theruvali S/S through a separate dedicate line may be examined.

In the 137th PSOC meeting, Sr. G.M (O&M), Zone-1 suggested to put Rayagada area load on Indravati for black start exercise. SLDC may develop the procedure accordingly.

The mock black start exercise for Indravati HEP was done on 7th November by extending Upper Indravati generation up to Aska through 220 kV Theruvali & Bhanjanagar bus section and 220 kV Theruvali-Bhanjanagar-Aska line.

SLDC / O&M/ OHPC may deliberate

C.7: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC

As a National Grid operator, POSOCO is continuously working for ensuring reliability and security of the Grid. With penetration of more and more renewable energy source the task is becoming complicated day by day.  An accurate dynamic modeling of the National Grid needs modeling of conventional as well as renewable / distributed generation sources. World Bank has engaged Digsilent as consultant for assisting POSOCO for building dynamic model of the Grid. A guideline for dynamic data collection has been developed in consultation with Digsilent Pacific team.   All the utilities are requested to collect data from the grid scale renewable power plants as well as from conventional power plants under their jurisdiction and submit the same to ERLDC/ERPC as early as possible.

In the 157th OCC advised all the SLDCs to submit the details to ERPC and ERLDC Format along with an explanation for collection of Wind and Solar Data had been shared by ERLDC with all SLDCs.

Bihar/ West Bengal and Orissa are having Solar Plant with more than 5 MW capacity. However, details have not yet been received in terms of modeling data.

In the 132nd PSOC meeting, all generators as well as RE sources were requested to furnish data to SLDC for onward transmission to ERPC.

In the 137th PSOC meeting, SLDC stated that the format has been forwarded to all entities and GRIDCO. It was requested that GRIDCO may pursue to all RE generators to submit the data.

In the 138th PSOC meeting, GRIDCO stated that they have received some of the Solar plant data, which will be forwarded to SLDC. SLDC requested GRIDCO to forward all the PPAs made with the Solar projects of the State.

SLDC has forwarded data for 5 Nos of Solar projects of the Statenamely: 1.Sadipali, Aftab, Jyoti, Dakhin Odisha and Vento Power at Kesinga to ERLDC. GRIDCO may explore for collection of the remaining plants data.

GRIDCO / SLDC may update

C.8: Implementation of Automatic Generation Control in Eastern Region--ERLDC

In compliance to CERC’s direction in order dated 06/12/2017 in petition no 79/RC/2017, AGC was commissioned in NTPC Barh on 01st August 2019 and operationalized since 23rd August, 2019.

Vide order dated 28th August 2019, CERC in Petition No.: 319/RC/2018 directed that all the ISGS stations whose tariff is determined or adopted by CERC shall be AGC-enabled and the ancillary services including secondary control through AGC be implemented as per the following direction:

I. All thermal ISGS stations with installed capacity of 200 MW and above and all hydro stations having capacity exceeding 25 MW excluding the Run-of-River Hydro Projects irrespective of size of the generating station and whose tariff is determined or adopted by CERC are directed to install equipment at the unit control rooms for transferring the required data for AGC as per the requirement to be notified by NLDC. NLDC shall notify the said requirements within one month of this order.

II. All such ISGS stations whose tariff is determined or adopted by CERC shall have communication from the nearest wide band node to the RTU in the unit control room.

xxxxxxxxx

IX. All new thermal ISGS stations with installed capacity of 200 MW and above and hydro stations having capacity exceeding 25 MW excluding the Run-of-River Hydro Projects irrespective of size of the generating station and whose tariff is determined or adopted by CERC shall mandatorily have the capability to provide AGC support.

In 161st OCC, all the ISGS stations were advised to implement the AGC within 6 months as per the above CERC order.

In the 162nd OCC, it was clarified that AGC signal for intra-state generating stations would be generated by the concerned SLDC and the relevant communication path is to be established between SLDC to plant. For ISGS stations, the AGC signal would be sent from NLDC.

OPGC and SLDC, Odisha agreed to submit their plan by 1st week of November 2019.

All concerned plants may please ensure taking necessary action for arranging the communication (through redundant and alternate paths) from the existing nearest wideband communication node to their unit control rooms through two fiber optic cables, in coordination with CTU. It may please be noted that all the ISGS stations whose tariff is determined by or adopted by CERC should be AGC-enabled before 28th February 2020, as per order of CERC.

In the 138th PSOC meeting SLDC stated that since the total capacity of State generators has been tied up with GRIDCO, AGC for State generators may not be required. SLDC may write a letter to ERPC for clarification also may deliberate in the next OCC.

OCC suggested that even though the total capacity is tied up with GRIDCO, depending the area control error during low/high frequency scenario, the generation can be increased / decreased up to 5% by sending AGC signal from SLDC. Member Secretary advised OPGC to submit their action plan within 7 days for implementation of AGC. Further OPGC may depute their officers to visit Barh NTPC station to study the mechanism they have adopted for AGC. SLDC may interact with NLDC in this regard.

SLDC/OPGC may discuss

C.9: Submission of data in MERIT Order portal--CEA

CEA vide mail dated 9th July 2019 informed that the MERIT Order portal had been launched on 23rd June, 2017 by Honourable  Minister of Power. One of the most important advantages of “Merit” Portal is Transparent information dissemination pertaining to marginal variable cost and source wise purchase of electricity and indication of supply side reliability, adequacy, and cost of power procurement.

However, it has been observed that many of the states are not filling the data regularly and sometimes the data filled varies widely from the data available on the respective RLDCs daily reports.

It is requested that the states may be advised to fill the data regularly and check that correct data is filled on the MERIT Portal.

In 159th OCC, all the SLDCs were advised to fill the correct data in MERIT portal on regular basis.

In the 138th PSOC meeting SLDC stated that SLDC is complying the decision of OCC.

SLDC may deliberate

C.10: Data for preparation Load Generation Balance Report (LGBR) of ER for the year 2020-21

As per the IEGC, RPC Secretariat is responsible for finalization of the Annual Load Generation Balance Report (LGBR) for Peak as well as Off-peak scenarios and the annual outage plan for the respective region To facilitate the preparation of LGBR of Eastern Region by ERPC Secretariat within the schedule period, the following data/information for the year 2020-21 in respect of the constituents/utilities of Eastern Region is urgently required:

i)  The unit wise and station wise monthly energy generation proposed from existing units during 2020-21 (thermal/hydro/RES).

ii)  Annual maintenance programme for each of the generating units (thermal and hydro both).

iii)  Generating units under R&M / long outage indicating date of outage and reasons of outage and expected date of return (thermal and hydro both).

iv) Partial and forced outage figures (in %) of generating units for the last 3 years.

v) Month wise peak demand (MW) – restricted and unrestricted peak demand.

vi) Month wise off-peak demand (MW).

vii) Month wise energy requirement (in MU).

viii) Month wise & source wise power (both MU & MW) purchase and/or sale plan.

ix) Schedule of commissioning of new generating units during 2020-21 and unit-wise

monthly generation programme (in MU).

x) Allocation of power from new generating units.

xi) Month wise and annual planned outage of transmission system (Transmission lines 220kV and above / ICTs / Reactors/ other elements.

Information may please also be submitted in the form of soft copy through email (mail ID: mserpcpower@nic.in / erpcjha@yahoo.co.in).

The data is yet to be received from following constituents:

- BSPHCL

- OPTCL

- NTPC: FSTPP, KhSTPS, TSTPS, TTPS, MTPS-II, BRBCL, NSTPS and Darlipalli  APNRL

- JITPL

- Sikkim

- DVC: Details of demand

- Mangdichu HPS, Bhutan

The LGBR Meeting for preparation of draft LGBR for 2020-21 is scheduled to be held at 11:00 hrs on 19th December 2019.

SLDC stated in the OCC that the required data to ERPC has already been forwarded to ERPC.

SLDC may deliberate

C.11: Monitoring of Next Six-Month New Element Integration in OCC and Its Update on Monthly Basis --ERLDC

It has been observed that many elements are getting interconnected into the system and beforehand details are not available with the system operator resulting in difficulty in carrying our operational planning activity. In view of this, as a regular agenda all ISTS and ISGS/IPP to update the OCC regarding any new elements at 220 kV and above which will be integrated in next six month with the grid. For State Grid, SLDC will be submitting the details on behalf of its intrastate Generation and transmission system. The format is given below:

| Transmission Elements | Agency/ Owner | Scheme (ERSS/ TBCB/ Standing Committee/State | Schedule Completion | Projected Month for Completion | Issue Being Faced |
| --- | --- | --- | --- | --- | --- |

In previous several OCC, Transmission licensees and SLDCs are requested to submit RLDC/RPC following details on monthly basis

  - List of transmission element /generators of State and ISTS licensees synchronised in the last month.

  - List of transmission element /generators expected to be synchronised during next month or in near future

Some SLDCs are submitting the list of intrastate and interstate line on regular basis, however transmission element /generators expected to be synchronised during next month or in near future is not submitted by any SLSC/Transmission licensee to RLDC/RPC.

In the 138th PSOC meeting AGM (Const.) assured to furnish the information sought to ERPC.

OCC stated that none of the constituents has furnished the information

CGM (O&M) may deliberate

C.12: Auxiliary  power consumption by Powergrid  Substations--GRIDCO

As per decision of Special   meeting on   this   issue held at ERPC  on 10.07.2018, drawal of auxiliary power through tertiary winding by Powergrid substations shall be treated as drawal by Powergrid from the DISCOM (s). For this, Powergrid shall approach the concerned DISCOM(s) and shall complete all the necessary formalities to become a consumer of the concerned DISCOM.

Powergrid is not becoming the consumer of DISCOM Utility as a result of which, GRIDCO/DISCOM(s) are unable to realize the revenue from Powergrid, whereas GRIDCO is paying for the said quantum of energy consumed by Powergrid since October, 2017.

This issue has already been discussed in the monthly Power System Operational Co­ ordination Committee (PSOC) meeting convened by SLDC, Odisha several times. Powergrid did  not  attend  these  meetings. DISCOMs stated  that  that  they  are  not  receiving  proper response from the Powergrid to regularize the consumer issue.

In 161st OCC, Powergrid informed that Odisha DISCOMs are charging for registration and security fees. Powergrid observed that these fees are not payable by Powergrid as Discoms don’t have to construct any infrastructure for this power. In other states, Powergrid had not paid these charges.

GRIDCO informed that DISCOMs were raising the bills as per the OERC regulations.

After detailed deliberation, it was decided that the issue would be discussed with DISCOMs in Odisha in November 2019 OCC meeting wherein the Discoms of Odisha would be invited to attend.

In the OCC DISCOMs stated that as per the OERC Supply Code provision, POWERGRID has to apply for making them a consumer of the respective DISCOMs indicating their Contract Demand by paying the security deposit. After deliberations from DISCOMs and POWERGRID, Members Secretary advised POWERGRID to apply for consumer and file a Petition before the OERC for exemption of security deposit and demand charges for them.

All DISCOMS/ POWERGRID may deliberate.

C.13: Review of the PSS Tuning of Generators in Eastern Region --ERLDC

On 31st January 2019, PSS Tuning Meeting was held at ERPC. All generating utilities were advised to complete the PSS tuning of their plant at earliest for improvement of damping in the grid during transients. In addition, the tuning reports have also to be submitted to ERLDC/ERPC for their validation.

In line with this ERLDC has communicated to following utilities in view of the recent oscillation observed during various events:

| Generating Power Plant | Remarks | Status of Action Plan to be informed to OCC |
| --- | --- | --- |
| All Units of OPGC and OHPC, | PSS are tuned long back and in many units PSS have not been tuned but are in service. | No Details on PSS tuning Plan shared. |
| GMR | Was done in 2013 and retuning is required with change in the network at Angul. | Plan not yet submitted |
| Sterlite 4 X 600 MW | Due to network changes. | Plan not yet submitted (Orissa SLDC) |

In the OCC meeting, OHPC agreed to forward their action plan. GMR stated that they have planned for PSS tuning during shutdown of their unit. OPGC stated to do PSS tuning during Ferruary’19 while shutdown of the unit. Sterlite (Vedanta) was not present to deliberate.

OHPC/ GMR / OPGC / Vedanta may deliberate.

C.14: Long term outage of transmission elements

400 kV main bay at Indravati (PG) is out of service since last 2 years for breaker problem at Indravati (PG). Line is charged through main bay of 125 MVA B/R breaker on bus-II.  As decided in the meeting between POWERGRID and OPTCL, the breaker has to be replaced by OPTCL. OPTCL may expedite the work for operational flexibility.

In the 16th GCC meeting Sr.G.M (O&M) Zone – I stated that the breaker was transferred to the site. Removal of old breaker foundation is under progress. The delay was due to difficulty in breaking the foundation.

OPTCL stated in the OCC meeting that the breaker commission work is expected to be completed by end of November’19

O&M may update the status

C.15: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber-attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA.

In 142nd OCC, ERLDC informed that, in line with Enquiry Committee Recommendation, cyber security audit is being conducted on regular basis for SCADA system installed at ERLDC and SLDC as well but cyber security audit for telecom infrastructure installed in Eastern Region is not being carried out.

OCC advised all the constituents to conduct the cyber security audit on telecom infrastructure installed in Eastern Region. It is further advised that compliance / mitigation of the points observed during the audit should also be completed for improvement of the telecom infrastructure in ER.

As suggested by CEA, a format has been circulated among ER constituents for furnishing the information of the respective systems for discussion in OCC Meeting. The format is enclosed at Annexure-E1.

OCC advised all the constituents to submit the information to ERPC as per Annexure-E1.

OPTCL has submitted the required data

In the 136th PSOC meeting, IT wing was requested to submit the quarterly report for the quarter ending September’2019.

In the 137th PSOC meeting, IT stated that after completion of the audit, the quarterly report will be submitted. Further, Telecom may intimate the details of their infrastructures to be incorporated in Cyber Security audit.

In the 138th PSOC meeting, IT stated that they will furnish the data after completion of Audit.

Sr. G.M (IT) /Telecom may update

PART-D – Operational Issues

D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of Oct’19:

| Sl. No | Name of Discom | No. of message issued | Over drawal (MU) | Deviation (%) |
| --- | --- | --- | --- | --- |
| 1 | CESU | 0 | -15.087 | 2.04 |
| 2 | WESCO | 0 | +1.48 | 0.24 |
| 3 | NESCO | 0 | +4.129 | 0.92 |
| 4 | SOUTHCO | 0 | -1.963 | 0.69 |
|  | Total | 0 | (-)11.441 |  |

It is noticed that CESU & SOUTHCO had underdrawn while WESCO & NESCO had overdrawn during the month. CESU has deviated 2.04% followed by NESCO 0.92% from the scheduled energy while SOUTHCO & WESCO have deviated 0.69 % & 0.24 % respectively. DISCOMs may forecast their drawal in realistic approach to minimise deviation. Daily drawal profile of all DISCOMs is as indicated in the presentation.

SLDC/ Discoms may please deliberate.

D.2: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.

As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith.

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.

A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.

In the 125th PSOC meeting GRIDCO have agreed to write a letter to M/s Chemtrol. It was decided that a committee shall be constituted with representatives of GRIDCO, O&M, Telecom & SLDC to take a decision.

In the 134th PSOC meeting, GRIDCO stated that M/s Camptrol has successfully completed the pilot project i.e real time data communication for MGM Solar at Tangi.

A committee has been constituted with representatives of GRIDCO, O&M, Telecom & SLDC. This issue was also discussed in the 16th GCC meeting held on 09.08.2019. GRIDCO assured to make a demo of data communication from MGM Solar at Tangi to SLDC by end of August’19.

In the 137th PSOC meeting, DGM (Telecom) stated that M/S Chemtrol has made a Demo but GRIDCO was not present to witness. However’ Chemtrol has agreed to show a Demo in last week of Sept’2019 with prior intimation to GRIDCO.

In the 138th PSOC meeting, it was decided that GRIDCO may fix a dead line for Chemtrol to make the Demo data communication. GRIDCO may convene a meeting to discuss the communication issue.

GRIDCO may deliberate the status.

D.3: Data communication from newly commissioned RE sources connected at 132 kV- SLDC

There are as many 8 Nos. of Solar projects with installed capacity of 272.5 MW have connected with OPTCL network through 132 kV lines. The real time data of these plants are yet to be received at SLDC control room. Since the generation quantum is quite substantial (to the tune of 0.6 MU during a day), this has an impact on real time generation monitoring.

In the 132nd PSOC meeting it was decided that SLDC shall convene a meeting with the defaulting Solar units and Telecom to discuss the issue.

In the 133rd PSOC meeting CGM (Telecom) stated that Vinto Solar data can be integrated only after laying of optical fiber, which has been proposed for PSDF funding

In the 134th PSOC meeting, CGM (Tel) stated that release of optical fiber has already processed.

This issue was discussed in the 16th GCC meeting held on 09.08.2019, where Director (Commercial) suggested to prioritize data communication from Solar plants.

In the 137th PSOC meeting CGM (Telecom) stated that laying of optical fiber is expected to be completed by December’2019. DGM (Telecom) suggested that SLDC may write a letter to Vento Power (Solar) at Kesinga to explore the data communication, since all communication equipment are available with them. Data communication can be made through after visit of the service Engineer of the company.

In the 138th PSOC meeting, it was suggested that Telecom may ensure establishment of data communication facility before recommending for connectivity for any Solar Plant.

SLDC /Telecom may deliberate the status.

D.4: Despatch Scheduling for RE Generation.

At present about 19 Nos of RE generating plants having 340 MW installed capacity operating in the State. None of the plants are furnishing day ahead schedule except 2-3 Nos. In absence of day ahead Declared injection Schedule, there is a substantial mismatch of day ahead generation planning. Also SLDC is not aware of the PPA made by GRIDCO with the Solar plants. As such, it is requested that GRIDCO may forward the copy PPA made with the Solar plants and insist the plants to submit day ahead DC in respect of their plants to SLDC in 15 minute blocks.

GRIDCO may discuss.

D.5: Information regarding RE Sources for RPO Compliance monitoring.

MNRE, Govt. of India has asked to provide information regarding source wise contracted capacity and power drawl from Solar/ Non Solar and large Hydro generators on monthly basis for RPO Compliance monitoring. GRIDCO has forwarded the information up to the month of September 2019, which was submitted to MNRE. It is requested that GRIDCO may furnish the information to SLDC by end of 1st week of each month, so that the same shall be submitted to MNRE by 1oth day of each month. The letter of MNRE and format is enclosed as Annexure-1.

GRICO may discuss.

D.6: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos. of meters integrated, around data from 750 nos. of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos. of meters integrated, data from 717 nos. of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos. of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately.

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.

In the 133rd PSOC meeting, DGM (IT) stated that Paralakhemundi and Balasore S/S meter data has been tested. The software fetching data for other S/Ss will be tested

In the 136th PSOC meeting, IT stated that the meter data has been checked and presentation done on 2nd August’2019.  The same has been forwarded to SLDC.

In the 137th PSOC meeting IT stated that, the software developed by M/S TCS has been tested for DLMS -2 energy meters. This has to be developed for DLMS-3 type energy meters. TCS has asked for one month time for the same.

In the 138th PSOC meeting IT stated that software development is under progress and expected to be completed for CESU area energy meters.

IT / SLDC may update the status

D.7: Collection of tie-line meter data

The inter-state tie-lime meter data are being collected by the concerned officers of the respective grid S/Ss on weekly basis and mailed to SLDC through different mail ID for onward transmission to ERLDC. To streamline the process, it is requested that all such data may be forwarded to SLDC in the Mail ID as mentioned below.

- emsldcorissa@gmail.com

- emsldcorissa@sldcorissa.org.in.

O&M may issue necessary instruction to all the executives entrusted for the mater data collection.

CGM (O&M) may note

D.8: Repair of OPGW, Groung wire and doubling of jumpers & summation meters for 220 kV RSP DC lines. – RSP Agenda

1. Repair of OPGW at Tower-33 &34 zone of 220 kV RSP-Tarkera DC line, which was defective on 2nd Sept’19 due to disturbance.

2. Restoration of fallen ground wire at diamond crossing with PGCIL line.

3. Doubling of all jumpers in 220 kV RSP-Tarkera ckt-1&2, damaged due to over loading.

4. Summation meters for all 4 Nos 220 kV RSP-Tarkera lines.

RSP may deliberate.

PART E: OPERATIONAL PLANNING

E.1:  Commissioning status of new Transmission elements.

The status of commissioning of new transmission elements deliberated in the last meeting is as follows:

| Sl. No | Transmission element details | Present Status |
| --- | --- | --- |
| 1 | 220 kV Jayanagar-Jeypore(PG) 2nd DC line | December’2019 |
| 2 | 400 kV Meramundali-Mendhasal 2nd ckt. | December’2019 |
| 3 | 132 kV Kesinga-Junagarh line | December’2019 |
| 4 | 220 kV Pandiabili-Pratapsasan line | March’20 |
| 5 | 132 kV Pratapsasan-Phulnakhara line | February’20 |
| 6 | 220/132/33 kV, Pratapsasan S/S | March’20 |
| 7 | 220/33 kV, Deogarh S/S | March’20 |
| 8 | 132/33 kV, Maneswar S/S | March’20 |
| 9 | 132/33 kV, Boriguma S/S | Feb’20 |
| 10 | 220/33 kV, 2x20 MVA Baliguda S/S | Forest clearance awaited |
| 11 | 220/33 kV, 2x20 MVA Kalimela S/S | Forest clearance awaited |
| 12 | 220/132/33 kV, Goda Chhak S/S (320 MVA) | March’20 |
| 13 | 220/132 kV Kesinga S/S | Mar’20 |
| 14 | 132/33 kV R.Udyagiri S/S | Mar’20 |
| 16 | 220/33 kV Laxmipur S/S 2nd 20 MVA Tfr | Nov’19 |
| 18 | 132/33 kV, Mancheswar GIS | Dec’19 |
| 19 | 132/33 kV, Satasankha S/S | February’19 |

In the 138 PSOC meeting, All the Discoms stated that the contractors have failed to execute the HT infrastructure work awarded to them. O&M stated that the DISCOMs shall intimate the name of contractor/ Agency/Scheme to OPTCL for necessary action.

The status of 33 kV bays and takeoff arrangement by DIDCOMs are as tabled

| Sl No. | Name of Project | DISCOM | Voltage | Date of Charging | Bays Available | Bays utilised |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Atri | CESU | 220/132/33 | 2/24/2016 | 4 | NIL |
| 2 | Chandaka - B | CESU | 220/132/33 | 3/28/2017 | 4 | NIL |
| 3 | Muniguda | Southco | 132/33 | 11/29/2017 | 4 | NIL |
| 4 | Baragarh New | Wesco | 220/132/33 | 3/21/2018 | 1 | NIL |
| 5 | Aska New | Southco | 220/132/33 | 3/31/2019 | 5 | NIL |
| 6 | Betanati | Nesco | 132/33 | 4/19/2019 | 3 | NIL |
| 7 | Kasipur | Southco | 220/33 | 6/30/2019 | 2 | NIL |
| 8 | Jayapatana | Southco | 220/132/33 | 7/11/2019 | 4 | NIL |
| 9 | Agarpada | Nesco | 132/33 | 8/30/2019 | 5 | NIL |
| 10 | Patangi | Southco | 132/33 | 9/15/2019 | 4 | NIL |
| 11 | Konark | CESU | 132/33 | 6/29/2015 | 4 | 1 |
| 12 | Mania | CESU | 132/33 | 3/31/2016 | 5 | 1 |
| 13 | Bangiriposi | Nesco | 132/33 | 10/3/2016 | 4 | 1 |
| 14 | Infocity-II | CESU | 220/33 | 12/23/2016 | 4 | 1 |
| 15 | Bhogarai | Nesco | 132/33 | 3/28/2017 | 4 | 1 |
| 16 | Tirtol | CESU | 132/33 | 1/5/2018 | 5 | 1 |
| 17 | Chandbali | Nesco | 132/33 | 2/20/2019 | 4 | 1 |
| 18 | Unit-8 | CESU | 132/33 | 4/1/2019 | 5 | 1 |
| 19 | Samagara | CESU | 220/132/33 | 7/14/2015 | 5 | 2 |
| 20 | Marshaghai | CESU | 132/33 | 10/16/2015 | 5 | 2 |
| 21 | Malkangiri | Southco | 220/33 | 3/27/2017 | 4 | 2 |
| 22 | Khajuriakata | CESU | 132/33 | 3/28/2017 | 5 | 2 |
| 23 | Podagada | Southco | 132/33 | 2/9/2018 | 4 | 2 |
| 24 | Kantabanji | Wesco | 132/33 | 2/28/2018 | 5 | 2 |
| 25 | Ghens | Wesco | 132/33 | 4/13/2018 | 4 | 2 |
| 26 | Khuntuni | CESU | 132/33 | 5/31/2018 | 5 | 2 |
| 27 | Narasinghpur | CESU | 220/33 | 8/24/2018 | 5 | 2 |
| 28 | Udala | Nesco | 132/33 | 9/16/2018 | 5 | 2 |
| 29 | Keonjhar | Nesco | 220/33 | 12/31/2018 | 5 | 2 |
| 30 | Chikiti | Southco | 132/33 | 2/25/2019 | 4 | 2 |

CGM (Construction) / DISCOMs may deliberate

E.2: HT metering at DISCOM interface points.-SLDC.

As per the Central Electricity Authority (Installation and Operation of Meters) Amendment Regulations, 2010, the interface meters shall be installed at the High Voltage side of the Inter Connecting Transformer. Accordingly POWERGRID has implemented the amended Regulation. GRIDCO / OPTCL may examine for metering in the High Voltage side of the ICT, which is done in the Low Voltage side at present.

In the 134th PSOC meeting, SLDC stated that Gridco may convene a meeting with DISCOMs and OPTCL to implement CEA Regulation to reduce the loss level of State system and increase revenue of GRIDCO. Further OERC vide order dated 29.03.2019 in case No. 71/2018 in the matter of ARR and Transmission tariff of OPTCL at Para 181 directed OPTCL to take necessary steps for reduction of transmission loss by avoiding over loading as well as other innovative action.

This issue was also discussed in the 16th GCC meeting, where the DISCOMs highlighted the PPA provision for receiving power at 33 kV Voltage level by them. Director (Commercial) agreed to convene a meeting between DISCOMs, O&M & SLDC to discuss the issue. If required, GRIDCO shall approach the Hon’ble OERC for amendment of the PPA/ Supply Code if required to comply CEA Regulation.

In the 137th PSOC meeting it was requested that GRIDCO may convene a meeting to discuss the issue

In the 138th PSOC meeting GRIDCO stated that a meeting will be convened in the month of November’19 to discuss the issue

OPTCL / GRIDCO may deliberate

E.3: Major Events in the month of October’19

- On Dt. 30.10.19 at 13:17 Hrs - 220 kV Tarkera – RSP (SAIL) ckt III charged.

- On Dt. 30.10.19 at 13:19 Hrs - 220 kV Tarkera – RSP (SAIL) ckt IV charged.

Members may note

E.4: Important Grid Incidences during the month of October’19.

- On dt.08-10-19 at 19.26 hrs, due to snapping of R-Ph wave trap at 220kV Budhipadar-Tarkera ckt-1, Bus-Bar protection relay of Bus-2 operated which led to tripping of all feeders emanating from bus -2.

- On dt.25-10-2019 at 04:44 hrs, due to detachment of drop jumper from SI clamp of B-Phase Main bus-II of 220kV Bargarh (N)-Bolangir(N) ckt, heavy spark noticed. The said ckt tripped from Bargarh(N) end but did not trip from Bolangir end. The breaker also could not be tripped remotely from Bolangir(New) end. To avoid any damage to equipment, 160MVA Auto-I & II at Bolangir (N) hand tripped. As the fault still persisted, with continuous fire, 220kV Bolangir(PG)-Bolangir (N) ckt hand tripped resulting total power failure at Grid S/S, Bolangir (New).

O&M may discuss

E.5: Outage of major transmission Elements during the month of September’19. (above 10 hrs).

| Sl No | Transmission line / element | Tripping Dt/time | Restoration Dt/time | Reason |
| --- | --- | --- | --- | --- |
| 1 | 132 kV Lapanga- Burla ckt -II | 04.10.19/ 13:46 hrs | 05.10.19 /16:37 hrs | Snapping of line conductor |
| 2 | 400 kV Lapanga –OPGC ckt -I | 06.10.19/ 00:49 hr. | 08.10.19/ 17:57 hrs. | Snapping of line conductor |
| 3 | 220 kV Rengali (SY) – Barkote ckt | 06.10.19 /16:10 hrs | 09.10.19 / 13:22 hrs | R- Ph line Conductor snapped at Loc -217 |
| 4 | 220 kV Budhipadar- Tarkera ckt -I | 08.10.19 / 19:26Hrs | 09.10.19 / 15:03 hrs | Conductor snapped at Grid S/S, Budhipadar |
| 5 | 220 kV Budhipadar – Korba ckt -III | 08.10.19 / 19:03hr | 09.10.19 / 19:14 | Charged after patrolling |
| 6 | 132 kV Jayanagar – Sunabeda ckt | 12.10.19 /16:48 hrs | 13.10.19 /19:22 | R-Ph CT failure |
| 7 | 220 kV Budhiapadar –Raigarh ckt | 18.10.19 / 14:37 hrs | 19.10.19 /16:08 hrs | DP relay operated. Zone -1, L2-E, 3.18 kA, 35.5 kM |
| 8 | 132 kV Atri – Argul ckt -II | 21.10.19 / 16:09 hrs | 22.10.19 / 11:11 hrs | Snapping of Line conductor |
| 9 | 132 kV Bhanjanagar – Aska ckt -I | 29.10.19 / 18:46 hrs | 30.10.19 / 21:02 hrs | B-ph CT failure at Aska S/S |

O&M may discuss

E.6: Prolonged outage of Transmission elements

| Sl No | Transmission line / element | Date of outage | Reason | Expected date of restoration |
| --- | --- | --- | --- | --- |
| 1 | 220 kV Samangara – Pandiavil ckt –I& II | 03.05.19 | Tower collapsed during the severe cyclonic storm FANI. |  |

O&M may discuss

E.7:  Review of Outage Program of State Generators for the month of December’19:

Tentative Outage programe for State Generators for the month of December’2019

| Sl. | Station | Unit | Period | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Burla | # 1 # 4 # 5 # 6 | 14.03.18 to continue 01.12.19 to 31.12.19 25.10.16 to continue 16.10.15 to continue | T&G coupling cover water leakage Annual Maintenance Under R,M & U Under R, M & U |
| 2 | Chipilima | # 1 | 15.12.19 to 14.01.20 | Annual Maintenance |
| 3 | Balimela | # 1 # 2 | 05.08.16 to continue 20.11.17 to continue | Under R,M work Under R,M work |
| 4 | Rengali | # 3 | 01.12.19 to 31.12.19 | Annual Maintenance & PSDF work |
| 5 | U. Indravati | # 1 # 3 | 17.12.19 to 16.01.20 15.11.19 to 13.12.19 | Annual Maintenance Annual Maintenance |

OHPC may deliberate

E.8: Generation Program for the month of December’19.

Generation schedule for the month of December’19 furnished by OHPC are given below.

| Name of Hydro Gen. Station | Generation Program (MW) | Reservoir Level as on 01.11.19 | Reservoir Level as on 01.11.18 | MDDL | High Flood Reservoir Level |
| --- | --- | --- | --- | --- | --- |
|  | Dec’19 (1st fortnight) | Dec’19 (2nd fortnight) |  |  |  |  |
| HPS-I, Burla | 40 | 40 | 629.89 ft. | 627.10 ft. | 590 ft. | 630 ft. |
| HPS-II, Chiplima | 25 | 25 | - | - | - | - |
| Balimela | 90 | 90 | 1515.30 ft. | 1511.50 ft. | 1440 ft. | 1516 ft. |
| Rengali | 40 | 40 | 124.03 mtr. | 118.70 mtr. | 109.72 mtr | 123.5 mtr. |
| U.Kolab | 30 | 30 | 857.29 mts. | 855.93 mtr. | 844 mtr | 858 mtr. |
| U. Indravati | 65 | 65 | 641.02 mtr. | 640.83 mtr. | 639.40 mtr | 642 mtr |
| MKD (O/D) | 30 | 30 | 2748.40 ft. | 2746.80 ft. | 2685 ft. | 2750 ft. |
| TOTAL | 320 | 320 |  |  |  |  |

Generation schedule may change depending on inflow & availability of machine.

SLDC / OHPC may deliberate

E.9: Anticipated power generation and demand for the month of December’2019.

| Sl. No | Discom | Average | Peak |
| --- | --- | --- | --- |
| 1 | CESU | 1000 | 1200 |
| 2 | WESCO | 950 | 1000 |
| 3 | NESCO | 800 | 900 |
| 4 | SOUTHCO | 400 | 450 |
| 5 | Total Discom | 3150 | 3550 |
|  | System Loss & others | 150 | 200 |
|  | Total Demand | 3300 | 3750 |
| Availability |  |  |
| 1 | Hydro | 320 | 800 |
| 2 | State Thermal | 1400 | 1400 |
| 3 | IPP, small hydro &RE | 350 | 300 |
| 4 | ISGS share (including OA& purchase) | 950 | 1000 |
| 5 | CGP support (OA) | 300 | 250 |
| 6 | Total availability | 3320 | 3750 |
| 7 | Surplus / Deficit | 20 | 0 |

Members may discuss.

PART F: OTHER ISSUES

F.1:  Date and Venue of the next (140th) PSOC meeting.