Distribution list

            - The Director (Commercial), Gridco, Bhubaneswar

            - The Director (Operation), OHPC, Bhubaneswar

            - The CGM (O & M), OPTCL, Bhubaneswar

            - The CGM (Const.), OPTCL, Bhubaneswar

            - The CGM, (RT&C), OPTCL, Bhubaneswar

            - The C.G.M. (PP), GRIDCO, Bhubaneswar

            - The CGM (IT), OPTCL, Bhubaneswar

            - The Sr. G.M (C.P), OPTCL, Bhubaneswar

            - The Sr. G.M. (TP&C), OPTCL, Bhubaneswar

            - The Sr. G.M. (CPC), OPTCL, Bhubaneswar

            - The Sr. G.M.(O&M), Zone-I, Narendrapur

            - The Sr. G.M.(O&M), Zone-II, Meramundali

            - The Sr. G.M. (Telecom), OPTCL, Bhubaneswar

            - The Member Secy., (GCC), OPTCL, Bhubaneswar

            - The C.E.O., CESU, Bhubaneswar

            - The A.O.,WESCO Utility, Burla

            - The A.O., NESCO Utility, Balasore

            - The A.O., SOUTHCO Utility, Berhampur

            - The Vice President (O), IMFA, Choudwar

            - The D.G.M (Electrical), IbTPS, OPGC, Banharpali

            - The G.M. (O &M), CPP, NALCO, Angul

            - The DGM (O & M), NTPC (TTPS), Talcher

            - The G.M., HINDALCO, Hirakud

            - The D.G.M. (Power Distribution), RSP, Rourkela

            - The D.G.M. (Elect.), JINDAL Stainless Ltd, Duburi

            - The G.M., Vedanta Aluminium Ltd., Jharsuguda

            - The G.M.(Elect.), Bhushan Steel & Power Ltd, Budhipadar

            - The Sr. G.M. (Elect.), Bhusan Steel Limited, Meramundali

            - The S.E., Machhakund

## Odisha Power Transmission Corporation Ltd. Bhubaneswar.

Minutes of 87th PSOC meeting held on 27.06.2015 at PTC, Chandaka

List of participants is at Annexure.

Sr. G.M (Power System) welcomed all the participants to the 87th Power System Operational Coordination meeting and highlighted the system performance during the month of May’2015 and overall power scenario of the State. He also emphasized on the drawal by all the Discoms during the month.

The meeting was chaired by CGM (O&M), OPTCL.

Manager (SS), SLDC took the agenda items for discussion.

The review proceeded as follows:

PART A: CONFIRMATION OF MINUTES

A.1: Confirmation of minutes of 86th PSOC meeting held on 23.05.2015

The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2014/2461(21), dated 11.06.2015 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting

Minutes of 86th PSOC meeting was confirmed since no comments were received.

PART B : SYSTEM PERFORMANCE

B1: Review of Grid Performance for the month of May’2015.

## (A)  Frequency

It was noticed that, during the month of May’15, 62.21% of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 56.89% during the month of April’15. The maximum and minimum System frequency during the month was 50.42Hz & 49.66Hz respectively.

## (B)  Grid demand

Grid demand for the month of May’15 was reviewed. The energy consumption during the month was 2393 MU. The maximum System demand of 3932 MW occurred on 29.05.2015 at 22:00 Hrs and minimum demand of 2319 MW occurred on 11.05.15 at 18:00 Hrs.

Deliberation in the meeting

It is observed that energy consumption during the month of May’ 15 was increased by 235 MU, and the peak demand during the month was increased by 81MW from that of April’15. The energy consumption during the month has been increased by 103 MU in comparison to May’14.

(C)  Voltage Profile of important Sub Stations in OPTCL System.

The Voltage profile at different 220 kV buses in OPTCL system during the month of May’15 was reviewed.

Deliberation in the meeting

Bolangir and Jayanagar 220 kV bus have the maximum voltage of 244.79 kV and 242.31 kV respectively, while Narendrapur, Paradeep and Budhipadar 220 kV bus have experienced the minimum Voltage of 177.59, 186.88 and 172.91kV respectively. High Voltage at Bolangir and low Voltage at Budhipadar were due to disturbance in those areas.

Sr. G.M (PS) stated that high voltage at Jayanagar has been arrested to some extent in comparison to previous months. Powergrid has scheduled for installation of additional reactor at Jeypore by June’2015, but no action is seems to be taken till date. It was decided to raise the issue in the OCC meeting of ERPC.

[Action: SGM (PS)]

(D) Energy Generation / import during the month of May’15

Energy generation and exchange during the month of MAy’15 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2392.51 MU.

(E) Drawal of Machhakund Power

The drawal of Machhakund power during the month of May’15 was 17.30 MU against AP drawal of 19.478 MU. Total generation was 38.508 MU

Since, the Auto at Jayanagar has already been charged. The bus modification work at Jayanagar S/S is to be taken up by OPTCL.

Deliberation in the meeting

Sr.GM (O&M), Zone-I stated that Jayanagar and Rayagada area load can be put in Machhakund system at present.

Sr. G.M (Telecom) stated that communication between SLDC and Machhakund has been established through Powergrid network as Remote Subscriber, temporarily. After restoration of Phailin damage permanent communication shall be made.

Southco Utility stated that work for tender has been done for linking of 33 kV Gumuda feeder with Akhusing S/S.

Gridco stated that a decision for sale of the State’s Machhakund share to AP is anticipated within a couple of weeks.

Sr. G.M (PS) stated that Machhakund is not allowing more drawal during off peak period to compensate State’s share. OHPC may raise this issue in their monthly meeting with Machhakund authority. Gridco may write APGENCO in this regard.

[Action:-Sr. G.M (Telecom) / Sr.GM (O&M)-I / SOUTHCO Utility]

(F) DISCOM Drawal during the month of May’15

The schedule and actual energy drawal by Discoms for the month of May’15 was reviewed.

Deliberation in the meeting

It was noticed that CESU have overdrawn substantially to the tune of 57.066 MU while SOUTHCO has overdrawn 7.461MU. CESU stated that they are predicting the drawal from the SCADA data. It was decided to analyze the Discoms drawal displayed in SCADA and compare with the actual drawal to ascertain the error.

[Action: All Distribution Utilities / SLDC]

(G) Under Frequency Relay operation in OPTCL System during the month of May’15.

There is no UF Relay operation occurred during the month of May’15 as the frequency had never gone beyond 48.50 Hz.

PART C – issues raised in 109th OCC meeting of ERPC

C1: PLCC Status installed in Eastern Region & EL status

In 106th OCC, Powergrid agreed to restore and maintain the PLCC system at both ends (its own end as well as the constituent end) of a line wherein the other ends are not being maintained by respective constituents for some reasons or others. It was decided that the cost of restoration and maintenance of PLCC system at such (constituent) ends of the line will be borne by the respective constituents. In addition to this the constituents also agreed to extend all possible support to Powergrid in carrying out the above work.

In 108th OCC, Powergrid raised several issues to maintain the PLCC system falling under control area of other constituents and pointed out difficulties in maintaining the same. OCC advised Powergrid to survey the PLCC equipment for the transmission lines given at Annexure and submit the status & requirement in the next OCC meeting.

List of PLCC equipments owned by OPTCL

| Sl. No | Tie Line | Connected System |
| --- | --- | --- |
| 1 | Indravati(PG)-Indravati | POWERGRID | OPTCL |
| 2 | Baripada(PG) - Mendhasal | POWERGRID | OPTCL |
| 3 | Balimela – Upper Silleru | OPTCL | APTRANSCO |
| 4 | Budhipadar - Raigarh | OPTCL | Chattisgarh |
| 5 | Budhipadar – Korba | OPTCL | Chattisgarh |
| 6 | Jayanagar – Jeypore (PG) | OPTCL | POWERGRID |
| 7 | Bisra - Tarkera | POWERGRID | OPTCL |
| 8 | Joda - Kenduposi | OPTCL | JUSNL |
| 9 | Rourkela - Goelkera | OPTCL | JUSNL |

Deliberations in the meeting

Sr. G.M (Telecom) has intimated the present status of PLCC as tabled below.

[Action: Sr. G.M. (Telecom)]

C2: Status of commissioned Islanding schemes in Eastern Region

Sl.4 Islanding scheme if IB TPS, Odisha

It was deliberated that Islanding scheme of IBTPS is yet to be commissioned.

Deliberations in the meeting

CGM (O&M) stated that during disturbance on 23rd May’15, IbTPS could not survive even if there was load at Budhipadar sub-station. IbTPS stated that the command for survival was not received from islanding relay to enable the governor to operate at island mode. CGM (O&M) stated that installation OPGW is required between IbTPS & Budhipadar for transmission of command. G.M. (Telecom.) assured to provide communication of signal to IbTPS with the existing PLCC till installation of OPGW.

[Action: Sr. G.M. (Telecom)]

C3: Status of 1st “Third Party Protection Audit”

The compliance report of 1st 3rd party Protection Audit in respect of OPTCL

Total observations:	59

Complied:		12

% compliance:		20.34

OCC advised to submit the Substation wise compliance to the observations as per the list.

Deliberations in the meeting

CGM (O&M) stated that the compliance report has already been submitted to ERPC.

C4: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG) S/s

400/220 kV, 2 X 315 MVA S/S at Bolangir has been established by Powergrid as part of  ISTS system & the following 220 kV interconnecting lines were envisaged to be established by OPTCL:

- LILO of OPTCL’s Katapali-Bolangir line (One ckt) at Bolangir (PG):

- Bolangir (PG)–Bolangir S/C line.

- Bolangir (PG)-Kesinga S/C line.

Deliberations in the meeting

The status of the lines is as follows:

- LILO of OPTCL’s Burla-Bolangir line (One ckt) at Bolangir (PG): July, 2015

- Bolangir –Bolangir (PG) S/C line, which is a part of proposed Bolangir- Kesinga D/C line with one ckt LILO at Bolangir(PG): May be delayed due to land dispute.

- Bolangir PG-Kesinga S/C line (Part of Bolangir-Kesinga D/C line): Work started

[Action: CGM (O&M) / CGM (Construction)]

C5: Breakdown Maintenance of OPGW

In 108th OCC, Powergrid informed that they are planning AMC for central sector OPGW and agreed to include the constituent part in the same AMC after getting requisitioned.

It was decided in the OCC that all constituents are required to give their requisition to Powergrid within a week for inclusion in the AMC proposed for central sector OPGW.

Deliberations in the meeting

Sr. G.M (Telecom) stated that OPTCL is in process of empanelment of rate contract holders for OPGW maintenance work. As such it is not required to send AMC proposal to Powergrid.

[Action: CGM (O&M)]

C6: Allotment of 2 Nos 132 kV bays at 400/220/132 kV Baripada (PG) S/S to OPTCL for 132 kV Jaleswar ckt 1&2.

It was deliberated in the OCC that Jharkhand Urja Sancharan Nigam Limited (JUSNL) may reconsider for issue of consent for utilization of 2 Nos 132 kV bays by OPTCL for its Jaleswar S/S, which shall be surrendered by OPTCL whenever required by them. CGM (O&M) may write a letter to JUSNL and JUVNL in this regard.

Deliberations in the meeting

It was decided that CGM (Const.) shall make correspondence in this regard with Jharkhand Urja Sancharan Nigam Limited (JUSNL) and Jharkhand Urja Vikas Nigam Limited (JUVNL).

[Action: CGM (Construction)]

C7: Future requirement of Special Energy Meters and DCDs

The requirement of frequency based ABT Special type meters up to 2014 has been procured by Powergrid and likely to be exhausted shortly. Beneficiary Constituents of ER are requested for assessment of their requirement of Special Type Energy Meters and DCDs for the period from 2015 to 2017 and intimate the same in the next OCC meeting so that the advance action for procurement can be taken.

In the last meeting SLDC stated that DCDs may not be required as Powergrid is going to adopt AMR for all the metering points soon. However, the existing DCDs may be replaced by Powergrid. SLDC has already intimated Powergid for replacement of defective DCDs.

Deliberations in the meeting

SLDC stated that POWERGRID shall replace the defective DCDs after procurement of new DCDs.

C8: Pollution mapping for Eastern Region

In 109th OCC meeting, it was decided that all constituents shall take on site measurement of ESDD & NSDD and intimate Powergrid / ERPC.

Measuring kits are being issued. Measurement will be completed by the end of June’2015.

Deliberations in the meeting

CGM (O&M) stated that the number of kits provided by POWERGRID to complete the measurement by June 2015. POWERGRID may be requested to provide more number of measuring kits.

[Action: CGM (O&M)]

C9: Mock Black Start Exercise in Eastern Region.

It was decided in the 109th OCC to conduct mock black start exercise for Upper Kolab HEP during the month of June’15.

Deliberations in the meeting

It was decided to conduct mock black start exercise during the month of July’15.  Sr. G.M. (PS) stated that since DG set has been commissioned at Burla PH, Mock black start exercise for Burla PH can be conducted to which OHPC agreed. A procedure for this exercise is to be developed by SLDC and sent to ERLDC for views.

[Action: OHPC / SLDC]

C10:Proposal for review of Power Demand Order (PDO) condition for HVDC Gazuwaka poles, in view of repeated tripping in South Odisha.

ERLDC had made a presentation on the existing and proposed PDOs at HVDC Gazuwaka poles and sought views of OPTCL for implementation in the 106th OCC meeting of ERPC. In 29th PCC, OPTCL agreed to the proposal.

In the OCC meeting it was decided that, OPTCL shall study and forward their comments to ERPC / ERLDC. OPTCL has already forwarded their comments to ERLDC.

OPTCL informed that the over Voltage set point may be considered at 420 kV instead of 435 kV as per upper steady state voltage limit for 400 kV system satisfied in clause (3) of grid regulation standard 2010 of CEA

It was decided in the OCC to hold a meeting between OPTCL, ERPC, ERLDC, SRLDC & NLDC at ERPC to discuss the issue.

Deliberations in the meeting

Sr. G.M. (PS) stated that normally the voltage at Jeypore command area is remaining high, as such it may not be possible for reduction of over voltage setting.

C11: Loading of Meramundali & Mendhasal ICTs

In view of exceeding the loading of Meramundali and Mendhasal ICTs beyond 200 MW, (N-1) contingency is not remaining satisfied. OPTCL may take action for augmentation of ICTs at these locations for improving Grid reliability.

Deliberations in the meeting

CGM (O&M) stated that installation of 3rd ICT at Mendhasal is in progress and proposal for installation of 3rd ICT at Meramundali shall be placed before the next BoD meeting of OPTCL.

[Action: CGM (O&M)]

PART-D – Operational Issues

D1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of May’2015 is as tabled.

| Sl. No | Name of Discom | No. of message issued | Over drawal (MU) |
| --- | --- | --- | --- |
| 1 | CESU | 27 | 57.066 |
| 2 | WESCO | 51 | 2.296 |
| 3 | NESCO | 24 | 2.878 |
| 4 | SOUTHCO | 24 | 7.461 |
|  | Total | 126 | 69.701 |

It is noticed that CESU is continuously over drawing since last 4 months. The drawal display of CESU in SCADA may be analyzed by SLDC and CESU, comparing with the actual energy meter data for last months and the reason of less display may be identified. The analysis report may be placed in the next meeting. All the Discoms are requested to predict their drawal in a realistic manner to avoid over drawal / under drawal. Frequent revision of drawal schedule may be avoided as for as possible.

Deliberations in the meeting

It was decided that SLDC and CESU shall analyze and compare the drawal display of CESU in SCADA with the actual energy meter data for last months and ascertain the reason of less display. The analysis report shall be placed in the next meeting.

[Action:  SLDC]

D2: Availability of data of real time power flow of feeders covered under Under-frequency Load shedding scheme (UFLS) and lower relief expected to obtained in real time system operation

Sr. G.M. (Telecom) stated that inspection of MFM is in progress. Work will be completed soon after receipt.

Deliberations in the meeting

Sr. G.M. (Telecom) stated that pilot project has been completed at Khurda grid sub-station (33kV Banki feeder) and for all other sub-stations MFM have been dispatched to the site and will be commissioned shortly.

[Action: Sr. G.M (Telecom)]

D3: Levy of Reactive Energy Charges due to injection of VAR to the grid.

It is noticed that GRIDCO is the only constituent in ER, liable to pay Reactive Energy charges due to injection of reactive power to the pool at the following inter connection point for the period from 23.02.2015 to 01.03.2015.

- 400kV Indravati-Indravati PG

- 400kV Meramundali- Angul PG D/C

- 220kV Rengali – Rengali PG D/C

- 132 kV Baripada PG – Rairangpur

In the last meeting, it was decided that SLDC shall monitor the VAr injection of IPP / CGP on real time basis.

Minimum number of ckts shall be kept in service in case of low hydro generation. Sr. G.M (PS) stated that Balimela HEP is keeping two Units in synchronization with minimum generation (10 MW each) to meet its auxiliary requirement in contingency conditions, even though DG set is available.

SLDC stated that Balimela PH may revive their 33/11kV station transformers for availing power supply in contingency conditions and avoid keeping two nos. of units in bar all the time. It was decided that OHPC shall approach OPTCL for extension of power supply at 33kV from 220/33 kV, Balimela sub-station.

Deliberations in the meeting

OHPC stated that existing station transformer at Balimela PH are very old and may not be possible for their revival. At present GT –I is being utilized for availing auxiliary supply. Sr. G.M. (PS) stated that there is no necessity keeping two numbers of units in spinning. OHPC may take necessary steps for procurement of new station transformer.

[Action: OHPC]

D4: Prolonged outage of transmission elements and tentative revival dates

| Sl.No | Name of transmission element | Reason of outage | Probable date of revival |
| --- | --- | --- | --- |
| 1 | 220 kV Jayanagar-Theruvali ckt-III Breaker | Breaker defunct | July 2015 |
| 2 | 220/132 kV, 100 MVA Auto-II at Duburi | After inspection by repairer, date can be ascertained | After rainy season. |
| 3 | 220 kV Budhipadar-Raigarh | Breaker problem at Raigarh Idle charged from Budhipadar |  |

D5: Communication issues

- Installation of communication equipment by CGPs / Industries.

The status of data communication from CGPs as deliberated in the last meeting is as follows

| Sl. No | Name of CGP | Present status |
| --- | --- | --- |
| 1 | M/s IFFCO, Paradeep | Outdoor commissioning work completed. Testing of DPLC is in progress. M/s. AREVA has been instructed for commissioning of RTU. |
| 2 | M/s MSP Mettalicks | PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited. |
| 3 | M/s NINL, Duburi | M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. |
| 4 | M/s Adhunik Metallics | PLCC & RTU installed. Database has prepared by OPTCL. Commissioning of RTU is yet to be done. |
| 5 | M/s Rohit Ferrotech | PLCC established and inspection by Telecom Engineers completed. Data base has already been prepared by OPTCL. |
| 6 | M/s VAL, Jharsuguda | No isolator status is available. MW/ MVAR not available for Sterlite 1&2 line, station transformer / Smelter. CBs of Bus coupler data, Bus-1 kV/Hz are not available. As per MOM between OPTCL & Sesa Sterlite, Jharsuguda dtd 22.09.2014, provision for telemetry data will be extended within 6 months (March,2015). The CGP is not responding. VAL intimated that data shall be made available in all respect by July, 2015. |

It was decided that GCC may write to all the defaulting CGPs to comply their data communication system early.

Deliberations in the meeting

Sr. G.M.(Telecom.) stated that installation of communication facility in respect of M/s NINL, Duburi, M/s Adhunik Metallics and M/s Rohit Ferrotech shall be discussed in GCC meeting proposed to be held at Duburi shortly.

[Action: GCC / Sr. G.M. (Telecom.)]

- Availability of Tap position of 400kV ICTs at Mendhasal & Meramundali.

It is noticed that tap position of Meramundali ICTS are not available for SCADA display.

In the last meeting G.M. (Telecom) stated that PCB for ICT –II has already been installed and working. PCB for ICT-I will be installed after availing of line shut down. Procurement of TPC-201 for Meramundali has been initiated.

Deliberations in the meeting

Sr. G.M. (Telecom) stated that action has been taken for procurement of TPI. The work is expected to be completed within a fortnight.

[Action: Sr. G.M (Telecom)]

- Availability of data at SLDC.

The data for the following elements are not available for SCADA display.

- Power flow through 132 kV Paradeep- Jagatsinghpur ckt.

- JSPL (Angul) generation data

In the last meeting Sr. G.M. (Telecom) stated that, for item (a), transducers have been installed and cable issued. (b) M/s JSPL has been asked to restore its generation data at SLDC, but not responding.

Deliberations in the meeting

Sr. G.M. (Telecom) stated that final testing & commissioning in respect of item (a) are pending and shall be completed shortly.

He also stated that M/s JSPL, Angul has been asked to restore its generation data at SLDC, but the CGP is not responding, which may be reviewed in the GCC meeting.

[Action: GCC / Sr. G.M. (Telecom.)]

- Interruption of SCADA.

It is noticed that there is frequent interruption of SCADA System, resulting problem in real time operation. Action may be taken to avoid such frequent interruption of SCADA.

Deliberations in the meeting

Sr. G.M. (Telecom) stated that transmission of data is dependent on fibre connectivity of POWERGRID. Most of the time communication is being interrupted between Rourkela PG (Bisra) to Kaniha for which ICCP link is also getting interrupted. However action is being taken to improve the link availability in co-ordination with POWERGRID.

[Action: Sr. G.M. (Telecom.)]

- Integration of new element.

M/s SSL-SEZ became a consumer of WESCO Utility with effect from 20.03.2015 and importing power through intra State open access from its CGP at Jharsuguda as well as from other utility. The drawal of SSL-SEZ needs to be integrated to SCADA to ascertain WESCO Utility drawal and State demand on real time basis. Since the SSL is reporting to ERLDC, Sr. G.M (Telecom) may write to ERLDC for integration of SSL-SEZ drawal in to the SCADA.

At present generation data of SSL-IPP connected with State Transmission System is being received through ERLDC. But most of the times the data become suspected. SEZ drawal data is yet to be received. However, the calculated figure is being displayed. Sr. G.M (Telecom) may write to SSL to transmit uninterrupted date of IPP generation as well as integrate SEZ drawal to ERLDC.

Deliberations in the meeting

Sr. G.M. (Telecom) stated that they have already written a letter to SSL in this regard and suggested that Sr. G.M. (PS) may also make correspondences with Vedanta Ltd.

[Action: SLDC / Sr. G.M. (Telecom.)]

D6: Display of dashboard data.

On receipt of feedback from Dist. Utilities, IT representatives have made a demo at SLDC in presence of all Discoms, Telecom and SLDC, wherein some modifications were suggested. However, the dashboard display is functioning satisfactorily.

The status of lease line of all Discoms as deliberated in the meeting are as detailed.

| Sl. No | Dist. Utility | Status of leased line | Remarks |
| --- | --- | --- | --- |
| 1 | CESU | Already connected. RVDU commissioned | Data display available |
| 2 | WESCO | Applied to BSNL for demand note | Expected by 15th July’15. |
| 3 | NESCO | Required amount deposited with BSNL | Expected by 30th June’15. |
| 4 | SOUTHCO | Required amount deposited with BSNL | Already connected |

[Action: Sr. G.M (Telecom) / CGM (IT) / NESCO / WESCO]

D7: Web based drawal / generation scheduling.

SLDC is going to implement web based drawal / generation scheduling for Distribution Utilities and State generating stations including IPPs and CGPs soon. The required formats are being forwarded to all the users. They are requested to forward their respective schedule in the prescribed format. In the last meeting it was decided that IT wing of OPTCL shall take up the work. The scheduling formats shall be forwarded to all users.

Deliberations in the meeting

IT representative stated that they will take two months for development of the software.

[Action: CGM (IT)]

D8: DISCOM Issues

SOUTHCO:

| Sl No | Issues raised | Deliberation |
| --- | --- | --- |
| 1 | ABT issues 1. Providing data in the new format submitted by SOUTHCO in the ABT Dash Board 2. Incorporation of data of new grid sub-stations i.e. Boudh, Dabugaon, Umerkote. Although RVDU equipments have installed at ABT cell of SOUTHCO and lease line is in service, the real time data is yet to be received. | IT representative stated that the display is being made as per the format forwarded by Discoms. In the meanwhile Southco has changed their format. The format needs to be examined. Data display shall be made available for the S/Ss integrated in SCADA system only. Display shall be made shortly. |
| 2 | Revision of Schedule In case of reduction of Southco drawal due to grid failure for a prolonged period or due to imposition of Load Restriction by SLDC, the actual drawal may be treated as schedule. In case of load crash, the downward revision is not being accepted by SLDC, indication technical minimum availability. | SLDC shall revise the schedule as per provisions in the OGC only |
| 3 | Other issues Construction of new Grid S/Ss at Baliguda, Chikiti and Gunupur to address low Voltage problem at those areas. | CGM (O&M) stated that decision has been taken for installation of Grid S/s at Baliguda, Chikiti and Gunpur. |

NESCO

Server error problem noticed since last three days need to be sorted out.

Deliberations in the meeting

Server problem has already been sorted out.

CESU

| Sl No | Issues raised | Deliberation |
| --- | --- | --- |
| 1 | Data display in RVDU- All 113 nos. metering point data on which monthly energy drawal of CESU is being computed are not displaying. Some of the data are remaining fixed, while some are showing as ‘suspect’. Interruption in data display. Mismatch of data with SLDC such as Frequency, Schedule and actual drawal Frequency related pricing chart on real time basis Previous drawal, schedule and frequency. | Data in respect of the Grid S/Ss integrated in SCADA are being displayed. Interruption of display may be due to lease line problem, which is beyond the control of SLDC. Mismatch of data display is being examined and resolved shortly. |
| 2 | Low Voltage problem at Cuttack, Salipur, Bhubaneswar and Jagatsingpur area including Rly traction S/Ss. This can be resolved by commissioning of Bidanasi-Cuttack line | Low Voltage problem shall be sorted out after commissioning of 400 kV Duburi S/S |
| 3 | Power drawal by Kaipadar traction feeder from Khurda S/S affects industrial activity in Khurda area. | Kaipadar is kept on Khurda only in contingency conditions. |
| 4 | Commissioning of 220 kV Atri S/S to address low Voltage problem | Under progress |
| 5 | Connecting 220 kV Grid S/Ss with the proposed 400/220 kV S/s by Powergrid | CESU may specify the S/Ss and Powergrid S/S. |
| 6 | Commissioning of 132/33 kV S/s at Marsaghai to meet the area load requirement. | Expected by July 2015 |
| 7 | Replacement of CT at Chainpal. | Being examined |
| 8 | Provision of additional 33 kV bay at Bidanasi Grid to feed Satichoura 33 kV S/s, which is scheduled to be completed by December’15. | No space available at Bidanasi. |
| 9 | Low Voltage problem at Khurda, Paradeep and Bhubaneswar. | Paradeep and Khurda area Voltage profile shall be addressed after commissioning of 400 kV Duburi & 220 kV Atri S/S respectively. After diversion of Bhubaneswar load to Phulnakhara Grid through 33 kV Nadiagurudi feeder, Bhubaneswar Voltage profile shall be improved. |
| 10 | Frequent interruption of power supply to Gorkhnath Rly traction S/S. | Pradeep-Jagatsingpur 2nd ckt is under construction, after which the interruption shall be reduced. |
| 11 | Failure of DC and AC auxiliary supply to Apex meters at PPL-I at Paradeep and TS Alloys at Choudwar. | May be resolved locally. |
| 12 | Voltage profile at different Grid S/Ss and power supply interruption to Gorekhnath TSS | Pradeep-Jagatsingpur 2nd ckt is under construction, after which the Voltage profile shall be improved. |

PART E: OPERATIONAL PLANNING

E1:  Commissioning status of New Transmission elements.

The status of commissioning of new transmission elements is as follows:

| Sl. No | Transmission element details | Present Status |
| --- | --- | --- |
| 1 | Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line | Work has already been started. Expected to be completed by July 2015. |
| 2 | Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt | Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal, which is under progress. |
| 3 | Commissioning of 400 kV Ib-Meramundali D/C line. | 400kV SSEL-Meramundali line has been idle charged from SSEL end. Due to theft of conductor line could not be charged. Expected to be charged by end of July’2015. |
| 4 | Commissioning of 400 kV Duburi-Meramundali D/C line. | Work is in progress after disposal of Case. Expected by the end of July 2015. |
| 5 | Commissioning of 220 kV Bidanasi-Cuttack line | Work in progress and expected to be completed by July 2015. |
| 6 | Commissioning of 220/132 kV Cuttack S/S | Work in progress and expected to be completed by July 2015. |
| 7 | Commissioning of 132 kV Baripada (PG)-Jaleswar line | Work has already been started, which will be completed by December 2015. |
| 8 | Commissioning of 220/132 kV Kesinga S/S | Work under progress. Expected by September 2016. |
| 9 | Connectivity to Keonjhar PG | Proposal is mooted to be placed in the BoD meeting for connecting the proposed 220 / 33 kV Keonjhar S/S and with Turumunga S/S through 2 Nos. 220 kV ckts each. |
| 10 | LILO of 220 kV Burla - Bolangir line (one ckt) at Bolangir(PG) | Work has been started. Expected to be completed by July, 2015 |
| 11 | 220 kV Bolangir –Kesinga D/C line and LILO of one ckt at Bolangir(PG). | 220kV Bolangir - Kesinga D/C line is under construction. It is proposed to connect Bolangir (PG) through LILO arrangement of one ckt. Land dispute is yet to be resolved. |

[Action: CGM (Construction)]

Status of Discom’s action plan for power drawal from the S/Ss expected to be commissioned in near future.

| Sl. No | Name of the sub-station | Probable month of commissioning | Name of DISCOM | Action taken by Discoms |
| --- | --- | --- | --- | --- |
| 1 | 132/33kV, 2x20 MVA Banki | Charged | CESU | One no. 33kV charged |
| 2 | 132/33kV, 2x20 MVA Konark | June’15 | CESU | Line existing |
| 3 | 132/33kV, 2x31.5 MVA Samuka beach | Charged | CESU | Availing load |
| 4 | 132/33kV, 2x20 MVA Khajuriakota | December’15 | CESU | 33 kV feeder work shall be completed by July’15 |
| 5 | 132/33kV, 2x40 MVA Sarasmal | Charged (one 40 MVA charged) | WESCO Utility | Availing load |
| 6 | 132/33kV, 2x40 MVA Kalunga | July’15 | WESCO Utility |  |
| 7 | 220/33kV, 2x20 MVA Banei | Dec’15 | WESCO Utility |  |
| 8 | 132/33kV, 2x12.5 MVA Dabugaon | Charged | SOUTHCO Utility | Availing load |
| 9 | 132/33kV, 2x12.5 MVA Umerkote | Charged | SOUTHCO Utility | Availing load |
| 10 | 132/33kV, 2x20 MVA Nawapara | Charged | WESCO Utility | Availing load |
| 11 | 132/33kV, 2x20 MVA Padmapur | July’15 | WESCO Utility |  |
| 12 | 132/33kV, 2x20 MVA Udala | Dec-15 | NESCO Utility | Line existing |
| 13 | 132/33kV, 2x20 MVA Somanathpur | July’15 | NESCO Utility | 33 kV feeder exists. |

CESU stated that action is being taken for construction of 33/0.4 kV S/S at Mendhasal to avail power supply for Mendhasal area.

E2: Installation of Energy Metering at Hydro / Traction & Solar projects.

In the last meeting OHPC stated that energy meters installed are showing erroneous readings in some of the OHPC stations. It was decided that OPTCL shall instruct Secure Meters to rectify the problem. SLDC suggested for providing PT supply to the energy meters from the respective feeder line PTs.

WESCO Utility have yet to approach Rly. Authority for installation of required Class of CT & PT at their Bhalulata, Bamara and Chandiposi Traction points.

Deliberations in the meeting

WESCO stated that they have already written to Railway authority for replacement of CT & PT and meter panel at the traction points.

[Action: WESCO]

OHPC stated that the problem relating to metering of all OHPC stations has been rectified. It was decided that, Gridco shall consider those meters for commercial purpose.

[Action: GRIDCO]

E3: TTPS Issue.

Implementation of Feeder Metering

Installation of feeder meters at TTPS outgoing feeders is yet to be completed. A meeting was convened by Gridco on 3rd June’2015 with TTPS, OPTCL & SLDC to explore TTPS feeder metering. It was decided to utilize the feeder meters already commissioned by TTPS for the purpose. TTPS stated that 132 kV TTPS- Duburi ckt-I is having 5 Amp CT, while all feeders are of 1 Amp CT. Complete metering is not possible due to mismatch of CT ratio. It was decided that DGM, Meramundali shall visit the site to examine the feasibility of installation of 1 Amp CT for the said feeders. As reported by DGM, Meramundali that 0.2C accuracy Class main and check meters bearing No. ORB 52368 and ORB 52369 have been installed in the TTPS-Duburi ckt-I. The CT ratio is 600/1, while meters are configured for 400/1 CT ratio.  The meters may be configured to 600/1 CT ratio to complete the feeder metering.

Deliberations in the meeting

Since 0.2C accuracy Class main and check meters have already been installed in the 132kV TTPS-Duburi ckt-I, there is no need of installation of new meters. TTPS representative stated that line CVT does not exist while the bus PT is being utilized for metering purpose. The existing CT ratio is 600/1having 0.5 class accuracy. CGM (O&M) agreed to provide three numbers of 400/1, 0.2C accuracy class CT & CVT for installation at TTPS. It was decided to implement feeder metering for TTPS with effect from 29.06.2015 pending installation of CT CVT.  The meter reading may be computed accordingly.

[Action: GRIDCO / TTPS / SLDC / CGM (O&M)]

E4: Shifting of 33 kV line from Balasore Grid S/S yard to facilitate separation of Tfr and Balasore Alloy bays.

In the last meeting, NESCO stated that the work has already been started and shall be completed by end of June 2015.

Deliberations in the meeting

NESCO stated that shifting work is in progress and expected to be completed by July’15

E5: Major Events in the month of May’15

There is no record of major events in OPTCL system during the month of May 2015.

E6: Important Grid Incidences during the month of May’15.

Important incidents occurred during the month of May’15 were reviewed.

Deliberations in the meeting

Sr. G.M (PS) stated that very often the reports received from the field are not in proper order and not containing the relay indications and sequence with justification. At times the report is being received after considerable lapses of time, even after 2-3 days, which lead to embarrassing situation in the protection coordination sub-committee meeting of ERPC. CGM (O&M) may instruct field S/Ss to analyze the incident in coordination with E&MR officers and forward the report to SLDC.

[Action : CGM (O&M)]

E7: Outage of major transmission Elements during the month of May’15. (above 10 hrs).

Deliberations in the meeting

Outage of major transmission elements above 10 hours during the month of May’15 are due to jumper snapping and insulator failure.

C.G.M. (O&M) may please deliberate.

E8: Review of Outage Program of State Generators / Transmission elements for the month of July’2015:

Tentative Outage programme for State Generators for the month of July’2015 are as follows:

| Sl. | Station | Unit | Period | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Burla | # 1 # 6 | 18.04.15 to 31.07.15 17.02.14 to continue | Capital Maintenance Programming for R, M & U |
| 2 | Chiplima | #3 | 15.02.14 to continue | Programming for R & M |
| 3 | Balimela | # 1 | 31.01.13 to continue | Programming for R & M |
| 4 | Upper Kolab | # 1 | 01.07.15 to 30.12.15 | Capital Maintenance |

[Action: SLDC / GRIDCO /OHPC]

E9: Generation Program for the month of July’15.

Generation schedule for the month of July’15 furnished by OHPC are given below.

| Name of Hydro Gen. Station | Generation Programme (MW) | Reservoir Level as on 01.06.14 | Reservoir Level as on 01.06.15 | MDDL | High Flood Reservoir Level |
| --- | --- | --- | --- | --- | --- |
|  | July’15 (1st fortnight) | July’15 (2nd fortnight) |  |  |  |  |
| HPS, Burla | 60+40 | 60+40 | 606.62ft | 604.23ft | 590 ft. | 630 ft. |
| Balimela | 150 | 150 | 1487.90ft | 1484.70ft | 1440 ft. | 1516 ft. |
| Rengali | 150 | 150 | 115.33mt 1.78mt mtr mt | 117.21mt mt | 109.72mtr | 123.5 mtr. |
| U.Kolab | 100 | 100 | 849.75mt mt | 851.23mt | 844 mtr | 858 mtr. |
| U.Indravati | 400 | 400 | 630.40mt mt | 631.10mt mt | 625mtr | 642 mtr |
| MKD (O/D) | 30 | 30 | 2726.80ft | 2718.35ft ft | 2685 ft. | 2750 ft. |
| TOTAL | 930 | 930 |  |  |  |  |

[Action: SLDC / GRIDCO /OHPC]

PART F: OTHER ISSUES

F1:  Date and Venue of the next (88th) PSOC meeting.