Distribution list

            - The Director (Commercial), Gridco, Bhubaneswar

            - The Director (Operation), OHPC, Bhubaneswar

            - The CGM (O & M), OPTCL, Bhubaneswar

            - The CGM (Const.), OPTCL, Bhubaneswar

            - The CGM, (RT&C), OPTCL, Bhubaneswar

            - The C.G.M. (PP), GRIDCO, Bhubaneswar

            - The CGM (IT), OPTCL, Bhubaneswar

            - The Sr. G.M (C.P), OPTCL, Bhubaneswar

            - The Sr. G.M. (TP&C), OPTCL, Bhubaneswar

            - The Sr. G.M. (CPC), OPTCL, Bhubaneswar

            - The Sr. G.M.(O&M), Zone-I, Narendrapur

            - The Sr. G.M.(O&M), Zone-II, Meramundali

            - The Sr. G.M. (Telecom), OPTCL, Bhubaneswar

            - The Member Secy., (GCC), OPTCL, Bhubaneswar

            - The C.E.O., CESU, Bhubaneswar

            - The C.O.O.,WESCO Utility, Burla

            - The C.O.O., NESCO Utility, Balasore

            - The C.O.O., SOUTHCO Utility, Berhampur

            - The Vice President (O), IMFA, Choudwar

            - The D.G.M (Electrical), IbTPS, OPGC, Banharpali

            - The G.M. (O &M), CPP, NALCO, Angul

            - The DGM (O & M), NTPC (TTPS), Talcher

            - The G.M., HINDALCO, Hirakud

            - The D.G.M. (Power Distribution), RSP, Rourkela

            - The D.G.M. (Elect.), JINDAL Stainless Ltd, Duburi

            - The G.M., Vedanta Aluminium Ltd., Jharsuguda

            - The G.M.(Elect.), Bhushan Steel & Power Ltd, Budhipadar

            - The Sr. G.M. (Elect.), Bhusan Steel Limited, Meramundali

            - The S.E., Machhakund

## Odisha Power Transmission Corporation Ltd. Bhubaneswar.

Minutes of 91st PSOC meeting held on 28.11.2015 at PTC, Chandaka

List of participants is at Annexure.

Sr. G.M (Power System) welcomed all the participants to the 91st Power System Operational Coordination meeting and highlighted the system performance during the month of October’2015 and overall power scenario of the State. He also emphasized on the drawal by all the Discoms during the month.

The meeting was chaired by CGM (O&M), OPTCL.

D.G.M. (SS), SLDC took the agenda items for discussion.

The review proceeded as follows:

1: Confirmation of minutes of 90th PSOC meeting held on 17.10.2015

The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2015/4037(30), dated 05.11.2015 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting

Since no comments have received from the members, the minutes of 90th PSOC meeting was confirmed.

PART A: CONFIRMATION OF MINUTES

List of items to be discussed in the meeting are given in the subsequent parts

PART B : SYSTEM PERFORMANCE

B1: Review of Grid Performance for the month of October’2015.

## (A)  Frequency

It was noticed that, during the month of October’15, 66.83% of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 61.04% during the month of September’15. The maximum and minimum System frequency during the month was 50.21 Hz & 49.71Hz respectively.

## (B)  Grid demand

Grid demand for the month of October’15 was reviewed. The energy average consumption during the month was 3177MW. The maximum System demand of 4157 MW occurred on 16.10.2015 at 19:00 Hrs and minimum demand of 2435 MW occurred on 13.10.15 at 14:00 Hrs.

Deliberation in the meeting

It is observed that the average demand during the month of October’ 15 was increased by 40 MW and the peak demand was increased by 308 MW from that of September’15. The average energy consumption during the month has been increased by 323 MW in comparison to Sept’14. The increase in maximum demand is due to lifting of load restriction during the month.

[Action: SLDC]

(C)  Voltage Profile of important Sub Stations in OPTCL System during the month of Oct’15.

The Voltage profile at different 220 kV buses in OPTCL system during the month of October’15 was reviewed.

Deliberation in the meeting

The maximum voltage of 246.17 kV and 245.71 kV occurred at Barkote and Jaynagar 220 kV bus respectively, while Narendrapur, Bhadrak and Bolangir 220 kV bus have experienced the minimum Voltage of 182.98 kV, 196 kV and 195.95 kV respectively.

Sr. G.M (PS) stated that the Voltage profile at Jayanagar has been improved and the over Voltage has been arrested substantially. CGM (O&M) stated that high Voltage at Barkote 220 kV bus may be analyzed.

[Action: CGM (O&M)]

(D) Energy Generation / import during the month of October’15

Energy generation and exchange during the month of October’15 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2363 MU.

(E) Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of October’15.

Auto loading of all 220 kV S/Ss was reviewed. It was noticed that some of the ICTs have not been provided with energy meter.

Deliberation in the meeting.

It was decided that Energy audit meter shall be made available for all the Auto transformers and keep in functional.

[Action: CGM (O&M)]

(F) Drawal of Machhakund Power during the month of October’15

The drawal of Machhakund power during the month of October’15 was 25.288 MU against AP drawal of 27.537 MU.

In the last meeting, it was decided that Jayanagar S/S shall explore the drawal during off peak period by providing matching load. It was also decided that OHPC shall convene a meeting between Machhakund authority, Gridco, OPTCL and SLDC. Southco shall expedite the construction of 33 kV line to connect Gumuda with Akhusing S/S.

Sr. G.M (PS) shall place the requisition for providing RVDU at Jayanagar control room for display of Machhakund drawal.

Deliberations in the meeting

Sr G.M(PS) stated that in the meeting with Machhakund authority, Gridco, OHPC and SLDC held on 26th November Machhakund agreed to allow drawal up to 65 % of generation. However the load drawal can be controlled through operation of tap changer of power transformers. Sr. GM (O&M), Zone-I stated that if all the units of Machhakund are in service maximum drawal was 50 MW. In absence of any unit the drawal needs to be regulated, this is not feasible in the present configuration.  Sr. GM (Telecom) stated that providing of RVDU shall be taken up with M/s Chemtrol. SLDC shall place requisition for providing a RVDU at Jayanagar control room. Southco stated that construction of 33 kV Gumuda-Akhusing feeder is expected to be completed by March 2015.

Sr. G.M (O&M) -I stated that it is proposed for extending power supply to Rayagada Rly traction S/S from Rayagada S/S. Normally Rayagada is on Machhakund system. There may be frequent interruption of Rly. Supply with the changeover of Rayagada sub-station from Machhakund to BTH system. Moreover, traction load has adverse impact on Machhakund units for which the traction feeder has already been disconnected from Machhakund PH.  It was decided to examine for connecting Rayagada Rly traction S/S feeder with Theruvali Grid S/S.

[Action: CGM (Const.) / CGM (O&M) / OHPC / Southco / Gridco / SLDC]

(G) DISCOM Drawal during the month of October’15

The schedule and actual energy drawal by Discoms for the month of October’15 was reviewed.

Deliberation in the meeting

It was noticed that all the Discoms except WESCO were drawn  energy almost as per their schedule during the month. SLDC stated that the error in real time drawal display for CESU and NESCO has been rectified. WESCO utility had over drawn 57.4 MU during the month.

[Action: All Distribution Utilities / SLDC]

(H) Under Frequency relay operation in OPTCL System during the month of October’15.

There is no UF Relay operation occurred during the month of October’15 as the frequency had never gone beyond 48.50 Hz.

PART C- Issues raised in 115th OCC meeting of ERPC held on 20.11.2015

C.1: Handing over of 2 nos 132 kV bays at 400/220/132 kV Kuchei (Baripada) Grid S/s in Odisha.

As discussed in the Standing Committee meeting held in New Delhi on 08.02.2012, OPTCL has been allotted 4 nos. 132 kV bay at Kuchei Grid S/s in Odisha. During site visit by OPTCL for connection of 2 nos.132kV feeders from Kuchei –Jaleswar line, there is not sufficient space for termination. It was noticed that 2 nos. equipped 132kV bay meant for Jharkhand is available at Kuchei S/s lying un-utilised and is learnt that the same bays shall not be used in near future. It was also informed that JUVNL is yet to construct 132kV line that will be connected with these 2 nos. bay. Since these 2 nos. bay cannot be used by Jharkhand and the guarantee period of equipment / materials will expire, it is better OPTCL, can immediately use these bays for its line, which is going to be completed within next 3 to 4 months.

JUSNL agreed to spare the bays for use of OPTCL.

Deliberation in the meeting

It was decided that CGM (Const.) may explore the connectivity of S/Ss with Baripada (PG).

[Action: CGM (Construction)]

C.2: Furnishing of data for Electricity Generation Targets for the year 2016-17

You are aware that the annual exercise of assessment and finalization of the generation targets and the planned maintenance schedules of the generating units for the year 2016-17 is being initiated by CEA. Although the generation performance of the various stations and their planned & unscheduled outages are regularly monitored in CEA but it is felt that a more realistic projection of month-wise generation in the coming year could be made by the respective Station Authorities.

While monitoring the generation performance during the current financial year, it has been observed that power utilities are facing the problem of loss of generation due to no / low schedules and losses accounted on other technical and commercial egresses. Accordingly, it is requested that the following inputs may kindly be submitted to this office as per the enclosed

Annexure:

i) (Annex- I (point no. 1 to 5)) The unit-wise proposed generation during 2016-17 (monthly and yearly) along with anticipated generation during 2015-16, the anticipated loss of generation on account of various constraints (e.g. Grid Constraints/ Low schedules/ Reserve shutdown /high fuel cost) may be accounted and furnish with necessary details. The details of units like boiler/ turbine make, date of commissioning etc may also be furnished.

ii) (Annex –I (point no. 6)) Utilities who have their Power Purchase Agreement (PPA) with various Discoms, Trader, states etc. and the details may be furnished in MW for Long and Medium term Agreement for assessing the expected generation for next year.

iii) (Annex- I (point no 7 (a) and (b)) The details of coal linkages from coal agencies and availability of gas/ liquid fuel.

iv) (Annex – I (point no. 8)) Unit wise cost of generation and rate of sale of power.

v) (Annex- II) Detailed unit-wise schedule of Planned Maintenance (approved by the respective Regional Power Committees) and R&M to be carried out during 2016-17 may also be furnished.

The information may please be furnished electronically at the email address

targetopmcea@gmail.com, kiran.meena@nic.in with a copy to ERPC (e-mail: mserpcpower@nic.in) latest by 31st October, 2015.

For any inconvenience in submission of data you may contact Mrs. Kiran Meena, Assistant Director, CEA, Ph- 011-26732684, Mob.08588831051 or write to the following address:

Chief Engineer (OPM Division), Room No.604 (N), Central Electricity Authority, Sewa Bhawan,

R.K. Puram, New Delhi-110066, Ph. 011-26105026 (Telefax)

For your convenience the input formats are also being made available at CEA website http://www.cea.nic.in in Whats New/ Flash News and ERPC website www.erpc.gov.in.

NTPC Farakka, TSTPS-Kaniha, OHPC, DPL and DGPC have submitted the relevant information

In the last meeting all Generators were requested to submit the data to CEA directly with copy to Gridco / SLDC

It was decided in the ERPC meeting that OPGC shall furnish the required data to CEA by end of this month.

Deliberation in the meeting

SLDC has furnished the generation projection for OPGC for FY2016-17

C.3: Commissioning of 400 kV Ind-Bharath to Jharsuguda D/C (dedicated line)

In 114th OCC, Ind-Barath updated the status as “The unit is also expected to be stabilized by November, 2015.”

Gridco may note.

C.4: Status of PLCC system installed in Eastern Region

In 30th TCC/ERPC, Powergrid agreed to restore the PLCC system at both ends (its own end as well as the constituent end) of a line wherein the other ends are not operational for some reasons or others as one time job.

111th OCC advised Powergrid to place their requirement along with cost estimate as per the Powergrid norms.

In 114th OCC, Powergrid ER-II has submitted the details of their control area. Subsequently, Powergrid-Odisha has submitted the details vide letter dated 6th November, 2015 along with the cost estimate.

Deliberation in the meeting

Sr. G.M (Telecom) stated that since most of the links are covered under optical fibre project, except 220 kV Budhipadar-Korba, 132 kV Joda-Kenduposi, Indravati-Indravati-PG and Rengali switchyard-Rengali (PG), PLCC is required only for Budhipadar-Korba and Joda-Kenduposi lines. Indravati & Rengali will be done through OPGW. CGM (O&M) shall intimate POWERGRID accordingly.

[Action: C.G.M (O&M)]

C.5: Third Party Protection Audit

Status of 1st Third Party Protection Audit:

The compliance status of 1st Third Party Protection Audit observations is as follows:

| Name of Constituents | Observations | Total Complied | % of Compliance |
| --- | --- | --- | --- |
| Odisha | 59 | 38 | 64.41 |

As deliberated in the OCC, OPTCL have complied 39 Nos observations out of total 49. The balance 10 nos belong to OHPC and OPGC. OHPC stated that they have complied their observations.

Member Secretary suggested to apply for PSDF for compliance of the observations.

Deliberation in the meeting

C. G.M (O&M) stated that OPTCL shall apply for 2nd phase PSDF for compliance of the observations.

[Action: C.G.M (O&M)]

C.6: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA.

NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In 113th OCC, Member Secretary informed that during interaction with consultants of Grid Study Committee, NLDC agreed that they will plan for conducting workshops on crisis management plan for Cyber Security and few workshops will also be held in Eastern Region.

In the last PSOC meeting, it was decided that CGM (IT) shall examine and prepare a Crisis Management Plan for countering the cyber attacks for OPTCL.

Deliberation on the meeting

It was decided that CGM (IT) shall examine and prepare a Crisis Management Plan for countering the cyber attacks for OPTCL.

[Action: C.G.M (IT)]

C.7: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.

In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In 85th OCC NTPC informed that, NTPC-Farakka has been certified with IS 18001. Other constituents including OHPC requested to interact with BIS with intimation to ERPC and get certified as per CEA direction. The matter is getting reviewed by highest authorities with top priority.

In 88th OCC NTPC informed that, all NTPC stations in Eastern Region are certified with IS 18001.

NHPC informed that, Teesta is also certified with IS 18001. After that, OHPC and CESC informed that their stations are certified with IS18001.

In 104th OCC, WBPDCL informed that Bandel TPS is certified with IS 18001.

OPTCL vide letter No.TB-SO-MISC-9/2010/1914 dated 20.12.2014 had proposed to go for IS 18001:2007 certification as per direction of CEA.

It was decided in the last PSOC meeting that CGM (O&M) may remind BIS again.

Deliberation in the meeting

CGM (O&M) stated that BIS is not responding for certification. SLDC may be get clarified from ERPC whether ISO or BIS is required.

[CGM (O&M)/ Sr. G.M (PS)]

C.8: Pollution mapping for Eastern Region

The Pollution Mapping work in ER was started with on-site measurement of ESDD and NSDD.

The latest available status is as follows:

| Utility | Scope | Installed Locations | Number of locations where 1st set of Measurements Completed |
| --- | --- | --- | --- |
| OPTCL | 164 | 102 | 99 |

OCC advised all constituents to complete the 1st set of measurements and send to Powergrid/ CPRI. Powergrid vide mail dated 5th November, 2015 requested to complete the 2nd set of measurements by end of Novemebr, 2015, as it is already passed 4 months after completion of 1st set of measurements for the most of the locations.

Powergrid also requested to provide probable pollution sources and direction details near the site with specific details e.g. type of pollution sources (factories, Brick Kiln, Agricultural pollutant, Saline pollutant from sea coast), direction form site, distance from site etc.

Deliberation in the meeting

CGM (O&M) stated that only Discom locations are left for non availability of testing kit. Since CPRI is not responding for supply of more kits, the existing kits will be diverted to Discom locations after completion of measurement for O&M locations.

[Action: CGM (O&M)/ Discoms]

C.9: Mock Black start exercises in Eastern Region – ERLDC

| Sl. No. | Name of Hydro Station | Schedule (1st) | Tentative Date | Schedule (2nd) |
| --- | --- | --- | --- | --- |
| 1 | U.Kolab | Last week of May, 2015 | Done on 16/07/2015 | Last Week of January, 16 |
| 2 | Rengali | 2nd week of June 2015 | Done on 13/10/2015 | Last week of November, 15 |
| 3 | U. Indravati | 3rd week of June 2015 | Done on 16/07/2015 | 2nd week of February 2016 |
| 4 | Balimela | 1st week of November,15 | Done on 24/11/2015 | 1st week of March 2016 |
| 5 | Burla |  | January 2016 |  |

A procedure for conducting mock black start exercise for Burla PH need to be developed by SLDC in coordination with OHPC.

Deliberations in the meeting

Mock black start for Balimela HEP was done on dated 27.11.2015. It was noticed that synchronization could not be done at Balimela end due to B/C breaker problem as well as Jayanagar end due to some problem. Since the black start programme is being forwarded before two weeks, the required switching operations should be checked and problems if any should be rectified before conducting the exercise.

SLDC stated that procedure for conducting mock black start at Burla is being developed after examining the facility for providing radial load.

[Action: SLDC/O&M / OHPC]

C.10: Restricted Governor Mode of Operation.

The latest status of units of ER under RGMO is available at ERPC website (http://www.erpc.gov.in/) under Operation>Important data.

In 108th OCC, ERLDC informed that the RGMO/FGMO response of the generators needs monitoring on continuous basis.

OCC advised ERLDC to intimate the event of sudden drop in frequency to the generators and requested all generators to provide the RGMO/FGMO response data to ERLDC during the said incidents.

ERLDC informed that on 12.10.2015 there was sudden load loss of 900 MW in NR and they observed 0.11 Hz change in the grid frequency.

As per the data of ERLDC they have received the RGMO/FGMO response only from Burla, Kahalgaon, Teesta-V and SSL generators. The response of other generators are not satisfactory.

In the OCC meeting, reports received from OPGC & Chiplima PH have been handed over to ERLDC.

In the OCC meeting, it was decided that hydro units of 10MW capacity & thermal units of 200MW capacity shall intimate the response of governor to ERLDC.

ERLDC intimated that a new web group was formed for sharing governor response of various generator in ER. The url of the group is https://in.groups.yahoo.com/neo/groups/er_gov_respons/info

ERLDC requested to send email ids (preferably Yahoo mail ids) of the Generators where invitation will be sent. Governor response for the event of 12-11-2015 at 23:05 hrs based on ERLDC SCADA data is already posted in the group.

CERC in the RoP dated 14.07.15 in Petition No. 84/MP/2015 filed by NRLDC has directed as under:

“10. The Commission also directed SLDCs to approach their respective SERCs to initiate appropriate action under the Act against the State generating stations which have not provided adequate primary response during both grid events reported by the petitioner.”

Deliberations in the meeting

All the generating stations including CGP may forward their Email Id to ERLDC and ERPC

[Action: All Generators / CGPs]

C.11: Information regarding commissioning of new transmission element

1.400kv Meramundali-New Duburi-I was charged for the first time at 20:20hrs of 19/10/15

2.400kV Jamshedpur-Rourkela-II (Looping up to dead end tower of Chaibasa) was charged for the first time at 19:46hrs of 31/10/15.

C.12: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.

In 110th OCC, OPTCL updated the completion schedule of inter-connecting system as follows:

| Sl. No. | Name of the transmission line | Completion schedule |
| --- | --- | --- |
| 1. | 2 X 315MVA 400/220kV Bolangir S/s |
| a. | LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir S/S. | Severe ROW problem, December’2015 |
| b. | LILO of one circuit of Katapalli-Sadeipalli 220 kV D/C line at Bolangir S/S. | December’2015 |
| 2. | 400/220 kV Keonjhar S/S. |
| a. | Keonjhar (PG)-Keonjhar (OPTCL) 220 kV D/C line | Tender processed |
| b. | Keonjhar (PG)-Turumunga (OPTCL) 220 kV D/C Line. | Yet to be awarded |
| 3. | 400/220 kV Pandiabil Grid S/s |
| a. | Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line | It will take 1 year for completion. |
| b. | LILO of one circuit of Atri-Puri (Samangara) 220 kV D/C line at Pandiabil (PG) | Work order issued. |

[Action: CGM (O&M)/ GM (Const)]

C.13: Dynamic data of Generator Models required in PSSE for Simulations -ERLDC

In the OCC meeting, it was decided that by 15th December 2015, all Generators including CGPs having capacity of 60MW & above shall furnish ERLDC, the generator parameters including exciter, governor, PSS required for modeling in PSSE for simulation. Further, the Generators shall intimate their email Id to ERLDC / ERPC.

Email Id of ERLDC	: erldcprotection@gmail.com

Email Id of ERPC	: mserpc-power@nic.in

Deliberations in the meeting

It was decided that OHPC, OPGC and TTPS shall forward their Email Id to ERPC directly

[Action: OHPC / OPGC / TTPS / CGPs]

C.14: Restoration of SCADA data

Updated latest status is circulated in the meeting. During deliberations in 99th OCC it was pointed out by most of the constituents that SCADA problem in many locations are due to behind the schedule progress of work on the part of CTU/PGCIL. OCC advised Powergrid / CTU to expedite and restore at least the priority RTUs by 31st July, 2014.

Updated status as updated in SCADA meeting which was held on 28th January’15 is circulated in the meeting.

The status as updated in the SCADA meeting is as given below:

- List of additional elements/feeders whose data is not available – station under ULDC project:

| Sl no | Name of Utility | KV | Name of station | Reason for non-reporting | Latest status |
| --- | --- | --- | --- | --- | --- |
| 1 | OPTCL | 220 | Vedanta (9x135 MW) | No status points are available. | No isolator status is available. MW/ MVAR not available for Sterlite 1/2 line, station transformer / Smelter. CBs of Bus coupler not available. Bus-1 KV/ HZ not available. Expected to be completed by 1st week of December |

iv) The updated status of telemetry of OPTCL Sub-Stations under ULDC project is project as given below:

| S/n | Name of RTU Locations | Latest status |
| --- | --- | --- |
| 1 | Nalco | OPTCL informed that RTU is reporting but intermittent since it was not configured properly. The issue was already taken up with Nalco and it will be resolved soon. OPTCL has resolved the issue. Unit 5, 7 & 9 generation data is not available due to reverse CT polarity. |

v) RTU telemetry provided but data are intermittent / new element not wired.

| SL No | Name of station/ Utility | Reason for non reporting | Latest status |
| --- | --- | --- | --- |
| II | JSPL (Meramundali - 400) | Most of the data not available. | Analog data available. Digital data (status of CB, isolator) not available. |

Deliberations in the meeting

Sr. G.M (Telecom) stated that Vedanta Ltd may explore for alternate Vender for rectification of problem at their CGP.

[Sr. G.M (Telecom) / Vedanta / JSPL / NALCO /GCC]

C.15: Status of commissioning of generating station and transmission elements

New transmission elements:

| Sl No. | Name of Element | Expected date |
| --- | --- | --- |
| 1 | 400 kV IB-Meramundali D/C | Ckt-I by Dec’15, Ckt-II by March’2016 |
| 2 | 220 kV Bidansai-Cuttack D/C | March’2016 |

[Action: C.G.M. (Const.)]

C.17: Energy Generation data management from Renewable Energy Sources.

It was suggested in the OCC meeting that the details of newly integrated / upcoming RE sources shall be intimated to ERLDC.

[Action: GRIDCO]

PART-D – Operational Issues

D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of October’15:

It is noticed that drawal of all the Discom utilities except WESCO are almost as per the schedule energy, while WESCO had overdrawn a substantial quantum of power to the tune of 57 MU during the month.

Deliberations in the meeting.

SLDC stated that maximum number of messages were issued to WESCO for compliance of drawal schedule. All the Discoms were advised to remain in the schedule to maintain grid discipline and security.

[Action: WESCO]

D.2: Reduction of off-peak drawal

It is noticed that the State’s demand is being reduced to 2000 – 2100 MW during off peak period forcing injection of power to the grid even after backing down of State’s hydro generation & surrender of State’s central sector share. During the said period the frequency normally remains high resulting injection of power at ‘ZERO’ cost & sometimes with penalty.

Deliberations in the meeting

Director (Commerce) stated that the Discoms should not restrict their demand during off-peak period

[Action: All Discom utilities]

D.3: Availability of data of real time power flow of feeders covered under Under-frequency Load shedding scheme (UFLS) and lower relief expected to obtained in real time system operation

In the last meeting Sr. G.M (Telecom) stated that MFMs have already been installed at the following S/Ss.

- Khurda			2. Bhanjanagar		3. Jayanagar		4. Theruvali

- Boinda			6. Chainpal			7. Dhenkanal		8. Balasore

9. Bhadrak		10. Jajpur Road		11. Bargarh		12. Bhadrak

13. Bolangir		14. Bolangir (New)		15. Rourkela		16. Sambalpur

Integration will be done soon after joint testing with EMR.

Deliberations in the meeting.

Sr. G.M (Telecom) stated that data availability for all feeders have been completed except three Nos. of S/Ss namely Boinda, Dhenkanal and Kendrapada, for which the CT/ PT output is required. It was decided that all the remaining S/Ss may be completed before the next meeting in coordination with the respective EMR wing, as the matter has been considerably delayed.

[Action: Sr. G.M (Telecom) / O&M]

D.4. High Voltage at 400 kV Meramundali & Duburi S/S_ Reactive Power Injection by OPTCL

Persistent high Voltage is being observed at Meramundali & Duburi 400 kV buses. Since these buses are the inter State exchange points, Reactive power injection penalty is being charged to Gridco. It is learnt that one no of 50 MVAr line reactor at Meramundali is not functioning. O&M may take action for rectification of the same early. It may also be examined for installation of 2nd reactor at Duburi to arrest the high Voltage. Further Powergrid may be requested to shift the line reactor of the 400 kV Baripada- New Duburi-Mendhasal ckt from Mendhasal to New Duburi.

It is also noticed that Balimela is not allowing for keeping 220 kV Balimela-Jayanagar one ckt in service in case of low generation at Balimela HEP resulting VAr injection to the grid from the State.

Deliberations in the meeting

SLDC stated that reactor at line reactor at Meramundali may be rectified early and Powergrid may be requested to enhance the capacity of reactor at New Duburi. OHPC stated that one ckt of 220 kV Balimela-Jayanagar is being kept in service during low generation.

[Action: C.G.M (O&M)]

D.5: Revival of Station Transformer for Station Auxiliary supply at Balimela HEP.

It was suggested in earlier meetings for revival of station supply for Balimela HEP from Balimela Grid S/S.

Deliberations in the meeting

OHPC stated that revival of station supply from Balimele 220/33 kV S/S will be done by end of January’ 2016.

[Action: OHPC]

D.6: Prolonged outage of transmission elements and tentative revival dates

The tentative revival dates of transmission elements are updated in the last meeting are as follows:

| Sl.No | Name of transmission element | Reason of outage | Probable date of revival |
| --- | --- | --- | --- |
| 1 | 220kV Jayanagar-Theruvali ckt-III breaker | Breaker already erected but not commissioned. Isolator problem | December 2015 |
| 2 | 220/132 kV, 100 MVA Auto-II at Duburi |  | Spares received. Work will be started soon. |
| 3 | 220/132 kV, 100 MVA Auto-I, Bhadarak |  | December’ 2015 |

C.G.M. (O&M) may please update the status.

D.7: Communication issues

- Installation of communication equipment by CGPs / Industries.

The status of data communication from CGPs as deliberated in the last meeting is as follows

| Sl. No | Name of CGP | Present status |
| --- | --- | --- |
| 1 | M/s IFFCO, Paradeep | Outdoor commissioning work completed. RTU was locally tested. After replacement of the faulty CVT data will be integrated. CVT is expected to be shifted from Kuanramunda by 1st Dec’2015. |
| 2 | M/s MSP Mettalicks | PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited. |
| 3 | M/s NINL, Duburi | M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. |
| 4 | M/s Adhunik Metalliks | RTU is integrated and analog data available. Digital data is yet to be available. |
| 5 | M/s Rohit Ferrotech | PLCC established and inspection by Telecom Engineers completed. Data base has already been prepared by OPTCL. |
| 6 | M/s VAL, Jharsuguda | Included in OCC, ERPC agenda |

It was decided that OPTCL, while issuing Technical clearance shall consider the provisions also. OPTCL may also approach OERC in this regard.

Deliberations in the meeting

It was decided that GCC, OPTCL may file a case before the OERC against those CGPs not complying the data communication provisions with SLDC.

[Action: GCC / O&M / Sr. G.M. (Telecom.)]

- Interruption of SCADA.

It is noticed that there is frequent interruption of SCADA System, resulting problem in real time operation. Action may be taken to avoid such frequent interruption of SCADA.

In the last meeting, Sr. G.M (Telecom) stated that Powergrid link between Rourkela-Kaniha is being used for data transfer. The link is not healthy due to heavy fibre loss. Powergrid have proposed to upgrade the existing SDH equipment to STM16. Work order has already been awarded.

In the last meeting Sr. G.M (Telecom) stated that up gradation of the existing SDH equipment to STM16 in progress.

Deliberations in the meeting

Sr. G.M. (Telecom) stated that Powergrid will complete the work by 1st week of December’2015

[Action: Sr. G.M (Telecom)]

- Integration of new element.

M/s SSL-SEZ became a consumer of WESCO Utility with effect from 20.03.2015 and importing power through intra State open access from its CGP at Jharsuguda as well as from other utility. The drawal of SSL-SEZ needs to be integrated to SCADA to ascertain WESCO Utility drawal and State demand on real time basis. Since the SSL is reporting to ERLDC, Sr. G.M (Telecom) may write to ERLDC for integration of SSL-SEZ drawal in to the SCADA.

At present generation data of SSL-IPP connected with State Transmission System is being received through ERLDC. But most of the times the data become suspected. SEZ drawal date is yet to be received. However, the calculated figure is being displayed. Sr. G.M (Telcom) may write to SSL to transmit uninterrupted date of IPP generation as well as integrate SEZ drawal to ERLDC.

It was decided that Sr. G.M. (Telecom) shall write issue reminder to M/s Vedanta Ltd for functioning the data communication system.

Deliberations in the meeting

Sr. G.M. (Telecom) stated that Vedanta SEZ drawal is being reported. IPP generation is not being received. Vedanta stated that reporting of IPP generation will be done by 10th December’2015.

[Action: Vedanta Ltd / Sr. G.M (Telecom)]

D.8. Islanding Scheme of Ib TPS

The islanding scheme for IbTPS has already been commissioned but not functioning due to non- incorporate the trip commands to the breakers at Budhipadar from the Islanding Relay. This has already been discussed in the 81st PSOC meeting, wherein Telecom wing of OPTCL assured to complete the optical fibre link, provided IbTPs allow for working in their premises. Ib TPS had also agreed to allow them. The link is yet to be completed yet.

Deliberations in the meeting

Sr. G.M. (Telecom) stated that all works have been completed. It was decided that Sr. G.M (Telecom) shall intimate the same to Ib TPS and mark a copy to ERPC.

[Action: Sr. G.M. (Telecom) / Ib TPS]

D.9: Display of dashboard data.

The status of lease line of all Discoms as deliberated in the meeting are as detailed.

| Sl. No | Dist. Utility | Status of leased line | Remarks |
| --- | --- | --- | --- |
| 1 | CESU | Already connected. RVDU commissioned | Data display available |
| 2 | WESCO | Already connected. RVDU commissioned | Data display available |
| 3 | NESCO | Already connected. RVDU commissioned | Data display available |
| 4 | SOUTHCO | Already connected. RVDU commissioned | Data display available |

The Dash board shall be kept in parallel with RDVU for three months.

Deliberations in the meeting

It was reported by CESU and other Discoms that the data of RVDU and Dashboard data are not matching. Also the RVDU data are remaining in hanging conditions. Telecom and IT may collect feedback and rectify the problems.

CGM (IT) / Sr. G.M (Telecom) / SLDC / All Dist. Utilities may please update the functioning status.

D.10: Web based drawal / generation scheduling.

SLDC is going to implement web based drawal / generation scheduling for Dist. Utilities and State generating stations including IPPs and CGPs soon. A demo has been organized on 29.07.15.

In the last meeting, CGM (IT) stated that, web based generation scheduling module for State generating stations has been already been developed by IT wing. Modules for Discom and CGP / IPP shall be made available before the next PSOC meeting. After approval by the stake holders the same shall be go live from September’15. All Users were requested to forward their respective schedule in the prescribed format.

In the last meeting IT representative deliberated that SLDC shall finalize the date preferably during first week of November-2015 for one day demonstration cum training programme at SLDC for web base scheduling.

Deliberations in the meeting

SLDC may finalize a date and intimate to CGM (IT) for conducting the training.

[Action: CGM (IT) / Discoms / OHPC / NTPC / OPGC / CGPs & SLDC]

D.11: Replacement of Battery bank at SLDC data centre.

It is noticed that the existing battery bank at SLDC data centre have become defunct and unable to supply back up in case of power failure. SLDC data centre experienced severe problem from 19.09.15 to 21.09.15 due to cable fault causing interruption of power. The DG set has to run continuously during the above period to provide power supply to the data centre. This issue has already been brought to the notice of IT wing of OPTCL, entrusted for maintenance of the Data Centre.

In the last meeting IT representative deliberated that tender has already been floated for replacement of Battery bank at SLDC data centre.

Deliberations in the meeting

DGM (IT) stated that replacement of Battery bank at SLDC data centre will be done by 10th December’2015.

[Action: CGM (IT) ]

D.12: DISCOM Issues

CESU

- Mismatch of displayed and actual drawal given in the bill and Fixed drawal assumption for inter Discom 33 kV feeders lead to inaccurate drawal prediction on day-ahead basis.

- RVDU installed at CESU H.O. is not functioning some times and Dashboard data is not matching with the RVDU.

- Spare 33 kV bay at Chainpal, Argul, Bidanasi & Kalrangi Grid S/Ss.

- Minimise interruption for Rly Traction S/Ss such as Solari, Kaipadar Road, Kendrapara Road. Joranda Road & Gorkhanath.

- Power supply to ESI hospital (2 MVA)

- Commissioning of 132/33 kV S/S at Nadiagurudi by March 2016 to cater the up coming load

- Up gradation of 132 kV Ransingpur-Kesura ckt with replacement of existing conductor by HTLS.

- Commissioning of 220/132 kV S/S at Atri by December2015 and 220/132 kV Cuttack Grid S/S by end of this winter.

- Commissioning of 132 kV Salipur-Kendrapara 2nd ckt.

Deliberations in the meeting

SLDC stated that the drawal of Discoms displayed in the control room are based on the SCADA data while actual drawal billed are energy meter data. The drawal is for monitoring purpose only. CESU may compute the “error correction factor” comparing both the data and adopt for their drawal estimation.

As stated earlier meetings, presently AREVA and CHEMTROLS system are in parallel. RVDU data is from Chemtrols system while Dashboard data is from AREVA system. Both the data may not match. However, AREVA system will be closed by December2015.

The other issues raised by CESU are mainly O&M issues. CESU may approach O&M through meeting to resolve those issues. The discussion in the meeting may be placed in the next PSOC meeting.

[Action: CESU / O&M)]

WESCO

- Drawal of energy by solar projects is not being deducted from WESCO’s BST bill.

- Mismatching of RVDU display with WESCO drawal – non-functioning since 23.11.15

- Display of Open access drawal, EHT consumers’ & all grid sub-station drawal in RVDU.

Deliberations in the meeting

The issue for deduction of energy drawal by Solar projects from Discom BSP bill had been discussed in earlier meetings, wherein it was decided for deduction of the quantum of energy from BSP bill. Director (Commerce) has also agreed to the above decision.

Mismatch of data has already been deliberated at CESU issue.

[Action: GRIDCO/ WESCO]

PART E: OPERATIONAL PLANNING

The status of commissioning of new transmission elements is as follows:

| Sl. No | Transmission element details | Present Status |
| --- | --- | --- |
| 1 | Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line | Work has already been started. Expected to be completed by March 2016. |
| 2 | Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt | Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal, which is under progress. |
| 3 | Commissioning of 400 kV Ib-Meramundali D/C line. | 400kV Ib-Lapanga-Meramundali ckt-1 will be charged by 15th December’2015. 2nd ckt is expected to be charged by March’2016. |
| 4 | Commissioning of 220 kV Bidanasi-Cuttack line | Work in progress and expected to be completed by March 2016. |
| 5 | Commissioning of 220/132 kV Cuttack S/S | Work in progress and expected to be completed by December 2015. |
| 6 | Commissioning of 132 kV Baripada (PG)-Jaleswar line | Work has already been started, which will be completed by December 2015. |
| 7 | Commissioning of 220/132 kV Kesinga S/S | Work under progress. Expected by September 2016. |
| 8 | Connectivity to Keonjhar PG | Proposal is mooted to be placed in the BoD meeting for connecting the proposed 220 / 33 kV Keonjhar S/S and with Turumunga S/S through 2 Nos. 220 kV ckts each. |
| 9 | LILO of 220 kV Burla - Bolangir line (one ckt) at Bolangir(PG) | Work has been started. Expected to be completed by December, 2015 |
| 10 | 220 kV Bolangir –Kesinga D/C line and LILO of one ckt at Bolangir(PG). | 220kV Bolangir - Kesinga D/C line is under construction. It is proposed to connect Bolangir (PG) through LILO arrangement of one ckt. Land dispute is yet to be resolved. |

Status of Discom’s action plan for power drawal from the S/Ss expected to be commissioned in near future.

| Sl. No | Name of the sub-station | Probable month of commissioning | Name of DISCOM | Action taken by Discoms |
| --- | --- | --- | --- | --- |
| 1 | 132/33kV, 2x20 MVA Khajuriakota | December’15 | CESU | By July’15 |
| 2 | 132/33kV, 2x40 MVA Kalunga | Charged on 03.11.15 | WESCO Utility |  |
| 3 | 220/33kV, 2x20 MVA Banei | Dec’15 | WESCO Utility |  |
| 4 | 132/33kV, 2x20 MVA Padmapur | Dec’15 | WESCO Utility |  |
| 5 | 132/33kV, 2x20 MVA Udala | Dec-15 | NESCO Utility | Line existing |
| 6 | 132/33kV, 2x20 MVA Somanathpur | Sept’15 | NESCO Utility | 33 kV feeder existing. |

CESU stated that action is being taken for construction of 33/0.4 kV S/S at Mendhasal to avail power supply for Mendhasal area.

It was suggested that WESCO shall explore the work for diversion of 11kV line at Sarsmal (Jharsuguda) and connecting 33 kV feeders with Lapanga Grid. The progress in this regard may be placed in the next meeting.

All DISCOMS may update the status / CGM(O&M) & CGM(Const.) may please deliberate.

E.2: Installation of Energy Metering at Hydro / Traction & Solar projects.

In the last meeting it was suggested to consider the energy meter reading of newly installed ABT compliance energy meters for billing as well as accounting purpose. The PPA for “joint meter reading” shall be modified, if required.

Deliberations in the meting

OHPC stated that billing for all the OHPC stations except Upper Kolab is being done from the newly installed energy meters. The energy meters at Upper Kolab is showing problem, which may be rectified soon.

[Action: GRIDCO / OHPC / O&M]

E.3: TTPS Issue.

Implementation of Feeder Metering

In the last meeting TTPS deliberated that all the meters were tested & calibrated by the STL on 09.10.2015. The 132kV CTs for TTPS-Duburi-1 have been replaced. Further, as per the PPA dated 08.03.1995, the energy meters are to be installed at GT end. Since the meter locations will be shifted to feeders, the corresponding clause in the PPA is required to be amended. Accordingly, the proposal has been sent to the competent authority of NTPC for approval.

As per the decision by Gridco the feeder metering has been implemented with effect from 1st October. SLDC has prepared the Deviation charge bill considering the feeder meter data for the month of October.

TTPS in their letter No.045/GGM/TTPS, Dated. 20.11.2015 addressed to CGM (PP) Gridco pointed out that, as per clause 7(1), 1st proviso of CEA (Installation and operation of Energy meters) Regulation, 2006 as amended in 2010 “ for existing stations the location of Main, Check and Standby meters shall not be changed unless permitted by the Authority”.

In the present case, for the first time, energy meters have been installed at the interface points, which should have been installed earlier, without changing the position of the existing meters. As such the regulation as mentioned by TTPS is not applicable. However the existing meters will be treated as standby meters.

Further, TTPS had also agreed to consider these feeder meters for Energy Accounting after being tested by STL.

Deliberations in the meeting

TTPS stated that they have written to CEA for clearance to the feeder meter installation, in view of which the metering may be considered from 1st November’ 2015. Director (Commerce) stated that installation of feeder meters will be informed to CEA by Gridco and NTPC.

[Action: GRIDCO / TTPS]

E.4: Major Events in the month of October’15

15.10.2015: 132/33 kV, 20 MVA 3rd Transformer at Angul S/S charged.

16.10.2015: 132/33 kV, 2x20 MVA Marsaghai S/S charged.

26.10.2015: 132/33 kV, 20 MVA 3rd Transformer at Junagarh S/S charged.

31.10.2015: 132/33 kV, 20 MVA 2nd Transformer at Konark S/S charged.

E.5: Important Grid Incidences during the month of October’15.

No major incident occurred during the month.

E.6: Outage of major transmission Elements during the month of October’15. (above 10 hrs).

Outage of major transmission elements above 10 hours during the month of October was reviewed.

E.7:  Review of Outage Program of State Generators / Transmission elements for the month of December’2015:

Tentative Outage programme for State Generators for the month of November’2015 are as follows:

| Sl. | Station | Unit | Period | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Burla | # 2 # 3 # 6 | 16.12.15 to 15.05.16 02.11.15 to 30.11.15 17.02.14 to continue | Capital Maintenance Annual Maintenance Programming for R, M & U |
| 2 | Chiplima | #3 | 15.02.14 to continue | Programming for R & M |
| 3 | Balimela | # 1 # 7 | 31.01.13 to continue 16.12.15 to 10.01.16 | TGB problem and started R,M & U Annual maintenance |
| 4 | Upper Kolab | # 1 | 29.07.15 to 31.01.16 | Capital Maintenance |
| 5 | Rengali | # 4 # 5 | 02.11.15 to 31.11.15 01.12.15 to 31.12.15 | Annual maintenance Annual maintenance |
| 6 | Upper Indravati | # 3 | 23.11.15 to 30.04.16 | Capital Maintenance |

OHPC / SLDC may deliberate.

E.8: Revised calculation of PAFM for OHPC stations

As per the direction of OERC, in case of any unit under R&M / Capital maintenance, the Installed capacity of that unit shall not be considered for determination of PAFM of the power station. OHPC has to intimate SLDC the details of units under R&M / Capital maintenance along with the approval of OERC for determination of PAFM of the station. It is noticed that OHPC is intimating such cases after a lapses of considerable time to the tune of 2 years.

Deliberations in the meeting

OHPC has agreed to intimate the capital maintenance programe as soon as approved in future.

[Action: OHPC]

E.9: Generation Program for the month of December’15.

Generation schedule for the month of December’15 furnished by OHPC are given below.

| Name of Hydro Gen. Station | Generation Programme (MW) | Reservoir Level as on 15.11.14 | Reservoir Level as on 15.11.15 | MDDL | High Flood Reservoir Level |
| --- | --- | --- | --- | --- | --- |
|  | Dec’15 (1st fortnight) | Dec’15 (2nd fortnight) |  |  |  |  |
| HPS, Burla | 30+20 | 30+20 | 629.31ft | 625.56ft | 590 ft. | 630 ft. |
| Balimela | 40 | 40 | 1514.40ft | 1500.60ft | 1440 ft. | 1516 ft. |
| Rengali | 20 | 20 | 122.02mt 1.78mt mtr mt | 118.94mt mt | 109.72mtr | 123.5 mtr. |
| U.Kolab | 40 | 40 | 856.90mt mt | 855.87mt | 844 mtr | 858 mtr. |
| U. Indravati | 50 | 50 | 640.43mt | 634.86mt mt | 625mtr | 642 mtr |
| MKD (O/D) | 30 | 30 | 2748.50ft | 2747.25ft | 2685 ft. | 2750 ft. |
| TOTAL | 230 | 230 |  |  |  |  |

Note: As decided in the meeting at the chamber of Hon’ble Minister, Energy dated 12.11.2015, SLDC shall maintain the hydro generation between 150 to 200 MW (excluding Machhakund share) as per the real time requirement.

E.10: RSP (SAIL), Rourkela Issue.

- Review of relay settings of Tarkera-RSP 220kV feeders at Tarkera.

- Drawal clearance during shutdown of 60MW unit-1 of NSPCL from 01.10.15 to 20.10.15.

- Clearance for construction of two 220kV bays at Tarkera grid sub-station and construction of 220kV D/C line.

Deliberations in the meeting

CGM (O&M) stated that WESCO as not intimated regarding enhancement of contract demand RSP. Field inspection report for feasibility of 220 kV bay at Tarkera is yet to be received.

[WESCO/ CGM (O&M) / CGM (Const)]

E11. Jindal Stainless Ltd. Issue

- In case of power import from other than the incumbent Discom (NESCO) through Open Access transaction, the energy accounting and RST billing mechanism may be clarified.

- To maintain the 220kV Bus Voltage of New Duburi sub-station between 227 to 230 kV so that JSL can utilize its generator VAr capability for demand management and avoid lagging power factor penalty reflected in the monthly energy bill raised by NESCO where absorption of VAr during high voltage condition is not accounted for.

Deliberations in the meeting

- SLDC stated that the schedule of power import through Intra / Inter State Open Access transaction by any consumer in 15 minute blocks is being intimated to their respective Discom Utility on the 1st day of the succeeding month. Energy drawal and maximum drawal  from Discom should be computed by deducting the OA import schedule in each block and invoice accordingly.

- Action has already been suggested for control of Duburi 220 kV Bus Voltage.

[Action: NESCO / CGM (O&M)]

E.12: Anticipated power generation and demand for the month of December’2015.

| Sl. No | Discom | Average | Peak |
| --- | --- | --- | --- |
| 1 | CESU | 900 | 1100 |
| 2 | WESCO | 800 | 1050 |
| 3 | NESCO | 620 | 800 |
| 4 | SOUTHCO | 330 | 450 |
| 5 | Total | 2650 | 3400 |
|  | Demand including Loss | 2900 | 3750 |
| Availability |  |  |
|  | Hydro | 230 | 970 |
|  | State Thermal | 750 | 750 |
|  | IPP, small hydro &RE | 750 | 750 |
|  | ISGS share | 920 | 1000 |
|  | CGP support (OA) | 250 | 280 |
| 6 | Total availability | 2900 | 3750 |
| 7 | Surplus / Deficit | 0 | 0 |

Deliberations in the meeting

SLDC stated that the availability shall be revised in view of outage of TTPS unit during the month. However, Central sector power shall be increased due to import through banking.

PART F: OTHER ISSUES

F.1:  Operating procedure for Odisha System.

As per provision in the Regulation 5.1(4) of Odisha  Grid Code, the draft Operating Procedure for Odisha System has been prepared and uploaded in the SLDC site (path: Commerce    information). Members are requested and forward their comments / suggestions to SLDC before 15th December2015. The final Operating Procedure shall be placed in the next meeting.

Deliberations in the meeting

All members were agreed to suggest their views on the draft procedure.

[Action: All Members]

F.2:  Online metering data acquisition.

M/s TCS has been entrusted for the project meant for collection of online metering data from the field. For the said purpose TCS personnel are installing required equipment at the metering points. It is noticed that sometimes the connectivity at the metering terminal & the CT / PT output are being disturbed effecting the energy recording. It is suggested to instruct all the sub-stations for taking up the work in presence of E&MR staffs only.

Deliberations in the meeting

CGM (O&M) stated that all S/Ss were instructed to take up the work in presence of EMR staff.

[Action: CGM (O&M)]

F.3:  Date and Venue of the next (92nd) PSOC meeting.

It was suggested by members that the next meeting may be convened under the ages of OHPC at any of their Power Stations. OHPC may examine the proposal and communicate their consent to Sr. G.M (PS). However SLDC shall write a letter to OHPC in this regard.

[Action: SLDC / OHPC]