Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

# Agenda

for

85th Power System Operational Coordination Meeting

## Date: 29.04.2015

### Venue: PTC, Chandaka

Odisha Power Transmission Corporation Ltd. Bhubaneswar.

Agenda for 85th PSOC Meeting to be held on 29.04.2015 at PTC, Chandaka

A1: Confirmation of the minutes of the 84th PSOC Meeting held on 26.03.2015

The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2014/914(30), dated 08 .04.2015 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART B: GRID PERFORMANCE

B1: Review of Grid Performance for the month of February’15 & March’15.

- Frequency:

Hourly frequency variation for the month of February’15 & March’15.

| Month | % of time frequency remained |
| --- | --- |
|  | <49.00 | 49.00-49.70 | 49.70-49.90 | 49.90-50.05 | >50.05 | 49.70-50.05 |
| Feb’15 | 0.00 | 0.13 | 10.34 | 57.36 | 32.17 | 67.70 |
| Mar’15 | 0.00 | 0.37 | 14.04 | 57.20 | 28.39 | 71.24 |

Maximum & Minimum frequency during the month of February’15 & March’15.

| Month | Freq (Hz) | Date | Time |
| --- | --- | --- | --- |
| Feb’15 | Maximum – 50.35 | 17.02.15 | 05:15 Hrs |
|  | Minimum – 49.68 | 17.02.15 | 20:45 Hrs |
| Mar’15 | Maximum – 50.47 | 01.03.15 | 03:30 Hrs |
|  | Minimum – 49.58 | 03.03.15 | 19:00 Hrs |

- Grid Demand for the month of February’15 & March’15.

| Month | Demand | Maximum Consumption | Maximum Demand | Minimum Demand |
| --- | --- | --- | --- | --- |
|  | MU | MU | Date | MW | Date | Time | MW | Date | Time |
| Feb’15 | 1806 | 68.75 | 26.02.15 | 3613 | 26.02.15 | 20:00 | 1979 | 12.02.15 | 16:00 |
| Mar’15 | 2203 | 79.38 | 25.03.15 | 3981 | 25.03.15 | 21:00 | 2219 | 06.03.15 | 15:00 |
| Mar’14* | 1796 | 66.54 | 25.02.14 | 3468 | 28.02.14 | 20:00 | 1950 | 16.02.14 | 15:00 |

Members may please discuss.

- Voltage Profile of 220 kV Buses in OPTCL system for the month of March’15

| Sl. No | S/s Name | Maximum | Minimum |
| --- | --- | --- | --- |
|  |  | kV | Day | Time | kV | Day | Time |
| 1 | Jayanagar | 246.93 | 1 | 13:45 | 224.29 | 30 | 7:00 |
| 2 | Theruvali | 231.97 | 1 | 15:00 | 205.76 | 31 | 19:15 |
| 3 | Bhanjanagar | 238.32 | 6 | 13:30 | 212.98 | 31 | 19:15 |
| 4 | Chandaka | 232.84 | 7 | 02:30 | 206.63 | 31 | 19:00 |
| 5 | Narendrapur | 232.55 | 6 | 13:30 | 196.81 | 13 | 18:30 |
| 6 | Joda | 241.85 | 7 | 03:45 | 218.45 | 26 | 21:00 |
| 7 | Tarkera | 234.40 | 7 | 03:45 | 223.14 | 28 | 19:15 |
| 8 | Bhadrak | 239.30 | 28 | 16:45 | 203.51 | 27 | 23:00 |
| 9 | Paradeep | 238.38 | 8 | 09:45 | 192.71 | 27 | 20:15 |
| 10 | Budhipadar | 233.88 | 7 | 03:30 | 196.70 | 17 | 11:45 |
| 11 | Duburi | 237.75 | 7 | 02:45 | 206.22 | 27 | 20:45 |
| 12 | Balasore | 236.88 | 4 | 04:45 | 212.40 | 20 | 19:15 |
| 13 | Meramundali | 234.57 | 7 | 01:45 | 196.59 | 13 | 11:45 |
| 14 | Bidanasi | 239.42 | 4 | 16:00 | 211.77 | 31 | 19:15 |
| 15 | Katapalli | 232.83 | 4 | 01:30 | 212.86 | 20 | 20:00 |
| 16 | Nayagarh | 235.15 | 6 | 13:30 | 208.94 | 31 | 19:15 |
| 17 | Mendhasal | 234.86 | 7 | 02:30 | 209.57 | 31 | 19:00 |
| 18 | Bolangir | 236.42 | 4 | 01:45 | 203.97 | 23 | 20:00 |

The maximum voltage of 246.93 kV occurred at Jayanagar Grid Sub-station while Paredeep 220 kV bus has experienced the minimum Voltage of 192.71 kV.

In the last meeting it was deliberated that CVT at Meramundali shall be checked.

CGM (O&M) may update and Members may discuss.

- Energy Generation / Import during the month of March’15

| Source of Power | Energy (MU) |
| --- | --- |
| Thermal (TTPS+IB) | 577.30 |
| OHPC Stations including Machhkund share | 377.39 |
| IPP & CGP Support | 565.47 |
| ISGS drawal | 682.40 |
| TOTAL | 2202.55 |

- Drawal of Machhakund Power

The drawal of  Machhakund power during the month of March’15 was 31.514 MU against AP drawal of 30.503 MU. Total generation was 65.021 MU.

In the last meeting Sr. GM (O&M), Zone-I stated that bus modification work at Jayanagar S/S will be taken up after charging of Auto at Jayanagar. G.M (Telecom) stated that installation of OPGW equipments at Machhakund and Jayanagar by POWERGRID is expected to be completed by June 2015. After which, Remote Subscriber (RS) phone provision can be made from Jayanagar S/S. Southco Utility stated that around 1.5 MW load has been extended to Akusingh Grid by linking 33/11kv Substation Kumbhar Dhamuni. Other linking lines as suitable are being taken up.

After finalizing TTPS metering issue, diversion of metering cubicle from TTPS to Machhakund shall be examined.

Sr. G.M (O&M), Zone-I / GM (Telecom) / Southco Ltd. / Gridco / TTPS may update.

- DISCOM Drawal up to the month of March’15

| Name of DISCOM | Month | Approved Energy Drawal Prorated for the month (MU) | Scheduled Energy (MU) | Actual Energy Drawal ( MU) | Open Access Import Schedule (MU) | Net Energy Drawal ( MU) | Overdraw (MU) |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | 1 | 2 | 3 | 4 | 5=(3-4) | 6=(5-2) |
| CESU | Apr’14 | 743.014 | 761.656 | 765.241 | 2.347 | 762.894 | 1.238 |
|  | May’14 | 767.781 | 762.55 | 789.927 | 2.34 | 787.587 | 25.037 |
|  | June’14 | 743.014 | 723.533 | 756.754 | 2.368 | 754.673 | 31.14 |
|  | July’14 | 767.781 | 697.006 | 714.674 | 2.984 | 711.69 | 14.684 |
|  | Aug’14 | 767.781 | 719.368 | 717.994 | 2.984 | 714.886 | -4.482 |
|  | Sept’14 | 743.014 | 693.26 | 725.186 | 1.1704 | 724.0156 | 30.7556 |
|  | Oct’14 | 767.781 | 702.494 | 707.59 | 3.247 | 704.343 | 1.849 |
|  | Nov’14 | 743.014 | 660.172 | 645.803 | 3.586 | 642.217 | -17.955 |
|  | Dec’14 | 767.781 | 623.206 | 620.432 | 4.589 | 615.843 | -7.363 |
|  | Jan’15 | 767.781 | 550.534 | 611.619 | 3.387 | 606.229 | 55.695 |
|  | Feb’15 | 693.479 | 522.025 | 573.657 | 4.571 | 569.657 | 47.632 |
|  | Mar’15 | 767.781 | 642.627 | 707.78 | 4.207 | 703.573 | 60.946 |
| WESCO | Apr’14 | 560.548 | 597.757 | 631.236 | 17.912 | 613.324 | 15.567 |
|  | May’14 | 579.233 | 636.485 | 649.787 | 21.92 | 627.867 | -8.618 |
|  | June’14 | 560.548 | 582.247 | 630.606 | 9.702 | 620.904 | 38.657 |
|  | July’14 | 579.233 | 546.269 | 605.904 | 27.784 | 583.344 | 37.075 |
|  | Aug’14 | 579.233 | 582.062 | 607.480 | 21.698 | 589.847 | 7.785 |
|  | Sept’14 | 560.548 | 612.084 | 639.319 | 20.574 | 622.605 | 10.521 |
|  | Oct’14 | 579.233 | 616.196 | 648.224 | 26.424 | 625.502 | 9.306 |
|  | Nov’14 | 560.548 | 590.951 | 579.818 | 2.621 | 581.21 | -9.741 |
|  | Dec’14 | 579.233 | 539.112 | 569.586 | 4.289 | 568.865 | 29.753 |
|  | Jan’15 | 579.233 | 514.264 | 546.661 | 4.822 | 547.233 | 32.969 |
|  | Feb’15 | 523.178 | 488.818 | 518.347 | 14.665 | 503.682 | 14.864 |
|  | Mar’15 | 579.233 | 575.837 | 638.138 | 53.603 | 584.535 | 8.698 |
| NESCO | Apr’14 | 438.082 | 425.34 | 466.612 | 23.735 | 441.212 | 15.872 |
|  | May’14 | 452.685 | 414.293 | 475.684 | 19.668 | 456.01 | 41.717 |
|  | June’14 | 438.082 | 391.799 | 458.513 | 33.207 | 425.287 | 33.488 |
|  | July’14 | 452.685 | 398.217 | 476.101 | 31.676 | 444.499 | 46.282 |
|  | Aug’14 | 452.685 | 447.333 | 454.435 | 22.476 | 428.789 | -18.544 |
|  | Sept’14 | 438.082 | 423.846 | 444.946 | 18.474 | 426.472 | 2.626 |
|  | Oct’14 | 452.685 | 418.854 | 445.755 | 20.311 | 425.387 | 6.533 |
|  | Nov’14 | 438.082 | 366.485 | 394.912 | 23.372 | 370.143 | 3.658 |
|  | Dec’14 | 452.685 | 396.403 | 406.233 | 21.769 | 382.459 | -13.944 |
|  | Jan’15 | 452.685 | 394.049 | 415.376 | 19.059 | 396.317 | 2.268 |
|  | Feb’15 | 408.877 | 377.958 | 392.532 | 18.182 | 374.35 | -3.608 |
|  | Mar’15 | 452.685 | 424.814 | 452.864 | 16.082 | 436.782 | 11.968 |
| SOUTHCO | Apr’14 | 274.521 | 286.062 | 275.453 | 0 | 275.008 | -11.054 |
|  | May’14 | 283.671 | 291.135 | 278.337 | 0 | 278.532 | -12.603 |
|  | June’14 | 274.521 | 264.148 | 270.431 | 0 | 269.739 | 5.591 |
|  | July’14 | 283.671 | 252.704 | 266.512 | 0 | 265.791 | 13.087 |
|  | Aug’14 | 283.671 | 267.643 | 278.181 | 0 | 277.861 | 10.218 |
|  | Sept’14 | 274.521 | 264.708 | 272.129 | 0 | 272.043 | 7.335 |
|  | Oct’14 | 283.671 | 260.148 | 260.909 | 0 | 259.509 | -0.639 |
|  | Nov’14 | 274.521 | 262.625 | 262.601 | 0 | 261.393 | -1.232 |
|  | Dec’14 | 283.671 | 254.595 | 257.974 | 0 | 257.783 | 3.188 |
|  | Jan’15 | 283.671 | 251.594 | 257.745 | 0 | 257.745 | 6.151 |
|  | Feb’15 | 256.219 | 228.697 | 239.717 | 0 | 239.717 | 11.02 |
|  | Mar’15 | 283.671 | 281.88 | 283.118 | 0 | 283.118 | 1.238 |

*The above figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali.

Members may please discuss

- Under Frequency Relay operation in OPTCL System during the month of March’15.

Since the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of March’15.

Members may note

PART C – issues raised in 108th OCC meeting of ERPC

C1: PLCC Status installed in Eastern Region

In 106th OCC, Powergrid agreed to restore and maintain the PLCC system at both ends (its own end as well as the constituent end) of a line wherein the other ends are not being maintained by respective constituents for some reasons or others. It was decided that the cost of restoration and maintenance of PLCC system at such (constituent) ends of the line will be borne by the respective constituents. In addition to this the constituents also agreed to extend all possible support to Powergrid in carrying out the above work.

It was decided in the OCC that the list of such PLCC equipments shall be forwarded to PGCIL. POWERGRID have written a letter to CGM (O&M) for execution of an agreement in this regard.

EL Status

In the last meeting, CGM (O&M) stated that commissioning of EL at Bidanasi has been done. Commissioning of EL at 11 Nos. of S/Ss shall be completed by April 2015. It was also decided that OHPC may take action for installation of EL at their Balimela, Rengali and Upper Kolab PHs and synchronization of Indravati EL with GPS.

CGM (O&M) / G.M. (Telecom) / OHPC may please deliberate.

C2: Status of UFRs healthiness installed in Eastern Region.

It was decided in the 105th OCC meeting of ERPC that constituents should check the UFR enunciation & PT fuse and thereby certify on monthly basis that UFRs are in service.

Further, it was decided to monitor the quantum of load connected to the UFR and constituents are to submit, on quarterly basis, maximum and average load quantum of each feeder with UFRs connected. OCC advised all constituents to submit the certificate on regular basis.

CGM (O&M) may please note.

C3: Status of “Third Party Protection Audit”

List of observations in 1st third Party Protection Audit along with updated compliances received from the constituents are available in ERP website

The format for data collection to initiate 2nd Third Party Protection Audit is circulated to the constituents and also made available in ERPC website. All constituents requested to send requisite information by 16th March 2015. On site inspection of 2nd Third Party Protection Audit will commence after receiving the data.

In 107th OCC, members agreed to start 2nd Third Party Protection Audit from the month of May, 2015 with the check lists already designed and modified by ERPC in line with recommendation of the Task Force Committee. It was decided that relevant information as per data format already circulated may be collected during actual visit of Audit team. Finally it was decided in the 108th OCC meeting to conduct 3rd Party Protection Audit from the month of June, 2015.

CGM (O&M) may please note.

C4: Status of 80 MVAr line reactor of 400 kV Meramundali-Angul at Meramundali.

The line reactor of 400 kV Meramundali-Angul at Meramundali was taken out of service without getting clearance from ERLDC, for which OCC expressed its concern. It was decided in the OCC that OPTCL shall investigate and furnish a report to ERPC for taking out the reactor from service without obtaining clearance from ERLDC.

CGM (O&M) / SLDC may please deliberate.

C5: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG) S/s

400/220 kV, 2 X 315 MVA S/S at Bolangir has been established by Powergrid as part of  ISTS system & the following 220 kV interconnecting lines were envisaged to be established by OPTCL:

- LILO of OPTCL’s Katapali-Bolangir line (One ckt) at Bolangir (PG):

- Bolangir (PG)–Bolangir S/C line.

- Bolangir (PG)-Kesinga S/C line.

The status as deliberated in the OCC was

that  GM (Construction) stated that 220 kV Bolangir-Bolangir (PG) line, which is a part of 220 kV Bolangir–Kesinga D/C line with one ckt LILO at Bolangir(PG) may be delayed due to land dispute issue raised by IDCO. The schedule of commissioning of the line is as follows:

- LILO of OPTCL’s Burla-Bolangir line (One ckt) at Bolangir (PG): May 2015

- Bolangir –Bolangir (PG) S/C line , which is a part of proposed Bolangir- Kesinga D/C line with one ckt LILO at Bolangir(PG): Getting delayed due to land dispute.

- Bolangir PG-Kesinga S/C line (Part of Bolangir-Kesinga D/C line): Tender opened but not finalized.

OCC advised to plan other alternatives for Sl. (ii) and (iii) as these were getting delayed due to land dispute.

CGM (Const.) / CGM (O&M) may please update the status.

C6: Future requirement of Special Energy Meters and DCDs

The requirement of frequency based ABT Special type meters up to 2014 has been procured by Powergrid and likely to be exhausted shortly. Beneficiary Constituents of ER are requested for assessment of their requirement of Special Type Energy Meters and DCDs for the period from 2015 to 2017 and intimate the same in the next OCC meeting so that the advance action for procurement can be taken.

SLDC has furnished the list of defective DCDs to ERPC. It was decided in the 108th OCC meeting that the list shall be forwarded to Powergrid for taking necessary action.

SLDC may deliberate.

C7: Certification through BIS as per IS 18001:2007 to all generating / transmission units.

In the last meeting CGM (O&M) stated that BIS has not responded yet. However, BIS will be reminded again.

CGM (O&M) may please deliberate the status.

C8: Pollution mapping for Eastern Region

In 107th OCC meeting, Powergrid informed that the Pollution measurement would start from 1st April, 2015. Constituents were requested to complete the “First set of Pollution Measurement” by 15th April, 2015 and communicate the measurement results to the ERPC, Powergrid and CPRI in the prescribed format (available in the ERPC website).

In the last meeting, Southco Utility stated that out of 26 Nos of locations hanging of insulators for 5 Nos have been completed. The remaining locations shall be completed soon. Other Distribution utilities shall take necessary action for hanging of insulators at their specified locations.

CGM (O&M) / SOUTHCO may please deliberate.

C9: Mock Black start exercises in Eastern Region–ERLDC

The mock black start exercise for OHPC stations for the FY 2015-16 has been scheduled by ERPC.  The test-1 schedule is as detailed.

- Upper Kolab HEP		Last week of May, 2015

- Rengali HEP			2nd week of June, 2015

- U. Indravati HEP		3rd week of June 2015

- Balimela HEP			1st week of November, 2015

Members may discuss-SLDC / OHPC may please note.

C10: Proposal for review of Power Demand Order (PDO) condition for HVDC Gazuwaka poles, in view of repeated tripping in South Odisha.

ERLDC had made a presentation on the existing and proposed PDOs at HVDC Gazuwaka poles and sought views of OPTCL for implementation in the 106th OCC meeting of ERPC. In 29th PCC, OPTCL agreed to the proposal.

In the OCC meeting it was decided that, OPTCL shall study and forward their comments to ERPC / ERLDC.

CGM (O&M) may please deliberate.

C11: Overloading of 400 kV Meramundali-Mendhasal line

The loading of 400 kV Meramundali-Mendhasal line as observed was 504 MW towards Mendhasal, out of which 56 MW power was flowing towards Baripada PG from Mendhasal through Mendhasal-Baripada 400 kV D/C line. Normally power flow is from Baripada to Mendhasal. This reverse power flow might be due to drawal by WB system. Moreover reactive power flow from Baripada was 120 MVAr. The reactive flow could have been reduced by isolating one of the 400 kV ckts. ERLDC may take appropriate action to reduce the reactive flow.

Members may discuss.

C12. Commissioning of new Transmission elements.

- NTPC Barh Unit-V (660 MW) was synchronized at 15:00 Hrs on 01.03.2015 but tripped. Subsequently synchronized at 19:55 Hrs on 04.03.2015 but tripped at 21:20 Hrs of same day.

- 400 kV GMR-Meramundali S/C line was idle charged at 14:40 hrs of 18.03.2015. Subsequently GMR Unit-III was shifted to Meramundali at 21:11 hrs of 18.03.2015.

- 3 X 500 MVA, 765/400 kV ICT-IV at Angul was charged at 16:15 hrs of 24.03.2015. Subsequently 3 X 80 MVAR L/R of 765 kV Angul-Jharsuguda line was charged at Angul at 19:02 hrs of 24.03.2015.

- 765 kV Angul-Jharsuguda ckt-II was finally charged at 15:41hrs of 30.03.2015.

- 765 kV, 330 MVAR B/R –II at Angul was charged at 16:53 hrs of 28.03.2015.

PART-D – Operational Issues

D1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of March’2015 is as tabled.

| Sl. No | Name of Discom | No. of message issued | Over drawal (MU) |
| --- | --- | --- | --- |
| 1 | CESU | 37 | 60.946 |
| 2 | WESCO | 47 | 8.698 |
| 3 | NESCO | 39 | 11.968 |
| 4 | SOUTHCO | 22 | 1.238 |
|  | Total | 145 | 82.850 |

All the Discoms are requested to predict their drawal in a realistic manner to avoid over drawal / under drawal. Frequent revision of drawal schedule may be avoided as for as possible.

Discoms may please deliberate.

D2: Availability of data of real time power flow of feeders covered under Under-frequency Load shedding scheme (UFLS) and lower relief expected to obtained in real time system operation

In the last meeting DGM (Telcom.) stated that the delivery date is 06.04.2015. The firm has requested to accept DD in place of CBG. However the firm is yet to submit offer for inspection.

G.M. (Telecom) / Sr. G.M. (CPC) may please update the status.

D3: Reporting of major incidents.

In the last meeting, GM (O&M) stated that, E&MR wing of respective circles are requested to create awareness between the Shift Engineers for study of the relay indications for proper reporting.

GM (O&M) stated that Electromagnetic Relays at Narendrapur and Bhanjanagar shall be replaced by 15th April’2015.

CGM (O&M) may please deliberate.

D4: Levy of Reactive Energy Charges due to injection of VAR to the grid.

It is noticed that GRIDCO is the only constituent in ER, liable to pay Reactive Energy charges due to injection of reactive power to the pool at the following inter connection point for the period from 23.02.2015 to 01.03.2015.

- 400kV Indravati-Indravati PG

- 400kV Meramundali- Angul PG D/C

- 220kV Rengali – Rengali PG D/C

- 132 kV Baripada PG – Rairangpur

In the last meeting, GM (O&M) stated that, the reactive power flow at both the ends of transmission line need to be compared to ascertain the VAr injection.  OPTCL / SLDC shall compare such VAr flow and confirm whether the line itself is generating VAr and do the needful.

Further, long transmission lines with less loading are responsible for reactive power injection to the grid. It may be examined to keep minimum number of circuits in service to evacuate power from Generating Stations during low generation e.g. Balimela-Jaynagar, Indravati-Theruvali, JSPL-Meramundali.

Members may discuss.

D5: Prolonged outage of transmission elements and tentative revival dates

| Sl.No | Name of transmission element | Reason of outage | Probable date of revival |
| --- | --- | --- | --- |
| 1 | 220 kV Jayanagar-Theruvali ckt-III Breaker | Breaker defunct | May 2015 |
| 2 | 220/132 kV, 100 MVA Auto-II at Duburi | After inspection by repairer, date can be ascertained | Can be ascertained after inspection. |

C.G.M. (O&M) may please update the status.

D6: Communication issues

- Installation of communication equipment by CGPs / Industries.

The status of data communication from CGPs as deliberated in the last meeting is as follows

| Sl. No | Name of CGP | Present status |
| --- | --- | --- |
| 1 | M/s Sri Ganesh Metalicks Ltd. | PLCC / SCADA not established. M/S Sri Ganesh proposed for communication through wireless communication mode. They have been permitted for testing. No progress thereafter. |
| 2 | M/s IFFCO, Paradeep | Work has been awarded to M/s Bharat Kumar Sahoo. Outdoor commissioning work is completed. Testing of DPLC is in progress. |
| 3 | M/s MSP Mettalicks | PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited. |
| 4 | M/s NINL, Duburi | M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. |
| 5 | M/s Adhunik Metallics | PLCC & RTU installed. Database has prepared by OPTCL. Commissioning of RTU is yet to be done. |
| 6 | M/s Rohit Ferrotech | PLCC established and inspection by Telecom Engineers completed. Data base has already been prepared by OPTCL. |
| 7 | M/s VAL, Jharsuguda | No isolator status is available. MW/ MVAR not available for Sterlite 1/2 line, station transformer / Smelter. CBs of Bus coupler data, Bus-1 kV/Hz are not available. As per MOM between OPTCL & Sesa Sterlite, Jharsuguda dtd 22.09.2014, provision for telemetry data will be extended within 6 months.(March,2015) |

In the last meeting, Member Secretary, GCC stated that after receiving the updated information from Telecom, a meeting shall be convened with all such defaulting CGPs by the GCC.

GCC / GM (Telcom.) may please deliberate

- Availability of Tap position of 400kV ICTs at Mendhasal.

It is noticed that tap position of Meramundali ICTS are not available for SCADA display.

In the last meeting, DGM (Telecom) stated that Tap position indicator (TPC 2000) have already installed and integrated with RTU for both the ICTs at Mendhasal. The same will be installed for Meramundali as soon as TPC2000 is available.

CGM (O&M) / G.M. (Telecom) may update.

- Availability of data at SLDC.

The data for the following elements are not available for SCADA display.

- Power flow through 132 kV Paradeep- Jagatsinghpur ckt.

- Power flow through 132 kV Jajpur Road- Anandpur ckt.

- Machhakund generation data

- JSPL (Angul) generation data

In the last meeting, DGM (Telecom) stated that, for item (a) and (b), transducers have been installed and cabling completed. Integration of Transducer with RTU shall be done shortly. For item (c) M/s Chemtrol has been intimated to restore and for item (d) M/s JSPL has been asked to restore its generation data at SLDC soon.

G.M. (Telecom) may please deliberate.

- Integration of new element.

M/s SSL-SEZ became a consumer of WESCO with effect from 20.03.2015 and importing power through intra State open access from its CGP at Jharsuguda as well as from other utility. The drawal of SSL-SEZ needs to be integrated to SCADA to ascertain WESCO drawal and State demand on real time basis. Telecom may explore for integration of SSL-SEZ drawal and display in the VPS of SLDC control room.

In the last meeting, DGM (Telecom) stated that, RTU of M/s SSL-SEZ is reporting to ERLDC. Data at SLDC is being displayed from ERLDC. ERLDC shall be requested to issue of necessary instruction to M/s SSL-SEZ for extending its Smelter data to them, so that the same can be displayed at SLDC. However, the smelter drawal has been made available at SLDC through generalized calculation procedure. It is observed that the smelter drawal is yet to be displayed correctly.

G.M. (Telecom) may please deliberate.

D7: Display of dashboard data.

In the last meeting, DGM (Telecom) stated that, Mr. P.L Gouda, DM (Telecom.) shall act as nodal officer to receive all complaints of Distribution utilities regarding Dashboard problems and rectify thereof. CGM (IT) stated that the newly designed Dashboard is working satisfactorily and the interruption has been reduced considerably. All Distribution Utility were requested to communicate their feedback to CGM (IT) for further modification of the Dashboard display.

DISCOM / CGM (IT) / G.M. (Telecom) may please deliberate.

D8:  Communication to Balimela HEP.

Very often it is noticed that the land line / PLCC telephone of Balimela HEP is remaining out of service. Due to failure of communication the Black Start exercise could not be conducted. Also important instructions could not be communicated. It is suggested to strengthen the communication system by providing additional Mobile phone to Balimela HEP as well as to other HEPs also.

OHPC may please deliberate

D9:  Non compliance of OGC provision by UI HEP.

Unit 1 of UI HEP was under shutdown for Annual Maintenance. On 17.04.2015 UIHEP requested SLDC to allow shutdown of Unit-2 for Annual Maintenance for the period from 24.04 to 19.05.2015. Since one unit was already under shutdown, SLDC did not issue shutdown of permission for Unit-2. UI HEP was taken shutdown of their Unit-2 on sou-motu, without waiting the consent of SLDC, which is a violation of OGC provision.

OHPC may deliberate.

D10: DISCOM Issues

SOUTHCO:

ABT issue

- The data in the new format for ABT Dash Board is not functioning properly except only the current Drawl.

- Feedback on the Data display system has been submitted.

- BSNL has been requested for providing the leased line with necessary application and is under process.

- Request for taking remedial measures for providing all 57 nos interception point data to Southco with Auto transformer Data as well as Energy reading at 00.00hrs of all points each day.

- Low voltage problem in Gunupur, Akhusingi &Parlakhemundi area during BTH power in peak hours.

- After charging of Dabugaon  Grid S/s South is drawing power. At present one No. of 12.5 MVA has been commissioned at Dabugaon, which is inadequate to meet the load requirement of the area. 2nd 12.5 MVA Tfr may be installed.

NESCO

- Display of Dashboard Data of NESCO as per the proposed format submitted in the 79th PSOC meeting.

- Long time server error problem to be sorted out, which had been occurred from 22.04.15.

PART E: OPERATIONAL PLANNING

E1:  Commissioning status of New Transmission elements.

As deliberated in lat meeting the status of commissioning of new transmission elements is as follows:

| Sl. No | Details of transmission element | Present Status |
| --- | --- | --- |
| 1 | Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line | Work has already been started. Expected to be completed by June 2015. |
| 2 | Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt | Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal for which work order / PO issued. (October-2015) |
| 3 | Commissioning of 400 kV Ib-Meramundali D/C line. | 400kV SSEL-Meramundali line has been idle charged from SSEL end. Due to theft of conductor line could not be charged. Expected to be charged by end of June’2015. |
| 4 | Commissioning of 400 kV Duburi-Meramundali D/C line. | Work is in progress after disposal of Case. Expected by the end of May 2015. |
| 5 | Commissioning of 220 kV Bidanasi-Cuttack line | Work in progress and expected to be completed by June 2015. |
| 6 | Commissioning of 220/132 kV Cuttack S/S | Work in progress and expected to be completed by June 2015. |
| 7 | Commissioning of 132 kV Baripada (PG)-Jaleswar line | Work has already been started, which will be completed by December 2015. |
| 8 | Commissioning of 220/132 kV Kesinga S/S | Work under progress. Expected by September 2015. |
| 9 | Connectivity to Keonjhar PG | Proposal is mooted to be placed in the BoD meeting for connecting the proposed 220 / 33 kV Keonjhar S/S and with Turumunga S/S through 2 Nos. 220 kV ckts each. |
| 10 | LILO of 220 kV Burla - Bolangir line (one ckt) at Bolangir(PG) | Work awarded. Expected to be completed by June, 2015 |
| 11 | 220 kV Bolangir –Kesinga D/C line and LILO of one ckt at Bolangir(PG). | 220kV Bolangir - Kesinga D/C line is under construction. It is proposed to connect Bolangir (PG) through LILO arrangement of one ckt. (may be delayed due to land dispute with IDCO) |

[Action: CGM (Construction)]

Status of Discom’s action plan for power drawal from the S/Ss expected to be commissioned in near future.

| Sl. No | Name of the sub-station | Probable month of commissioning | Name of DISCOM | Action taken by Discoms |
| --- | --- | --- | --- | --- |
| 1 | 132/33kV, 2x20 MVA Banki | Charged | CESU | 33 kV feeder shall be charged by April’15 |
| 2 | 132/33kV, 2x20 MVA Konark | Apr’15 | CESU | Line existing |
| 3 | 132/33kV, 2x20 MVA Samuka beach | Charged | CESU | Completed by end of Apr’15 |
| 4 | 132/33kV, 2x20 MVA Khajuriakota | June’15 | CESU | 33 kV feeder work shall be completed by June’15 |
| 5 | 132/33kV, 2x40 MVA Sarasmal | Charged | WESCO Utility |  |
| 6 | 132/33kV, 2x40 MVA Kalunga | Apr’15 | WESCO Utility |  |
| 7 | 220/33kV, 2x20 MVA Banei | Dec’15 | WESCO Utility |  |
| 8 | 132/33kV, 2x12.5 MVA Dabugaon | Charged | SOUTHCO Utility | 33 kV Dabugaon and Papadahandi feeder completed |
| 9 | 132/33kV, 2x12.5 MVA Umerkote | Charged | SOUTHCO Utility | 33 kV feeder shall be completed by May’15 |
| 10 | 132/33kV, 2x20 MVA Nawapara | Charged | WESCO Utility | 33 kV feeder work completed. |
| 11 | 132/33kV, 2x20 MVA Padmapur | June’15 | WESCO Utility |  |
| 12 | 132/33kV, 2x20 MVA Udala | Dec-15 | NESCO Utility | Line existing |
| 13 | 132/33kV, 2x20 MVA Somanathpur | May’15 | NESCO Utility | 33 kV feeder existing |

As decided in the last meeting, CESU stated that action is being taken for construction of 33/0.4 kV S/S at Mendhasal to avail power supply for Mendhasal area.

It is noticed that commissioning of new transmission elements is not being intimated to SLDC by respective field units, which required for operation as well as reporting purpose.

All DISCOMS may update the status / CGM(O&M) & CGM(Const.) may please deliberate

E2: Installation of Energy Metering at Hydro / Traction & Solar projects.

ABT compliance meters have been installed in all OHPC stations except UIHEP. As per report received four sets of meters have been installed at 220kV UIHEP_Theruvali circuits. Installation of meters at ICT-I & II is yet to be done.

Billing from those energy meters is yet to be done by Gridco.

WESCO Utility shall approach Rly. Authority for installation of required Class of CT & PT at their Bhalulata, Bamara and Chandiposi Traction points.

CGM (O&M)may update the status / OHPC / WESCO may please deliberate.

E3: TTPS ISSUE.

Implementation of Feeder Metering

Installation of feeder meters at TTPS outgoing feeders is yet to be completed.

GRIDCO / TTPS may please update.

E4: Shifting of 33 kV line from Balasore Grid S/S yard to facilitate separation of Tfr and Balasore Alloy bays.

In the last meeting, CGM (O&M) stated that NESCO has to expedite the work, as it is very much delayed.

NESCO may please deliberate.

E6: Major Events in the month of March’15

132/33kV, 2 X 40 MVA  Sarsamal sub-station & 132/33kV, 2 X 20 MVA  Samuka sub-station commissioned during March’ 2015.

E7: Important Grid Incidences during the month of March’15.

Important incidents occurred during the month of March’15 are as detailed.

- On 12.03.2015 at 17:19   hrs, 400 kV Angul Ckt-II , 400 kV IbTPS  Ckt-II, Mendhasal Ckt, ICT-I, JSPL-I  (main breaker only) tripped at Meramundali S/S. 400 kV Bus-I at Meramundali S/S became dead.

- On 24.03.2015 at 13:09   hrs, GMR, JSPL Ckt-I&II tripped at Meramundali S/S

C.G.M. (O&M) may please deliberate.

E8: Outage of major transmission Elements during the month of March’15. (above 10 hrs).

Outage of major transmission elements above 10 hours during the month of March’15 is as detailed.

| Sl No | Transmission lines | Tripping Dt /time | Restoration Dt/time | Reason |
| --- | --- | --- | --- | --- |
| 1 | 132 kV Aska-Berahmpur Ckt | 03.03.15 14:14 | 04.03.15 10:45 | ‘Y’ ph insulator damaged at Loc. No-65 |
| 2 | 400/220 kV , 315 MVA ICT-I at Mendhasal | 03.03.15 22:58 | 04.03.15 12:32 | ‘Y’ ph LA burst at Baripada S/S. |
| 3 | 220 kV Mendhasal-Bhanjanagar Ckt | 11.03.15 10:47 | 12.03.15 15:23 | ‘Y’ ph conductor damaged between Loc. No-331 and 332 |
| 4 | 220 kV Meramundali-Kaniha Ckt-I | 21.03.15 13:43 | 24.03.15 20:33 | Breaker problem at Meramundali end. |
| 5 | 132 kV Kendrapara-Paradeep Ckt-II | 21.03.15 17:42 | 24.03.15 11:21 | ‘R’ ph jumper snapped at Loc. No-218 |
| 6 | 132 kV Budhipadar-MCL Ckt-I | 28.03.15 15:00 | 29.03.15 14:35 | ‘Y’ ph insulator damaged at Loc. No-20 |
| 7 | 220 kV Budhipadar-IbTPS Ckt-IV | 30.03.15 16:30 | 31.03.15 13:19 | ‘R’ ph conductor snapped at Loc. No-13 |

C.G.M. (O&M) may please deliberate.

E9: Review of Outage Program of State Generators / Transmission elements for the month of May’2015:

Tentative Outage programme for State Generators for the month of May’2015 are as follows:

| Sl. | Station | Unit | Period | Remarks |
| --- | --- | --- | --- | --- |
| 1 | Burla | # 1 # 6 # 7 | 18.04.15 to 31.07.15 17.02.14 to continue 28.02.15 to 30.04.15 | Capital Maintenance Programming for R, M & U Annual Maintenance |
| 2 | Chiplima | # 1 #3 | 15.05.15 to 31.05.15 15.02.14 to continue | Annual Maintenance Programming for R & M |
| 3 | Balimela | # 1 #4 #8 | 31.01.13 to continue 15.04.15 to 10.05.15 15.05.15 to 10.06.15 | Programming for R & M Annual Maintenance Annual Maintenance |
| 4 | Rengali | # 1 # 2 | 11.05.15 to 31.05.15 11.05.15 to 31.05.15 | Governor Rectification Governor Rectification |
| 5 | Upper Kolab | # 1 | 05.05.15 to 28.08.15 | Capital Maintenance |
| 6 | Upper Indravati | # 1 # 2 | 27. 03.15 to 22.04.15 24.04.15 to 18.05.15 | Annual Maintenance Annual Maintenance |

OHPC may deliberate.

E10: Generation Program for the month of March’15.

Generation schedule for the month of March’15 furnished by OHPC are given below.

| Name of Hydro Gen. Station | Generation Programme (MW) | Reservoir Level as on 01.04.14 | Reservoir Level as on 01.04.15 | MDDL | High Flood Reservoir Level |
| --- | --- | --- | --- | --- | --- |
|  | May’15 (1st fortnight) | May’15 (2nd fortnight) |  |  |  |  |
| HPS, Burla | 60+40 | 30+20 | 619.04ft | 614.02ft | 590 ft. | 630 ft. |
| Balimela | 80 | 170 | 1497.90ft | 1493.30ft | 1440 ft. | 1516 ft. |
| Rengali | 100 | 100 | 121.10mt 1.78mt mtr mt | 120.05mt mt | 109.72mtr | 123.5 mtr. |
| U.Kolab | 80 | 80 | 853.16mt mt | 853.76mt | 844 mtr | 858 mtr. |
| U.Indravati | 300 | 300 | 637.55mt mt | 636.18mt mt | 625mtr | 642 mtr |
| MKD (O/D) | 30 | 30 | 2736.35ft | 2730.50ft ft | 2685 ft. | 2750 ft. |
| TOTAL | 690 | 730 |  |  |  |  |

OHPC may update.

PART F: OTHER ISSUES

F1:  Suspension of ABT for the block period from 42 to 49 on dated 27.03.2015

On dated 27.03.2015 SLDC instructed TTPS for backing down of generation to limit he Auto-2 Power flow, to allow shutdown of 132 kV TTPS-Duburi D/C line. Auto-1 was under shutdown. During the process of shutdown all Stage-I Units of TTPS got tripped.

However, TTPS on dated 31st March 2015 has requested for suspension of ABT for the block period from 42 to 49 of 27.03.2015 considering the case as a transmission constraint. Again on 20.04.2015 TTPS in its mail indicated that the Deviation Charges has been suspended for the block period from 41 to 49 of 27.03.2015.

TTPS may please deliberate / Members may discuss

F2:  Date and Venue of the next (86th) PSOC meeting: