[image: image1.png]PTC



                                                                                                                  
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image11.png]VOLTAGE PROFILE OF NARENDRAPUR 220 kV BUS

FORMAY 2018

f;

y
7
2’/
4
N‘

E =





Agenda

for

122nd Power System Operational Coordination Meeting

Date: 25.06.2018
Venue: PTC, Chandaka, Bhubaneswar 
[image: image10.png]VOLTAGE PROFILE OF MERAMUNDALI 400 kV BUS

FORMAY 2018

v
S
&
=

[ STHLT

425

420

415

t i
o 0
= =}
< <

M| u] @8e3 oA

8
<

395

Time In Hrs





Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 122nd PSOC Meeting to be held on 25.06.2018 at PTC, Chandaka, Bhubaneswar
Item no. 1: Confirmation of the minutes of the 121st PSOC Meeting held on 26.05.2018
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2017/1457 (47) dated 19.06.2018 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   : Grid Performance for the month of May’2018
C.1: Status of projects funded under PSDF scheme

C.2: Automatic Under Frequency Load Shedding
C.3: Data for GEOSPATIAL energy portal of Neeti Aayog-CEA 

C.4: 220kV Interconnecting line of OPTCL with 400/ 220kV Bolangir PG, Keonjhar & Pandiabil s/s

C.5: Auxiliary power consumption by Powergrid Substations-GRIDCO 
C.6: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

C.7: Certification through BIS as per IS 18001:2007 to all generating/ transmission units 
C.8: Implementation of Automatic Demand Management Scheme
C.9: Mock Black start exercise in Eastern Region 
C.10: Implementation of Islanding Scheme.
D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Prolonged outage of transmission elements and tentative revival dates

D.3: Communication issues. 
D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.5: Web based drawal / generation scheduling 
D.6: DISCOM Issues
E.1: Commissioning status of New Transmission elements. 

E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
E.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.

E.4: Major Events in the month of May’18
E.5: Important grid incidences during the month of May’18.

E.6: Outage of major transmission Elements during the month May’18. (above 10 hrs).
E.7: Review of Outage Program of State Generators for the month of July’2018
E.8: Generation Program for the month of July’2018.
E.9: Anticipated power generation and demand for the month of July’2018.

F.1:  Date and Venue of the next (123rd) PSOC meeting
PART B: GRID PERFORMANCE
Review of Grid Performance for the month of May’18.

A. Frequency:

Hourly frequency variation for the month of May’18.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	Mar’18
	0.00
	0.00
	9.39
	78.69
	11.92
	49.98

	Apr’18
	0.00
	0.02
	10.35
	78.33
	11.30
	49.98

	May’18
	0.00
	0.14
	18.41
	69.25
	12.17
	49.91


Maximum & Minimum frequency during the month of May’18.
	Month
	Freq (Hz)
	Date
	Time

	April’18
	Maximum –50.22
	30.04.18
	07:04 Hrs

	
	Minimum – 49.63
	23.04.18
	10:45 Hrs

	May’18
	Maximum –50.13
	03.05.18
	04:00 Hrs

	
	Minimum – 49.69
	05.05.18
	22:45 Hrs


In the 121st PSOC meeting SLDC stated that the frequency profile indicated by SLDC is not matching with that of ERLDC frequency profile. Telecom was requested to investigate the same.

Telecom may please discuss.
B. Grid Demand for the month of May’18
	 Month
	Max. Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	Apr’18
	92.65
	23.04.18
	2400
	3334
	4430
	22.04.18
	21:00
	2348
	01.04.18
	24:00

	May’18
	98.61
	24.05.18
	2735
	3798
	4692
	07.05.18
	21.00
	2113
	14.05.18
	12.00

	May’17
	88.13
	23.05.17
	2534
	3406
	4281
	04.05.17
	24:00
	2553
	06.05.17
	23:00


C. Voltage Profile of 220 kV Buses in OPTCL system for the month of: May’18

	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Atri
	232.67
	3
	1:15
	208.13
	31
	20:30

	2
	Balasore
	233.94
	1
	5:45
	212.63
	30
	20:30

	3
	Barkote
	230.59
	3
	6:00
	221.87
	21
	19:30

	4
	Bhadrak
	236.88
	13
	22:00
	212.46
	30
	20:30

	5
	Bhanjanagar
	235.03
	3
	1:15
	214.88
	31
	20:30

	6
	Bidanasi
	232.09
	23
	9:00
	212.81
	9
	15:30

	7
	Bolangir
	231.34
	3
	5:30
	207.72
	12
	16:30

	8
	Budhipadar
	230.01
	3
	7:30
	201.09
	29
	00:30

	9
	Chandaka
	232.26
	3
	1:15
	207.26
	31
	22:00

	10
	Cuttack
	230.53
	23
	10:00
	206.05
	31
	22:00

	11
	Duburi(O)
	235.03
	3
	4:30
	220.54
	30
	19:30

	12
	Duburi (N)
	231.11
	3
	4:30
	216.62
	30
	20:30

	13
	Jayanagar
	239.88
	15
	4:45
	223.89
	5
	21:00

	14
	Joda
	231.51
	18
	10:15
	214.08
	29
	15:30

	15
	Katapalli
	231.51
	1
	1:00
	215.11
	12
	16:30

	16
	Lapanga
	232.72
	1
	1:45
	221.41
	12
	16:30

	17
	Laxmipur
	239.71
	15
	4:45
	222.97
	25
	16:45

	18
	Mendhasal
	234.11
	3
	1:15
	209.34
	31
	20:30

	19
	Meramundali
	227.53
	3
	5:30
	219.33
	12
	22:45

	20
	Narendrapur
	237.00
	3
	1:15
	207.20
	31
	20:15

	21
	Nayagarh
	233.70
	3
	1:15
	209.51
	31
	20:45

	22
	Paradeep
	232.78
	14
	13:15
	206.45
	30
	22:15

	23
	Tarkera
	245.14
	29
	11:30
	220.08
	30
	21:00

	24
	Theruvali
	235.78
	3
	5:30
	213.44
	28
	23:00

	25
	Samangara
	233.01
	3
	1:15
	207.20
	31
	20:30


The maximum Voltage of 239.88 kV occurred at Jayanagar 220 kV bus, while Budhipadar 220 kV bus has experienced the minimum Voltage of 201.09 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Mendhasal, Meramundali  and New Duburi bus during the month of May 2018 are indicated. 

[image: image2]
[image: image3.png]VOLTAGE PROFILE OF JAYANAGAR 220 kV BUS

FORMAY 2018

Fsmer
Foeee
Fspre
FooTz
Estioz
Foe6T
Fspsr
F 08T
Fstur
Foeor
EstisT
£ o0isT
ESTT
Foeier
Fspier
Footer
Fsurr
£ ogi0T
£ sti60
£ 0060
Fs1i80
F oo
Fspi90
£ 00:90
£sTis0
£ 0€%0
£ stie0
£ 00:€0
Fstieo
FoeTo
F svi00
f 00:00

Time In Hrs





[image: image4.emf]360

365

370

375

380

385

390

395

400

405

410

415

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MENDHASAL 400 kV BUS

FOR MAY' 2018



[image: image5]
[image: image6.png]VOLTAGE PROFILE OF NEW DUBURI 400 kV BUS

FORMAY'2018





Members may discuss.
D. Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of May-2018 [image: image7.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  MAY'2018

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

2x160 46.36 25 14:45 6.68 14 12:30

58.28 24 12:45 6.60 14 12:30

76.52 30 21:00 21.08 16 18:45

76.48 30 21:00 21.08 16 18:45

77.40 30 21:00 21.44 16 18:45

1x100 56.36 29 13:30 6.44 18 23:45

1x160 99.16 29 13:30 6.96 19 00:15

YET TO BE COMMISSIONED

1x160 96.12 24 07:45 13.84 3 00:15

1x160 103.16 26 07:15 12.00 3 00:15

1x160 43.04 18 20:45 9.72 6 07:30

1x100 30.44 12 23:00 6.64 6 07:30

1x100 30.44 12 23:00 6.64 6 07:30

2x160 121.32 27 20:00 18.36 2 07:00

127.52 27 20:00 19.56 2 07:00

91.88 26 09:15 10.32 30 22:45

83.68 12 18:45 10.56 30 22:45

1x100 66.92 30 15:00 6.16 14 12:15

1x160 115.40 30 15:00 10.72 14 12:30

1x100 80.04 23 07:45 6.40 14 12:30

1x160 110.76 30 15:15 10.00 14 12:30

CUTTACK 1x160

91.04

29 13:15 5.96 17 04:00

Under shut down

69.20 10 15:30 6.48 14 12:15

65.80 10 15:30 6.20 14 12:15

1x160 75.48 5 21:00 6.04 20 15:00

1x160 76.20 27 20:30 6.08 20 15:00

56.44 7 20:15 16.96 2 18:15

56.76 7 21:15 16.96 2 18:30

56.80 7 21:15 17.24 2 18:30

1x100 34.88 15 16:15 5.72 11 11:30

1x100 35.00 15 16:15 6.04 12 17:30

1x160 52.52 15 16:15 9.08 12 17:30

1x160 57.44 1 00:30 11.08 31 01:45

58.60 3 18:45 11.04 31 01:45

58.36 9 20:15 6.08 18 23:45

70.68 13 19:15 6.00 18 23:45

Under shut down

2x100 25.80 28 05:45 3.00 13 02:00

35.40 29 07:15 2.40 13 02:00

2x160 107.72 21 20:30 18.04 1 19:00

107.36 21 20:30 18.68 1 04:30

1x100 61.80 21 20:30 10.00 1 19:00

1x160 114.76 30 21:45 6.28 17 09:15

1x100 77.12 29 14:00 4.20 14 17:30

1x50

4x100  77.96 18 15:15 7.68 14 00:30

68.08 7 21:30 8.36 14 00:30

77.88 18 15:15 7.68 14 00:30

77.44 18 15:15 8.28 14 00:30

2x100 83.68 22 19:45 4.96 3 05:15

78.84 22 19:45 5.40 3 05:45

1x160 

1x160

1x100 61.88 31 22:00 9.88 1 04:45

62.00 31 22:00 10.08 1 04:45

KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & 

Katapali area load.}



DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, 

Jajpur Road, Kalarangi, Jajpur Town}

Mendhasal { Part area load of Khurda S/S}

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }

JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]



"*" - Alternate P/S from 

Kuchei.



BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), 

MCL, Sundergarh,Brajarajnagar, 

Rajgangpur}

2x160 

BHADRAK 220/132 KV

{Bhadrak area load, Bhadrak(T),Soro,  

FACOR (I), Dhamra Port}

LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 

BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

SAMANGARA                                          

{ Puri, Nimapara & Konark}

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, 

Digapahandi, Mohana.}

THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

Rayagada & Paralakhemundi 

can be fed from Machhkund 

system.

ATRI                                                     

{Banki, Khurda, Chandpur & Argul}

Supported by Burla & 

Chipilima power.

PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

BIDANASI 220/132 KV

{Bidanasi, Khurda }

3x100 

3x100 

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}

3x160 



BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

Drawal details

Maximum Minimum


E. DISCOM Drawal for the month of May’18
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	Apr’18
	745.479
	734.495
	770.403
	19.655
	750.748
	16.253

	
	May’18
	770.329
	819.870
	850.674
	19.558
	831.116
	11.246

	WESCO
	Apr’18
	585.205
	636.576
	689.137
	57.318
	631.819
	-4.757

	
	May’18
	604.712
	636.024
	1042.198
	361.670
	680.528
	44.504

	NESCO
	Apr’18
	504.658
	418.945
	528.936
	105.079
	423.857
	4.912

	
	May’18
	521.479
	521.479
	576.819
	102.344
	474.475
	-47.004

	SOUTHCO
	Apr’18
	300.822
	298.760
	298.778
	0
	298.778
	0.018

	
	May’18
	310.849
	310.849
	323.114
	0
	323.114
	12.265


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
     Members may please discuss.

F. Energy Generation / Import up to the month of May’18
Figures in MU  
	Month
	Thermal

(TTPS+IbTPS)
	OHPC 
& MKD
	CGP Support
	IPP Inj.
	RE
	ISGS
	Total

	April’18
	535.10
	421.70
	362.53
	198.95
	9.69
	872.26
	2400.24

	May’18
	567.940
	573.520
	313.169
	199.23
	14.39
	1066.64
	2734.893

	Total
	1103.040
	995.220
	675.699
	398.184
	24.080
	1938.900
	5135.133


G.  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of May’18 are as detailed:
	Month
	Total Generation
	Odisha Drawl
	AP Drawl

	
	MU
	Avg (MW)
	MU
	Avg (MW)
	MU
	Avg (MW)

	Apr’18
	37.162
	51.61
	18.613
	25.851
	16.943
	25.532

	May’18
	48.888
	65.70
	22.424
	30.140
	24.492
	32.919

	Total
	86.050
	
	41.037
	
	41.435
	


In the 118th PSOC meeting, O&M stated that Machhakund drawal shall be increased after drawal of power from Podagada S/S by SOUTHCO. 
In the 119th PSOC meeting Sr. G.M SLDC stated that there is no matching load available, in case more Nos of Machhakund units synchronized. Southco may explore their takeoff arrangement from newly commissioned Podagada 132/33 kV S/S to increase Machhakund drawal of the State. 

In the 120th PSOC meeting Southco has assured to complete the work by 1st week of May’2018. 

SOUTHCO may deliberate.
H. Under Frequency Relay operation in OPTCL System during the month of May’18.

 Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of May’18.
I. Status of Open Access applications up to the month of May’2018
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’18
	26
	79
	0
	31
	136
	26
	76
	0
	31
	133
	3

	2
	May’18
	59
	90
	0
	26
	175
	59
	89
	0
	26
	174
	1

	
	Total
	85
	169
	0
	57
	311
	85
	165
	0
	57
	307
	4


PART C – Issues discussed in the 146th  OCC meeting of ERPC held on 15.06.2018
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
145th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	30.11.18
	162.5 Cr.


	37.79Cr.
	Total contract awarded for

Rs. 51.349 Cr



	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.225 Cr
	
	Tender floated

	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov

2018,

Chiplima

Dec 2018
	22.35 Cr.
	
	Tendering under process

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 


	28-08-17
	
	31.94 Cr
	
	Appraisal committee recommends for project cost of 30.23 Cr and 27.23 Cr for grant to monitoring

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost
	
	Compliance to TSEG observation submitted.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	20.02.2018  Date of submission 
	
	41.1 Cr
Estt cost
	
	Compliance to TSEG observation submitted.


In the 121st PSOC meeting O&M stated that for Implementation of ADMS by SLDC and Protection up-gradation & installation of SAS for 7 Nos. of S/Ss projects, PSDF raised some queries, which have been submitted.  

CGM (Telecom) stated that for implementation of OPGW based reliable communication at 132 kV and above S/Ss, tender has been floated. CGM (O&M) stated that for installation of Bus reactor, PSDF Appraisal committee have recommended for project funding. Compliance to TSEG observation has been submitted for implementation of ADMS by SLDC and protection up-gradation and installation of SAS for 7 Nos. of S/Ss.

CGM (O&M) / SLDC may please update the status.
C.2: Automatic Under Frequency Load Shedding

NPC vide letter dated 30 May 2018, informed that considering the grid size and assuming Power Number of 7000, the following two options of AUFLS are proposed.

Option-1

AUFLS scheme with 4 stages of frequency viz 49.2, 49.0, 48.8 & 48.6 Hz

	AUFLS
	Frequency (Hz)
	Load relief in MW

	
	
	NR
	WR
	SR
	ER
	NER
	Total

	Stage-I
	49.2
	3920
	3360
	3170
	1380
	170
	12000

	Stage-II
	49.0
	3950
	3380
	3190
	1380
	170
	12070

	Stage-III
	48.8
	3970
	3400
	3210
	1390
	170
	12140

	Stage-IV
	48.6
	4000
	3430
	3230
	1400
	170
	12230

	
	Total (MW)
	15840
	13570
	12800
	5550
	680
	48440


 Option-2

AUFLS scheme with 4 stages of frequency viz 49.4, 49.2, 49.0 & 48.8 Hz

	AUFLS
	Frequency (Hz)
	Load relief in MW

	
	
	NR
	WR
	SR
	ER
	NER
	Total

	Stage-I
	49.4
	3900
	3340
	3150
	1370
	170
	11930

	Stage-II
	49.2
	3920
	3360
	3170
	1380
	170
	12000

	Stage-III
	49.0
	3950
	3380
	3190
	1380
	170
	12070

	Stage-IV
	48.8
	3970
	3400
	3210
	1390
	170
	12140

	
	Total (MW)
	15740
	13480
	12720
	5520
	680
	48140


Constituents may forward their views within 10 days regarding frequency and quantum of load shedding
[Action: SLDC / O&M)]
C.3:    Data for GEOSPATIAL energy portal of Neeti Aayog-CEA
NITI Aayog is developing a user friendly GIS based Energy Map of India, which would provide true locations of all energy resources in India including power plants, coal and oil reserves, transmission lines etc. 
CEA sought the information of name, Voltage level, capacity, longitude and latitude of 33 kV and 66 kV S/Ss and lines.

The information may be shared with CEA vide email: cedpd-cea@gov.in.

All Discoms are requested to submit the above data to CEA with a copy to SLDC for forwarding to ERPC.                                                                                         [Action: All DISCOMS]

C.4: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 121th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by June’18. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by June’18. 

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Keonjhar S/S (220/33 kV) by June’18.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	December 2018 


C.5:Auxiliary power consumption by Powergrid Substations-GRIDCO 

GRIDCO vide letter dated 14th May 2018 informed that, GRIDCO had convened a meeting with Powergrid with a suggestion to become the consumer of state DISCOM and make the payment towards auxiliary power consumption as per the applicable tariff. Further, GRIDCO prevailed upon Powegrid that the amount to be paid to DISCOM should not be claimed in transmission tariff as the same has already been factored in the tariff as per the Regulation 29(4) of 2014 Tariff Regulations.  

In this regard, Powergrid is not signing the minutes for commercial settlement.  It was decided in the OCC that the issue may be raised in the Commercial sub-Committee meeting of ERPC

In the 121st PSOC meeting it was suggested that Gridco shall write a letter to Powergrid to become consumer of DISCOM. The matter may be raised in the Commercial Sub-Committee meeting of ERPC.

CGM (PP) may please update the status.
C.6: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber-attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber-attacks vide letter dated 2nd August, 2013.

In the 107th PSOC meeting, CGM (IT) informed that “Crisis management plan” work is awarded to M/s Digital Age Strategies Pvt. Ltd. The said firm has completed the study of Servers and Firewalls at SLDC, Bhubaneswar and back-up SLDC at Meramundali. Presently the data centers of SLDC and GRIDCO are being audited for IT security vulnerability assessment.

In the 121st PSC meeting CGM (IT) stated that the certificate has been received. Audit for FY-2018-19 will be started from June’2018.
CGM (IT) may please update the status.
C.7: Certification through BIS as per IS 18001:2007 to all generating / transmission units.
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In the 111th PSOC meeting CGM (O&M) stated that 22 No’s of officers are nominated from Chandaka, Mendhasal, Atri, Kesura, Bidanasi & Cuttack S/Ss to undergo training. Awareness training shall be started from 1st week of August’17. After receiving the price offer, order will be placed. 

In the 113th PSOC meeting CGM (O&M) stated that certification for 6 Nos of S/Ss will be done by December’2017.
In the 116th PSOC meeting, CGM (O&M) stated that draft modality has been prepared. Order for Mendhasal S/S will be issued as a pilot project.

In the 117th PSOC meeting CGM (O&M) stated that draft project report for Mendhasal S/S has been submitted to BIS. The report will be approved in the meeting to be conducted by them.

In the 118th PSOC meeting, O&M stated that the report has already been submitted. Approval is yet to be received.
In the 121st PSOC meeting CGM (O&M) stated that Audit team is expected soon.

CGM (O&M) may please deliberate the status

C.8: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************

The latest status along with proposed logic as follows:
[image: image8.emf]
[image: image9.emf]
In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 117th PSOC meeting it was decided that SLDC shall process for tendering.

In the 118th PSOC meeting, SLDC stated that the tender specification is expected to be received from CPC by 1st week of March’2018. After receiving the same SLDC will process for tendering
In the 121st PSOC meeting SLDC stated that M/S GE has given a presentation on ADMS during at SLDC. Tendering will be done by end of June18.
SLDC may please deliberate the status.
C.9: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2018-19 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2018
	Done on 08.06.2018
	Last week of January 2019
	

	3
	Rengali
	2nd week of June 2018
	June’18
	Last week of November 2018
	

	4
	U. Indravati
	3rd week of June 2018
	
	2nd week of February 2019
	

	6
	Balimela
	3rd week of October  2018
	
	1st week of March 2019
	

	9
	Burla
	Last week of June 2018
	Done on 07.06.2018
	Last week of February 2019
	


In the 120th PSOC meeting SLDC stated that ERPC has proposed to conduct a workshop at U. Kolab / Balimela, probably during the month of July’18. Mock Black start exercise for Upper Indravati will be done at that time. 
OHPC / SLDC may please deliberate.
C.10: Implementation of Islanding scheme:

Efforts should be made to design islanding scheme based on frequency sensing relays so that in case of imminent grid failure, electrical islands can be formed. These electrical islands can not only help in maintaining supply to essential services but would also help in faster restoration of grid.
No islanding scheme is available in Odisha, Bihar and Sikkim.

OPTCL has submitted the detail plan of  IbTPS islanding scheme

OCC advised OPTCL to give a presentation on CPP islanding scheme existing in Odisha with the details of extending power capacity to Odisha during emergencies.

OPTCL / SLDC have convened a meeting with major CGPs of the State. The views of CGPs for extending power during blackout is awaited. 
In the 68th PCC meeting held at ERPC, Kolkata, members suggested for review of IbTPS islanding scheme considering present load scenario which will be discussed in the 69th PCC meeting.


CGM(O&M) / SLDC may deliberate the status.
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of May’18:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	11.246
	1.3717

	2
	WESCO
	0
	44.504
	6.9972

	3
	NESCO
	0
	-47.004
	-9.0136

	4
	SOUTHCO
	0
	12.265
	3.9456

	
	Total
	0
	21.011
	


It is noticed that CESU, WESCO & SOUTHCO have over drawn while NESCO has under drawn during the month. 
SLDC/ Discoms may please deliberate.
D.2: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl. No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220/132 kV, 100 MVA, Auto- 1 at Duburi
	Main tank severely damaged
	June-2018

	2
	220/132kV, 100MVA  Auto-2  at Bhadrak
	Fire hazard on 31.05.2017
	June-2018


CGM (O&M) may update the progress.

D.3: Communication issues 
The status of data communication from CGPs as deliberated in the 120th PSOC meeting meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	2
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. 
In the 121st PSOC meeting G.M. (RT&C) stated that they have raised certain queries regarding the provision of providing data communication facilities to SLDC by the CGP / Industries. SLDC stated that the “Procedure on Communication and Data Transmission”  approved by Hon’ble OERC  vide orders, dated 23.09.2011 passed in case Nos. 41, 42 and 51/2011 followed by corrigendum order issued in letter No.2243, dated 01.12.201, published in the Odisha Gazette No. 485 Dated 29th March 2012 was circulated by RT&C wing of OPTCL vide letter No. R&T-REGN-08/2011/198 (8) dated 19.04.2012. RT&C may refer the said letter wherein the provisions have been clearly mentioned.  Also RTC may take necessary initiative for filing Petition before the OERC. 
GCC / RT&C may please deliberate & update the progress.
D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 119th PSOC meeting IT stated that Parameters of 16 Nos meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
In the 120th PSOC meeting IT stated that M/s Secure Meter is not responding to them. It was decided that O&M shall convene a meeting with M/s Secure meters to resolve the issue.  
In the 121st PSOC meeting it was decided that SLDC shall write CPC and OPTCL to convene a meeting with TCS and Secure meters to discuss the issue. 

OPTCL/ SLDC may please deliberate.
D.5: Web based drawal / generation scheduling.

In the 111th PSOC meeting it was decided that from 1st August 2017 the schedule submitted through web portal will be considered. The web based schedule will be implemented for TTPS and Ib TPS from 1st September’2017. 
At present all State thermal generating stations including IPPs & CGPs are furnishing their schedule through web portal.

The following fetchers need to be incorporated in the software: 

1. Provisions for acceptance of backing down schedule for past block.

2. Provision for automatic extraction of Power Exchange schedule from the worksheet for incorporation in the schedule of respective Generator / CGP.

3. Navigation between different web pages within the portal

4. Report generation in excel format with down loading provision.
In the 120th PSOC meeting it was decided that SLDC and IT may discuss the issue and resolve.
In the 121st PSOC meeting it was decided that SLDC & IT will discuss the issue and resolve.

IT/SLDC may update the progress.

D.6.DISCOM Issues
CESU

1.   Construction of 132/33 kV S/s at Parjang and Kantilo
2.   Providing of 15 mins drawal data.
In the 121st PSOC meeting, AGM (Const.) stated that construction of 132/33 kV S/s at Parjang and Kantilo S/S will be placed in the next BoD meeting. 
C.G.M (Const.) may deliberate the status
NESCO
1. Day ahead Open access schedule is being changed at the end of day since last two months on daily basis due to which NESCO is facing either huge over-drawal or under-drawal.   

2. Data suspect for Joda and Jajpur Road feeder.

3. Although RVDU shows suspected data but actually drawing the actual load and it is quite unpredictable to know the exact drawal schedule position for that suspected data. Therefore it is requested to reflect the normal loading position for the above suspected datas.

4. There is huge difference of 7-10MU occur between RVDU drawal data and actual drawal data since last month due to which it is difficult to maintain the minimum deviation at the end of the month.   
NESCO may deliberate                                               
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by June’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by April’2018.

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	August’18

	4
	400/220 kV, 2x315 MVA Lapanga S/S
	July’18

	5
	220/33 kV, 2x20 MVA Baliguda S/S
	December’18

	6
	220/33 kV, 2x20 MVA Kalimela S/S
	December’18

	7
	220/33 kV, 2x20 MVA Kasipur S/S
	July’18

	8
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	June’18

	9
	220/33 kV, 2x20 MVA Narasinghpur S/S
	July’18

	10
	220/132 /33 kV, 2x100 MVA Aska S/S
	December’18

	11
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	Charged during March’18

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	December’18

	13
	220/132/33 kV Jayapatana S/S(320 MVA)
	December’18

	14
	220/132 kV Pratapsasan S/S(320 MVA)
	March’19

	15
	220/132 kV Kesinga S/S (320 MVA)
	December’18

	16
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	June’18

	17
	132/33 kV Ghense S/S
	Charged during April’18

	18
	132/33 kV Dhenkikote S/S 
	Charged on 24.02.2018

	19
	132/33 kV Betanati S/S
	July’18

	20
	132/33 kV Kantabanji S/S
	Charged on 28.02.18 

	21
	132/33 kV R.Udyagiri S/S
	July’18

	22
	132/33 kV Chikiti S/S
	August’18

	23
	132/33 kV Athagarh S/S
	June’18


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. 
CGM (Construction) / DISCOMs may please deliberate the status.
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC

As per the provision in the Act, SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators will record 15 min block energy injection,   the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the 119th PSOC meeting CGM (O&M) stated that Ib TPS may deposit the required amount to release meters (for check meter).

In the 121st PSOC meeting it was deliberated that IB TPS is yet to deposit the required amount for release of Energy meters.

In the 121st PSOC meeting it was decided that SLDC shall write IBTPS to attend the meeting and to deposit the required amount for release of Energy meter by O&M.
SLDC / IBTPS may please deliberate the status.

E.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same.
In the 113th PSOC meeting, it was decided that GRIDCO will take follow up action with all the RE generators to provide real time generation data to SLDC. ERLDC has reminded again to intimate the status.   

A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.
In the 121st PSOC meeting  it was decided that SLDC shall write a letter to Gridco to expedite the pilot projects.

SLDC/GRIDCO may please deliberate the status.
E.4: Major Events in the month of May’18
18.05.18: 132 kV Kesinga Traction feeder charged from Kesinga S/S..
23.05.18: 132 kV Pratapsasan bus charged through LILO arrangement of 132 kV Nimapara-Kesura line

31.05.18 : 132/ 33 kV, 1x40 MVA, Khuntuni GIS charged  through LILO arrangement of 132 kV Dehekanal-Grid Steel Alloys line.

E.5: Important Grid Incidences during the month of May’18.
On 25.05.18 at 16:30 hrs 220 kV Jaynagar-Laxmipur Ckt-I tripped at Jaynagar end due to bursting of ‘R’ ph LA (Relay indication at  Laxmipur-O/C in ‘R’ ph and ‘Y’ ph E/F, D/P, 44.3 km fault current-2.53 kA). 220 kV Jaynagar-Balimela Ckt-II tripped at   Jaynagar.  220 kV Jaynagr-Laxmipur Ckt-II tripped at Laxmipur on O/C in ‘R’ ph, ‘Y’ ph, E/F, D/P, 21.4 km, fault current-1.758 kA. On investigation it was also noticed that earth wire of 220 kV Jaynagar-Balimela Ckt-I snapped from gantry tower to  Loc. No-1454A at Jaynagar end.
O&M may deliberate
E.6: Outage of major transmission Elements during the month of May’18. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration
Dt/time
	Reason

	1
	220 kV Balasore-New Duburi Ckt
	16.05.18

19:32
	18.05.18

15:10
	‘R’ ph and ‘Y’ ph  insulator damaged at Loc. No-147. ‘R’ ph insulator damaged  at loc. No-189 and loc. No-281.

	2 
	220 kV Balasore-New Duburi Ckt
	18.05.18

16:56
	19.05.18

15:22
	 ‘R’ ph insulator damaged  at loc. No-189 and loc. No-297.

	3
	220 kV Balasore-Bhadrak Ckt
	22.05.18

21:50
	23.05.18

12:58
	Insulator damaged at Loc. No-327.


C.G.M. (O&M) may please discuss.
E.7:  Review of Outage Program of State Generators / Transmission elements for the month of July’18:
Tentative Outage programme for State Generators for the month of July’2018 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 2

# 5

# 6
	14.03.18 to 30.06.18
25.05.18 to 30.06.18

25.10.16 to continue

16.10.15 to continue
	T&G coupling cover water leakage
Shaft seal problem

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to continue
	Under R,M & U

	3
	Balimela
	# 1

# 2
	05.08.16 to continue

20.11.17 to continue
	Under R,M & U

Programming for R&M

	4
	Rengali
	# 5
	04.06.18 to 20.06.18
	Shaft seal problem

	4
	Upper Kolab
	# 2
	28.05.17 to continue
	Upstream leakage & intake gate Problem

	5
	TTPS
	# 2
	24.06.18 to 08.07.18
	Annual Maintenance


OHPC / SLDC may deliberate. 
E.8: Generation Program for the month of July’18.
Generation schedule for the month of July’18 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.06.17
	Reservoir Level as on 01.06.18
	MDDL
	High Flood    Reservoir Level

	
	July’18
(1st fortnight)
	July’18
(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	35
	35
	605.12
	606.33
	590 ft.
	630 ft.

	HPS-II, Chiplima
	25
	25
	-
	-
	-
	-

	Balimela
	120
	120
	1467
	1449.60
	1440 ft.
	1516 ft.

	Rengali
	30
	30
	115.12
	113.75
	109.72mtr 
	123.5 mtr.

	U.Kolab
	60
	60
	849.39
	847.69
	844 mtr 
	858 mtr.

	U. Indravati
	130
	130
	630.14
	628.77
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2705.3
	2712.20
	2685 ft.
	2750 ft.

	TOTAL
	430
	430
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

OHPC / SLDC may deliberate & Members may discuss. 
E.9: Anticipated power generation and demand for the month of July’2018.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1050
	1320

	2
	WESCO
	950
	1150

	3
	NESCO
	750
	950

	4
	SOUTHCO
	350
	450

	6
	Total Discom
	3100
	3870

	
	System Loss & others
	150
	200

	
	Total Demand
	3450
	4070

	Availability
	
	

	1
	Hydro
	430  
	1200

	2
	State Thermal
	770
	770

	3
	IPP, small hydro &RE
	350
	450

	4
	ISGS share (including OA& purchase)
	1350
	1350

	5
	CGP support (OA)
	300
	300

	6
	Total availability
	3200
	4070

	7
	Surplus / Deficit
	0
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (123rd) PSOC meeting.
PAGE  

