                                                                                                                  
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image1.png]PTC




Agenda

for

125th Power System Operational Co-ordination Meeting

Date: 20.09.2018
Venue: Hotel May Fair (Orchid), Bhubaneswar 

Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 125th PSOC Meeting to be held on 20.09.2018 at Hotel May Fair (Orchid), Bhubaneswar
Item no. 1: Confirmation of the minutes of the 124th PSOC Meeting held on 27.08.2018
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2017/2767 (47) dated 01.09.2018 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   :  Grid Performance for the month of August’2018
C.1:  Status of projects funded under PSDF scheme

C.2 :  Over drawal/under injection by ER Entities 

C.3:  Scheduling of Un-requisitioned Surplus (URS) power from ISGS – ERLDC
C.4:  Multiple Contingency due to the Tower Collapse of 400 kV PurneaBiharsharif D/C and 400 kV Kishenganj-Patna D/C in the Eastern RegionERLDC 

C.5:  Long Outage of transmission elements in Eastern Region
C.6:  Guidelines for the charging of Transmission line connecting two generating plants after tripping on fault or outage  

C.7:  Guidelines on Availability of Communication System 

C.8:  Review of Cyber Security Works/Activities 

C.9:  Data for preparation Load Generation Balance Report (LGBR) of ER for the year 2019-20 

C.10: Status of Implementation of islanding schemes in ER- Islanding scheme at IbTPS- OPGC 

C.11: Mock Black start exercises in Eastern Region 

C.12: Implementation of Web based PSP report in ERLDC 

C.13: PSS tuning of Generators in Eastern region 

C.14: Prolonged outage of Power System elements in Eastern Region 

C.15: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

C.16: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

C.17: Data for GEOSPATIAL energy portal of Neeti Aayog-CEA

C.18: Agenda point related to load forecasting by SLDC   

C.19: Implementation of Automatic Demand Management Scheme

C.20: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s

C.21: Update on status of telemetry.
D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Communication issues. 
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.
D.4: DISCOM agenda.
E.1: Commissioning status of New Transmission elements. 

E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
E.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.

E.4: Major Events in the month of August’18
E.5: Important grid incidences during the month of August’18.

E.6: Outage of major transmission Elements during the month August’18. (above 10 hrs).
E.7: Review of Outage Program of State Generators for the month of October’2018
E.8: Generation Program for the month of October’2018.
E.9: Anticipated power generation and demand for the month of October’2018.

F.1:  Date and Venue of the next (126th) PSOC meeting
PART B: GRID PERFORMANCE
Review of Grid Performance for the month of August’18.

A. Frequency:

Hourly frequency variation for the month of August’18.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	June’18
	0.00
	0.08
	8.36
	71.44
	20.13
	49.90

	July’18
	0.00
	0.05
	6.90
	72.04
	21.02
	49.98

	Aug’18
	0.00
	0.04
	5.30
	72.12
	22.54
	49.97


Maximum & Minimum frequency during the month of July & August’18.
	Month
	Freq (Hz)
	Date
	Time

	July’18
	Maximum –50.12
	04.07.18
	13:00 Hrs

	
	Minimum – 49.73
	18.07.18
	19:30 Hrs

	Aug’18
	Maximum –50.12
	13.08.18
	13:00 Hrs

	
	Minimum – 49.70
	04.08.18
	19:00 Hrs



In the 124th PSOC meeting Telecom stated that adoption of PMU frequency is under process.
Telecom may please deliberate.
B. Grid Demand for the month of Aug’18
	 Month
	Max. Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	July’18
	94.27
	29.07.18
	2572
	3457
	4498
	28.07.18
	22:00
	2010
	16.07.18
	13:00

	Aug’18
	114.57
	24.08.18
	3165
	4254
	5428
	23.08.18
	21:00
	3313
	28.08.18
	14:00

	Aug’17
	85.74
	26.08.17
	2500
	3360
	4269
	26.08.17
	24:00
	2647
	17.08.17
	16:00


C. Voltage Profile of 220 kV Buses in OPTCL system for the month of: Aug’18

	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Atri
	228.22
	18
	15:00
	212.05
	4
	19:15

	2
	Balasore
	228.51
	6
	5:45
	209.23
	9
	19:45

	3
	Barkote
	231.86
	20
	6:00
	224.81
	4
	19:15

	4
	Bhadrak
	231.11
	15
	13:00
	209.11
	23
	20:45

	5
	Bhanjanagar
	231.28
	7
	2:30
	213.21
	4
	9:15

	6
	Bidanasi
	229.72
	19
	9:45
	212.86
	7
	8:15

	7
	Bolangir
	229.14
	19
	3:45
	212.81
	4
	19:00

	8
	Budhipadar
	232.90
	19
	4:00
	221.29
	4
	19:15

	9
	Chandaka
	228.62
	19
	15:00
	211.88
	4
	19:15

	10
	Cuttack
	226.72
	19
	15:00
	209.80
	4
	19:15

	11
	Duburi(O)
	231.68
	26
	13:30
	218.69
	23
	20:45

	12
	Duburi (N)
	228.10
	26
	13:30
	215.17
	23
	20:45

	13
	Jayanagar
	235.73
	20
	16:30
	228.05
	22
	19:15

	14
	Joda
	234.40
	31
	14:30
	215.00
	10
	20:45

	15
	Katapalli
	235.15
	19
	4:00
	217.83
	4
	19:15

	16
	Lapanga
	235.55
	19
	4:00
	200.51
	21
	11:45

	17
	Laxmipur
	234.57
	15
	4:00
	224.87
	4
	19:15

	18
	Mendhasal
	229.61
	19
	15:00
	213.73
	4
	19:15

	19
	Meramundali
	226.78
	19
	16:00
	218.98
	23
	20:45

	20
	Narendrapur
	228.51
	26
	14:00
	209.23
	4
	19:15

	21
	Nayagarh
	231.16
	7
	3:45
	211.07
	4
	19:15

	22
	Paradeep
	226.43
	7
	5:45
	203.91
	23
	21:00

	23
	Tarkera
	233.30
	20
	6:00
	225.10
	4
	20:15

	24
	Theruvali
	232.43
	15
	4:00
	214.19
	4
	19:15

	25
	Samangara
	228.45
	19
	15:00
	211.53
	4
	19:15


The maximum Voltage of 235.73 kV occurred at Jayanagar 220 kV bus, while Lapanga 220 kV bus has experienced the minimum Voltage of 200.51 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Mendhasal, Meramundali  and New Duburi bus during the month of August’2018 are indicated. 
[image: image2.emf]200

205

210

215

220

225

230

235

240

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NARENDRAPUR 220 kV BUS

FOR AUGUST' 2018


[image: image3.emf]210

215

220

225

230

235

240

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF 220 KV JAYANAGAR BUS

FOR AUGUST'2018


[image: image4.emf]360

365

370

375

380

385

390

395

400

405

410

415

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF 400 KV MENDHASAL BUS

FOR AUGUST'2018


[image: image5.emf]390

395

400

405

410

415

420

425

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MERAMUNDALI 400 KV BUS

FOR AUGUST'2018


[image: image6.emf]390

395

400

405

410

415

420

425

430

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NEW DUBURI 400 KV BUS

FOR AUGUST'2018


Members may discuss.
D. Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of Aug-2018 [image: image7.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  AUGUST'2018

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

2x160 41.12 18 21:30 7.44 9 16:15

41.12 18 21:30 12.36 18 14:45

87.84 21 10:45 24.40 17 19:00

88.80 21 10:45 24.40 17 19:00

80.36 30 20:15 24.68 20 18:30

1x100 57.80 13 19:30 9.64 5 17:30

1x160 102.00 17 21:15 18.94 5 17:30

1x160 73.00 23 19:00 16.00 25 09:00

1x160 91.12 21 12:15 24.24 27 19:45

1x160 80.36 21 12:15 21.16 27 19:45

1x160 48.40 1 19:30 10.04 12 15:00

1x100 39.68 3 10:45 7.00 12 15:00

1x100 39.56 3 10:45 7.12 12 15:00

2x160 124.36 4 20:45 19.88 11 13:00

131.32 4 20:45 21.04 11 13:00

90.36 29 19:00 8.28 31 01:45

90.24 29 19:00 8.24 16 15:45

1x100 52.60 4 22:45 20.80 5 18:15

1x160 90.64 4 22:45 36.04 5 18:15

1x100 56.52 4 22:45 22.24 5 18:15

1x160 87.16 10 11:30 34.36 5 18:15

CUTTACK 1x160

77.52

4 13:15 15.36 30 09:45

1x160 56.48 1 19:45 7.84 6 13:30

1x100 35.68 1 19:45 7.08 4 14:15

1x100 28.64 30 11:15 4.80 1 11:00

1x160 59.48 15 19:00 8.28 15 07:45

1x160 60.00 15 19:00 8.40 15 07:45

51.80 15 21:15 27.12 8 13:45

52.16 15 21:15 26.32 8 13:45

52.12 15 21:15 26.52 8 13:45

1x100 25.52 11 20:15 6.40 3 01:00

1x100 27.48 17 10:00 6.40 3 01:00

1x160

2x160 65.48 8 19:00 8.96 8 14:30

65.28 8 19:00 11.36 8 14:45

45.20 29 12:30 3.88 6 15:00

36.96 7 08:15 3.88 6 15:00

43.52 29 12:30 3.36 14 16:00

2x100 25.80 18 10:45 9.00 10 12:00

36.00 17 06:15 14.40 10 12:00

2x160 105.40 9 21:45 34.64 21 11:45

105.16 9 20:30 34.68 21 11:45

1x100 60.48 9 21:45 19.56 21 11:45

1x160 113.32 22 19:30 17.92 12 19:45

1x100 69.40 30 19:15 10.88 12 19:45

1x50

4x100  61.68 20 19:45 12.12 28 03:45

63.16 20 19:45 13.08 28 03:45

58.16 31 01:45 12.28 28 03:45

65.36 21 12:30 9.32 31 20:15

2x100 82.04 7 07:45 13.72 15 04:00

77.36 7 07:45 13.48 17 09:15

1x160  52.18 1 19:45 0.00 10 16:00

1x160 52.18 1 19:45 0.00 10 16:00

2x100 59.28 21 20:15 21.80 7 05:30

78.08 21 15:30 21.00 19 14:30



BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

Drawal details

Maximum Minimum



BHADRAK 220/132 KV

{Bhadrak area load, Bhadrak(T),Soro,  

FACOR (I), Dhamra Port}

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}

3x160 

ATRI                                                     

{Banki, Khurda, Chandpur & Argul}

SAMANGARA                                          

{ Puri, Nimapara & Konark}

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, 

Digapahandi, Mohana.}

THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), 

MCL, Sundergarh,Brajarajnagar, 

Rajgangpur}

2x160 

Rayagada & Paralakhemundi 

can be fed from Machhkund 

system.

Supported by Burla & 

Chipilima power.

PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 



"*" - Alternate P/S from 

Kuchei.



DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, 

Jajpur Road, Kalarangi, Jajpur Town}

Mendhasal { Part area load of Khurda S/S}

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100



BIDANASI 220/132 KV

{Bidanasi, Khurda }

3x100 



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }

JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]

LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 

BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & 

Katapali area load.}



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}


E. DISCOM Drawal up to the month of August’18
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	Apr’18
	745.479
	734.495
	770.403
	19.655
	750.748
	16.253

	
	May’18
	770.329
	819.87
	850.674
	20.004
	830.67
	10.8

	
	June’18
	745.480
	836.254
	848.445
	14.721
	833.724
	-2.53

	
	July’18
	770.329
	805.001
	823.135
	16.707
	806.428
	1.427

	
	Aug’18
	770.329
	825.849
	833.67
	17.428
	816.242
	-9.607

	WESCO
	Apr’18
	585.205
	636.576
	689.137
	57.318
	631.819
	-4.757

	
	May’18
	604.712
	636.024
	1042.198
	362.004
	680.194
	44.17

	
	June’18
	585.205
	640.766
	995.1281
	359.629
	635.4991
	-5.267

	
	July’18
	604.712
	612.348
	767.095
	160.722
	606.373
	-5.975

	
	Aug’18
	604.712
	586.549
	1,152.89
	561.626
	591.265
	4.716

	NESCO
	Apr’18
	504.658
	418.945
	528.936
	105.079
	423.857
	4.912

	
	May’18
	521.4799
	480.187
	576.819
	102.344
	474.475
	-5.712

	
	June’18
	504.658
	488.448
	598.361
	113.554
	484.807
	-3.641

	
	July’18
	521.4799
	481.593
	581.864
	95.907
	485.957
	4.364

	
	Aug’18
	521.4799
	494.386
	644.557
	138.545
	506.012
	11.626

	SOUTHCO
	Apr’18
	300.822
	298.76
	298.778
	0
	298.778
	0.018

	
	May’18
	310.849
	321.453
	323.114
	0
	323.114
	1.661

	
	June’18
	300.822
	316.746
	315.514
	0.57
	314.944
	-1.802

	
	July’18
	310.849
	316.309
	313.076
	0.574
	312.502
	-3.807

	
	Aug’18
	310.849
	322.184
	322.519
	0
	322.519
	0.235


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
     Members may please discuss.

F. Energy Generation / Import up to the month of Aug’18
Figures in MU  
	Month
	Thermal

(TTPS+IbTPS)
	OHPC 
& MKD
	CGP Support
	IPP Inj.
	RE
	ISGS
	Total

	April’18
	535.100
	421.700
	362.530
	198.950
	9.690
	872.260
	2400.240

	May’18
	567.940
	573.520
	313.169
	199.230
	14.390
	1066.640
	2734.893

	June’18
	485.813
	481.601
	219.983
	203.230
	11.897
	1084.870
	2487.390

	July’18
	440.179
	421.582
	213.953
	193.928
	10.102
	1292.141
	2571.886

	Aug’18
	473.390
	689.310
	163.300
	202.940
	13.680
	1621.990
	3164.600

	Total
	2502.422
	2587.713
	1272.935
	998.278
	59.759
	5937.901
	13359.009


G.  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of Aug’18 are as detailed:
	Month
	Total Generation
	Odisha Drawl
	AP Drawl

	
	MU
	Avg (MW)
	MU
	Avg (MW)
	MU
	Avg (MW)

	Apr’18
	37.162
	51.610
	18.613
	25.851
	16.943
	25.532

	May’18
	48.888
	65.700
	22.424
	30.140
	24.492
	32.919

	June’18
	43.185
	59.980
	19.692
	27.350
	21.635
	30.048

	July’18
	45.146
	60.680
	20.894
	28.083
	22.148
	29.769

	Aug’18
	51.319
	68.977
	23.507
	31.595
	25.708
	34.554

	Total
	225.700
	61.465
	105.13
	28.630
	110.926
	30.208


Machhakund drawal is expected to be more in the coming months due to drawal of power from Podagada S/S by SOUTHCO. 
SLDC/ SOUTHCO may deliberate.
H. Under Frequency Relay operation in OPTCL System during the month of Aug’18.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of Aug’18.
I. Status of Open Access applications up to the month of Aug’2018
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’18
	26
	79
	0
	31
	136
	26
	76
	0
	31
	133
	3

	2
	May’18
	59
	90
	0
	26
	175
	59
	89
	0
	26
	174
	1

	3
	June’18
	14
	57
	0
	30
	101
	14
	57
	0
	30
	101
	0

	4
	July’18
	18
	145
	0
	26
	189
	18
	145
	0
	26
	189
	0

	5
	Aug’18
	26
	90
	0
	37
	153
	26
	90
	0
	37
	153
	0

	
	Total
	143
	461
	0
	150
	754
	143
	457
	0
	150
	750
	4


PART C – Issues discussed in the 149th  OCC meeting of ERPC held on 18.09.2018
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
146th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	30.11.18
	162.5 Cr.


	38.09Cr.
	90% equipment installed and commissioned. Stn Tfr and some measuring instruments are under tendering process.



	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.22 Cr
	Request for 10% grant already submitted as agreement has signed
	Tender floated

	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov

2018,

Chiplima

Dec 2018
	22.35 Cr.
	
	Tendering under process

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 


	28-08-17
	
	31.94 Cr
Ested. Cost. Approved amount 30.26 Cr. Grant amount 27.23 Cr.
	
	Appraisal committee recommends for project cost of 30.23 Cr and 27.23 Cr grant by monitoring committee. Tender floated.

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost. 2.93 Cr recommended by Appraisal committee.
	
	Recommendation by Appraisal committee already forwarded to CERC for concurrence.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	20.02.2018  Date of submission 
	
	41.1 Cr

Estt cost
	
	Compliance to TSEG observation submitted. Protection audit by ERPC under progress. Report will be submitted after completion.


   CGM (O&M) / OHPC/ SLDC may please update the status.
C.2 : Over drawal/under injection by ER Entities 

Over drawl figure of DVC, West Bengal and Odisha from 21-08-2018 to 31-08-2018 are shown below: 

Odisha 


 




 Over Drawl 
     
Max. Over Drawl 
   

     (MU)  
               (MW)
21-08-2018 
5.391589

508.9596

22.08.2018
4.865006

519.5552
23.08.2018
2.888012

546.7861

24.08.2018
1.254641

357.1823

25.08.2018
2.337058

475.7424

26.08.2018
3.006029

594.2872

27.08.2018
3.141262

540.3314

28.08.2018
4.496704

542.6694

29.08.2018
2.459407

386.3548

30.08.2018
2.800647

437.8613

31.08.2018
2.524151

495.7537

West Bengal, DVC and Odisha may please deliberate the reason of continuous over drawal and future action plan to mitigate such contingency situation. 
SLDC/ GRIDCO may deliberate
C.3: Scheduling of Un-requisitioned Surplus (URS) power from ISGS – ERLDC 

In 148th OCC meeting, NTPC and beneficiaries of ER are agreed that the decision of ERLDC in respect of scheduling & dispatch of URS power from the NTPC stations in the Eastern Region shall be binding on them and also indemnify ERLDC in all respects for this scheduling of URS power. 

In line to this and as per the CERC vide order dated 17/10/2017 against Petition No. 16/SM/2015, ERLDC has given permission to the beneficiaries to punch their URS requisition from the respective generating station in ERLDC WBES portal using their login credentials. No real time approval/consent form NTPC Patna is required now onwards. URS scheduling methodology followed: 

1. All day-ahead URS requisitions punched by various beneficiaries from a particular ISGS station till 19:00 Hrs are considered together and allocated on pro-rate basis.
2. 19:00 Hrs on ward for day-ahead schedule and real time schedule preparation, URS allocation is done on first cum first serve basis. 
3. URS requisition of different beneficiaries punched for a particular generator for a particular block is scheduled on pro-rate basis. 

SLDC may note

C.4: Multiple Contingency due to the Tower Collapse of 400 kV Purnea-Biharsharif D/C and 400 kV Kishenganj-Patna D/C in the Eastern Region-ERLDC 

On 01-09-18 400 kV Kishenganj-Patna D/C got tripped on Tower Collapse. With this tower collapse and already ongoing outage of 400 kV Purnea-Biharsharif D/C on tower collapse (since 10-08-18) the network in NR/ER/NER corridor has become significantly depleted. The high hydro generation scenario prevailing at Tala, Chukha, Sikkim and NER is causing high flow in the chicken neck corridor. Under such condition, it is pertinent to note that contingency of Purnea-
Muzaffarpur or Purnea-Malda D/C line will lead to islanding of Sikkim, Bhutan, N. Bengal, NERand the HVDC from the rest of the system. 

 In order to ensure the system reliability following actions have been taken: 

xxxxxx

Desired Actions from All Utilities in the Eastern region: 

1. ENCIL and PGCIL:To expedite the restoration of 400 kV Purnea-Biharsharif D/C and 400 kV Kishenganj-Patna D/C on war footing basis. 

2. PGCIL:  

a. Any untoward contingency of Kishenganj and Purnea substation to be informed to ERLDC/NLDC at the earliest and to be ready for handling any emergency like flood/equipment failure etc. 

b. Protection System at Binaguri, KishenganjandPurnea to be kept healthy. No unwanted tripping of transmission lines is desired from these substations because of protection mal-operation. c. Communication System along with SCADA data to ERLDC to be ensured at all points of time.

3. All Utilities of the Eastern region:  

a. Keeping the Lines/ICTs available all the time. 

b. Any outage at 220 kV level affecting the East Bihar, North Bengal and Sikkim to be done with prior information to ERLDC.

 c. All defence mechanism such as UFR, SPS and df/dt to be kept in service all the time.

4. All SLDCs and Generators: All constituents to adhere drawl according to their schedule to avoid any stress in the grid and corridor. 

5. All Generators of Eastern Region: RGMO/FGMO for all eligible generating unit to be kept in service.  

6. All Hydro Generation of Sikkim/Bhutan: Blocking of high-frequency tripping of Units in Hydro station of NER/Sikkim/Bhutan during the contingency of system separation and high Rate of change of frequency (3.5 to 4 Hz/sec). 

O&M/ All Generators/SLDC may discuss

C.5: Long Outage of transmission elements in Eastern Region
e) Breakers at 400/220kV Indravati (OHPC) S/s  

In 141st OCC, it was explained that 3x105 MVA 400/220kV ICT-I tie breaker, 220kV Bus coupler and transfer bus breakers are not in service at 400/220kV Indravati (OHPC) S/s.  

In 142nd OCC, OHPC submitted the action plan as follows: 

1. 220kV Bus Coupler: CB and CT needed to be replaced. They would restore the Bus coupler by August 2018.  
2. 220kV Bus tie: CB and CT needed to be replaced. They would restore the Bus Tie by November 2018. 
3. 400kV Tie-1 Breaker: CB and CT needed to be replaced. They would restore the 400kV  Tie-I by January 2019.  

In 148th OCC, OHPC informed that 220kV Bus Coupler would be restored by end of August 2018.  

In the 124th PSOC meeting OHPC stated that 220 kV Bus coupler CB is in operational condition. Spare CT is not available for restoration of Bus coupler. Tendering for 220 kV Bus tie and 400 kV Tie –I are expected to be done by January’2019. It was suggested that OHPC may borrow CTs from OPTCL for restoration of 220 kV Bus coupler. 

OHPC may please update. 

C.6:  Guidelines for the charging of Transmission line connecting two generating plants after tripping on fault or outage  

There is a prevailing issue on the charging of transmission line connecting two generating complex after its outage/tripping. It has been observed sometimes that either of the utility is not ready for charging of the line from their end after its tripping on fault/outage. This results in the delay in the restoration of line and thus affecting the reliability of both the generating station. In view of this, there is a need of guideline on charging of such transmission lines.  

List of such transmission lines is given below: 

I. 400 kV Farakka-Kahalgaon Q/C. 

II. 400 kV Kahalgaon-Barh D/C.  

III. 400 kV Farakka-Sagardighi D/C.

IV. 400 kV RTPS-DSTPS D/C. 

As a general guideline following may be considered   

   If voltage difference between two system is more than 5 kV system which have lower voltage should charge the line

   In case voltage difference is less than 5 kV system which have higher fault level should charge

   If only one end has line reactor than the end which is not having the line reactor should attempt to charge first.
SLDC / O&M may discuss

C.7: Guidelines on Availability of Communication System 

As per Regulation 7.3(i) of CERC (Communication System for Inter-State transmission of Electricity), Regulations, 2017 and CERC letter dated 27.06.2017, National Power Committee (NPC) has been entrusted to prepare Guidelines on Availability of Communication System in consultation with RPCs, NLDC, RLDC and other stakeholders. 

 Accordingly, a Working  group was  constituted  with  Chief  Engineer  & Member  Secretary  (NPC) as Chairperson of the Working group and consisting of members from all the RPCs, PGCIL, POSOCO and few of the STUs. Three meetings of the Working group were held and a draft guidelines on “Availability of Communication  System” was finalized  in the 3rd meeting. 
Draft copy is enclosed at Annexure-B10. 

Members requested to send their comments to cenpc-cea@gov.in with a copy to mserpcpower@nic.in.  

Telecom may note and comply.

C.8: Review of Cyber Security Works/Activities 

CEA vide letter informed that Secretary (Power) is going to review the cyber security related works /activities being carried out in Power Sector. In this regard, it is requested to provide the State wise status on following action points pertaining to cyber security at the earliest: 

 1. Appointment of organization-wise Chief Information Security Officers and its status 

2. Identification of organization-wise Critical Infrastructure and its status 

3. Preparation of organization-wise Crisis Management Plan and its status 

4. Status of Cyber Security Mock Drill activity in coordination with CERT-In 

5. Status of Training / Workshops on Cyber Security organized / participated by power sector entities

6. Status of action taken on CERT-In / NCIIPC advisories 

IT may Discuss & comply

C.9: Data for preparation Load Generation Balance Report (LGBR) of ER for the year 2019-20 

As per the IEGC, RPC Secretariat is responsible for finalization of the Annual Load Generation Balance Report (LGBR) for Peak as well as Off-peak scenarios and the annual outage plan for the respective region  

To facilitate the preparation of LGBR of Eastern Region by ERPC Secretariat within the schedule period, the following data/information for the year 2019-20 in respect of the constituents/utilities of Eastern Region is urgently required: 
i) The unit wise and station wise monthly energy generation proposed from existing units during 2019-20 (thermal/hydro/RES).

ii) Annual maintenance programme for each of the generating units (thermal and hydro both).

iii)  Generating units under R&M / long outage indicating date of outage and reasons of outage and expected date of return (thermal and hydro both). 

iv) Partial and forced outage figures (in %) of generating units for the last 3 years.                                  

v) Month wise peak demand (MW) – restricted and unrestricted peak demand. i) Month wise off-peak demand (MW).  

vi) Month wise energy requirement (in MU). 

vii) Month wise & source wise power (both MU & MW) purchase and/or sale plan. ix) Schedule of commissioning of new generating units during 2019-20 and unit-wise monthly generation programme (in MU).

viii) Allocation of power from new generating units. 

ix) Month wise and annual planned outage of transmission system (Transmission lines 220kV and above / ICTs / Reactors/ other elements. 

Information may please also be submitted in the form of soft copy through email (mail ID: mserpcpower@nic.in / erpcjha@yahoo.co.in). 

All Generators/GRIDCO/O&M/SLDC may furnish the above data at the earliest

C.10: Status of Implementation of islanding schemes in ER- Islanding scheme at IbTPS- OPGC 

2. Islanding scheme at IbTPS- OPGC 

The islanding scheme was discussed in 68th PCC Meeting held on 18-06-2018.  PCC opined that the draft scheme submitted by Odisha was three years old and the draft scheme is needed to be reviewed with existing network configuration.   

PCC decided to discuss the islanding scheme in next PCC Meeting and advised OPTCL to submit all the relevant details to ERPC and ERLDC.  

In 69th PCC Meeting, it was decided that ERLDC and ERPC would study and finalize the islanding scheme in next PCC Meeting.
In the 124th PSOC meeting SLDC stated that PCC sought data from SLDC to finalize the quantum of load i.e max, min and avg to be considered for islanding scheme. It was decided to convene a meeting with IBTPS, SLDC and O&M to discuss and finalize.

     O&M / IbTPS may discuss 
C.11: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2018-19 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2018
	Done on 08.06.2018
	Last week of January 2019
	

	3
	Rengali
	2nd week of June 2018
	Done on 18.08.2018
	Last week of November 2018
	

	4
	U. Indravati
	3rd week of June 2018
	August’18
	2nd week of February 2019
	

	6
	Balimela
	3rd week of October  2018
	September’18
	1st week of March 2019
	

	9
	Burla
	Last week of June 2018
	Done on 07.06.2018
	Last week of February 2019
	


Mock black start exercise for Balimela will be done at the time of workshop conducted by ERPC at Upper Kolab on dated 28th Sept’18.

SLDC/OHPC may deliberate

C.12: Implementation of Web based PSP report in ERLDC 

After successful parallel testing of Web based PSP and with continuous support from ER beneficiaries and generators, the web based PSP has successfully migrated from excel based PSP reporting to Web based PSP reporting portal on 07th September 2018. However, some utilities are still not filling-in data in Web based portal regularly during night hours. It is once again requested to the parties to fill the 24hrs generated energy, energy exchange data in ERLDC portal by 02:00hrs on daily basis regularly for error free and in time publication of the report during night hour. 

Nodal Persons from ERLDC side: 

1. Shri Tushar Ranjan Mohapatra - (9433041873)

2. Shri Chandan Mallick – (9007059660) 

OCC advised all the utilities to nominate a nodal officer to ERLDC vide mail: erldcso@posoco.in and submit the relevant data in PSP reporting portal.  

In the 124th PSOC meeting SLDC stated that implementation of the above operation was scheduled to be started from 1st August’2018. OHPC, OPGC, TTPS and IPPS were requested to furnish the required data to SLDC and nominate their nodal person to ERLDC.

Members may discuss.

C.13: PSS tuning of Generators in Eastern region 

Several Cases of Low frequency Oscillations have been observed in the Eastern Region. In view of this, it is desirable to have the PSS tuning of Generators in Eastern region to improve the system damping. It is mandatory as per existing CERC and CEA regulation to tune 100 MW and above generating units.  

In view of that, Generating station may kindly update the following details to ERLDC/ERPC: 

 Name of Generating Power Plant:  

	Unit

No
	Type of Excitation  System  (Static/ Brushless /Other)
	IEEE Model (IEEET1/ ESST1A/ Other)
	Name of Excitation System Vendor (ABB/GE /Hitachi/ other)
	Whether PSS is Tuned of not (If tuned Date of tuning)
	Whether Report of tuning Submitted or not

	
	
	
	
	
	


In line with regulations, all generating power plant to take up the PSS tuning activities at earliest with their vendors and submit the report after PSS tuning for verification. The response data with PSS tuning also to be shared with ERLDC/ERPC for validation in either excel or .csv format. This will be monitored in OCC on regular basis.  

OCC advised all the generators to submit the relevant data as per the format to ERLDC and ERPC. 

Generators may kindly submit the details and inform the tentative plan for PSS Tuning.

C.14: Prolonged outage of Power System elements in Eastern Region 
(ii) Hydro Generating units: 

 Sr. No Generating Station Unit No 

Cap(MW) 
Reasons for outage 
Outage date

1 Burla 



1 

37.5 

R&M Work

25.10.2016
2 Burla 



2 

37.5

R&M Work

16.10.2015 

3 Burla 



5 

37.5

R&M Work

25.10.2016 

4 Burla 



6 

37.5

R&M Work

16.10.2015 

5 Balimela 


1 

60 

R & M Work

05.08.2016
6 U.Kolab 


2 

80

Repair of MIV&

Draft tube gate leakage28.05.2017 

7 Chipilima 


3 

24 

R&M work

21.07.2018
8 Chipilima 


1 

24

Flood water

21.07.2018 

It is therefore seen that about 338 MW hydro capacity in Odisha is under forced outage / R&M and therefore not available for providing the much needed peaking support. SLDC / OHPC may please indicate the restoration plan of the units.
OHPC may deliberate

C.15: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA. 

In 142nd OCC, ERLDC informed that, in line with Enquiry Committee Recommendation, cyber security audit is being conducted on regular basis for SCADA system installed at ERLDC and SLDC as well but cyber security audit for telecom infrastructure installed in Eastern Region is not being carried out.  

OCC advised all the constituents to conduct the cyber security audit on telecom infrastructure installed in Eastern Region. It is further advised that compliance / mitigation of the points observed during the audit should also be completed for improvement of the telecom infrastructure in ER. 

In 37th TCC meeting, it was decided that a workshop would be conducted by CEA at ERPC for further benefit of ER Constituents.  

In 144th OCC, ERLDC informed that they have already conducted a workshop with the help of NPTI, Durgapur on 21st March 2018. 

A workshop on cyber security was conducted by CEA at ERPC, Kolkata on 09-05-2018.  

As suggested by CEA, a format would be circulated among ER constituents for furnishing the information of their respective systems for discussion in OCC Meeting. The format is enclosed at Annexure-E2. 

OCC advised all the constituents to submit the information to ERPC as per Annexure-E2.  

In the 123rd PSOC meeting IT stated that the Audit report has already been received. After depositing the required charges, audit for FY 2018-19 will be started. It was suggested that IT shall furnish the information as sought by ERPC in the required format.
In the 124th PSOC meeting IT stated that the Audit team have arrived on 27.08.18 to impart training.  

CGM (IT) may update the status.   

C.16: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.  

As per the information received from the constituents the following generators certified with IS 18001:  

 All NTPC stations in Eastern Region  

 Teesta, NHPC 

 All OHPC generating units  

 All CESC generating units  

 All units of WBPDCL 

 DGPC units 

In the 117th PSOC meeting CGM (O&M) stated that draft project report for Mendhasal S/S has been submitted to BIS. The report will be approved in the meeting to be conducted by them.

In the 122nd PSOC meeting CGM (O&M) stated that Audit team is expected soon.

In the 123rd PSOC meeting CGM (O&M) stated that the report is yet to be received.

In the 124th PSOC meeting O&M stated that program for imparting training has been scheduled   during 1st week of September’2018. Audit will be done after completion of training.
     O&M may deliberate the status

C.17: Data for GEOSPATIAL energy portal of Neeti Aayog-CEA
NITI Aayog is developing a user friendly GIS based Energy Map of India, which would provide true locations of all energy resources in India including power plants, coal and oil reserves, transmission lines etc.  

CEA sought the information of name, voltage level, capacity, longitude and latitude of 33kV and 66 kV substations and lines.  

The information may be shared with CEA vide email: cedpd-cea@gov.in.  

All Discoms are requested to submit the above data to CEA with a copy to SLDC for forwarding to ERPC.                                                                                        

In the 122nd PSOC meeting it was deliberated that for submission of line data, detail mapping of the line is required, which involve a lot of expenditure. However, the Discoms may furnish the S/S data in 1st phase. 

All primary S/Ss data in respect of CESU, NESCO & WESCO has been received.
In the 124th PSOC meeting SOUTHCO was requested to furnish the data. 
The information may be shared with CEA vide email: cedpd-cea@gov.in. 
DISCOMs /SLDC may deliberate 

 C.18: Agenda point related to load forecasting by SLDC   
For better grid management and shutdown planning, RLDCs needs to do short term load forecasting. Accuracy and effectiveness of load forecasting depend on input data. As per current practice, day ahead load forecasting is being done at ERLDC by analyzing trend previous days demand. However, for further tuning and better accuracy of load forecasting result, demand estimation from SLDCs are to be done at their end and same need to be shared with ERLDC for estimation of Eastern Region demand. 

In the 123rd PSOC meeting SLDC stated that the State demand forecasting is being done as per the drawal forecast by all the DISCOMs. The DISCOMs were requested to share their forecast methodology for intimation to ERLDC.
In the 124th PSOC meeting SLDC requested all the DISCOMs to forward their load forecast methodology by 1st week of September’2018.

SLDC & DISCOMs may deliberate
C.19: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************

The latest status along with proposed logic as follows:
[image: image8.emf]
[image: image9.emf]
In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 123rd PSOc meeting SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval

In the 124th PSOC meeting SLDC stated that the revised estimate has been approved in the BoD.

SLDC may deliberate the status.
C.20: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 123th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by Dec’18. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by Dec’18.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Keonjhar S/S (220/33 kV) by September’18.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	December 2018 


C.21: Update on status of telemetry  

CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed  NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action.

ERLDC stated that status of Breaker & isolator of NALCO & JITPL are not available.

Telecom & NALCO may deliberate.  

PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of August’18:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	-9.607
	1.163

	2
	WESCO
	0
	4.716
	0.804

	3
	NESCO
	0
	11.626
	2.351

	4
	SOUTHCO
	0
	-9.108
	2.826

	
	Total
	0
	-2.373
	


It is noticed that NESCO & WESCO have over drawn while CESU & SOUTHCO were under drawn from their scheduled energy during the month. 
SLDC/ Discoms may please deliberate.
D.2: Communication issues 
The status of data communication from CGPs as deliberated in the 124rd PSOC meeting meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	2
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. 
In the 123rd PSOC meeting it was deliberated that RT&C have sought some information from Telecom wing which will be intimated. NALCO stated that due to problem in their internal communication system, data communication to SLDC is being interrupted.
In the 124th PSOC meeting Telecom stated that communication system for Paradeep area industries will be completed by September’2018. Telecom was advised to give a reply to the information sought by RT&C. 

GCC / RT&C may please deliberate & update the progress.
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 119th PSOC meeting IT stated that Parameters of 16 Nos meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
In the 120th PSOC meeting IT stated that M/s Secure Meter is not responding to them. It was decided that O&M shall convene a meeting with M/s Secure meters to resolve the issue.  
In the 121st PSOC meeting it was decided that SLDC shall write CPC and OPTCL to convene a meeting with TCS and Secure meters to discuss the issue. 
In the 123rd PSOC meeting IT stated that out of 840 Nos interface meters connected with AMI, 750 Nos are reporting at present. The newly replaced meters are not reporting. 2 Nos. of meters has sent to M/s SECURE meters for study.

In the 124th PSOC meeting O&M stated that SLDC may intimate the list of defective energy meters to O&M on monthly basis for necessary action. IT may ask TCS to co-ordinate with Secure meters and develop a driver data extraction  
IT/ SLDC may please deliberate.
D.4: DISCOM Agenda

CESU

Providing of 15 minute drawal data by SLDC.

CESU may deliberate

PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by Dec’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by Oct’2018.

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	Oct’18

	4
	400/220 kV, 2x315 MVA Lapanga S/S
	Sept’18

	5
	220/33 kV, 2x20 MVA Baliguda S/S
	July’19

	6
	220/33 kV, 2x20 MVA Kalimela S/S
	March’19

	7
	220/33 kV, 2x20 MVA Kasipur S/S
	Oct’18

	8
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	September’18

	9
	220/33 kV, 2x20 MVA Narasinghpur S/S
	Charged on 24th August’18

	10
	220/132 /33 kV, 2x100 MVA Aska S/S
	March’19

	11
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	Charged during March’18

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’19

	13
	220/132/33 kV Jayapatana S/S(320 MVA)
	March’19

	14
	220/132 kV Pratapsasan S/S(320 MVA)
	Dec’19

	15
	220/132 kV Kesinga S/S (320 MVA)
	March’19

	16
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	September’18

	17
	132/33 kV Ghense S/S
	Charged during April’18

	18
	132/33 kV Dhenkikote S/S 
	Charged on 24.02.2018

	19
	132/33 kV Betanati S/S
	March’19

	20
	132/33 kV Kantabanji S/S
	Charged on 28.02.18 

	21
	132/33 kV R.Udyagiri S/S
	December’18

	22
	132/33 kV Chikiti S/S
	October’18

	23
	132/33 kV Athagarh S/S
	Charged on 31.05.2018

	24
	132/33 kV Udala S/S
	Charged on 16.09.2018


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement.
In the 124th PSOC meeting Construction stated that Narsingpur S/S has been charged with T arrangement of 220 kV Meramundali-Bhanjanagar line. After laying of optical fiber LILO arrangement will be done. Telecom stated that ERLDC has advised to provide at least one side data either from Meramundali or from Bhanjanagar end.  

CGM (Construction) / DISCOMs may please deliberate the status.
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC

As per the provision in the Act, SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators will record 15 min block energy injection,   the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the 119th PSOC meeting CGM (O&M) stated that Ib TPS may deposit the required amount to release meters (for check meter).

In the 122nd PSOC meeting Ib TPS stated that this has already been approved by their Authority. The required amount will be deposited soon.

In the 123rd PSOC meeting O&M stated that the required amount is yet to be deposited by IB TPS. Ib TPS have not sent their representative to the meeting for deliberation.

In the 124th PSOC meeting IbTPS stated that due to change in price of energy meters, the revised proposal has been sent to their management for approval.
O&M/ IBTPS may please deliberate the status.

E.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same.
A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.

M/S Secura Meters Ltd has shown a demo for the pilot project on dated 09.07.2018. However, the data integration with SLDC VPS was not elaborated in the said demo. 
In the 123rd PSOC meeting Telecom stated that M/S Secure meters could not complete the Demo, as M/S Chemtrol requires Rs. 3.5 lacs to allow firewall access to them. M/s Chemtrol also interested to take up the work. GRIDCO may allow them for the pilot project. OPTCL may examine for Firewall access to avoid burden to the Solar projects.

In the 124th PSOC meeting it was suggested that GRIDCO may write a letter to Chemtrol for the pilot project.
SLDC/GRIDCO may please deliberate the status.
E.4: Major Events in the month of August’18
24.08.18: At 13:50 Hrs 220/33 kV Narsingapur S/S charged with T arrangement from 220 kV  Meramundali-Bhanjanagar Ckt-I.  
28.08.18: At 18:23 Hrs 132 kV Nuapatana-Banki line charged.
For information of Members 

E.5: Important Grid Incidences during the month of August’18.
On 31.08.2018 at 13:43 hrs220 kV Joda-TTPS Ckt-I & II tripped at both ends (Ckt-I-At TTPS –D/P, Zn-I, dist trip-dist 93.32 km, ‘Y’ ph to ‘B’ ph, IY-2.6 kA, IB-2.4 kA. At Joda-D/P, ‘Y’ ph to ‘B’ ph, Zn-I, dist-61.164 km, fault current IL1-408.77 amp, IL2-911.32 amp, IL3-968.97 amp, IN-983.97 amp. Ckt-II-At TTPS –D/P, Zn-I, dist trip-dist 93.17 km, IY-2.6 kA, IB-2.4 kA. At Joda-D/P, ‘, ‘Y’ ph to ‘B’ph, Zn-I, dist-60.264 km, fault current IL1-417.89 amp, IL2-936.51 amp, IL3-910.79 amp, IN-1105.11 amp). At 13:50 hrs 220 kV JSPL-Jamshedpur Ckt tripped at Jamshedpur and 220 kV Joda bus became dead as 220 kV Joda-Ramchandrapur Ckt tripped at both end at 10:53 hrs and B/d work was under progress at Joda S/S.

Members may discuss
E.6: Outage of major transmission Elements during the month of August’18. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration

Dt/time
	Reason

	1
	132 kV Duburi-Mesco Ckt-I
	04.08.18
17:59
	05.08.18
12:31
	‘Y’ ph insulator damaged at Loc. No-3

	2 
	400 kV Meramundali-Duburi Ckt-I
	09.08.18
09:40
	09.08.18

21:27
	‘B’ ph jumper snapped at Loc. No-24


C.G.M. (O&M) may please discuss.
E.7:  Review of Outage Program of State Generators / Transmission elements for the month of October’18:
Tentative Outage programme for State Generators for the month of October’2018 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 2

# 5

# 6
	14.03.18 to 15.10.18
25.05.18 to 25.09.18

25.10.16 to continue

16.10.15 to continue
	T&G coupling cover water leakage
Shaft seal problem

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 1
# 3
	22.07.18 to 10.10.18
15.10.15 to continue
	Flood water inrush to turbine 
Under R,M & U

	3
	Balimela
	# 1
# 2
# 3

# 5
	05.08.16 to continue
20.11.17 to continue
20.10.18 to 20.12.18

26.08.18 to 12.10.18
	Under R,M & U

Programming for R&M
Gen. Oil leakage & shaft alignment

PMG problem & Annual Maintenance

	4
	Upper Kolab
	# 2
	25.05.17 to 30.09.18
	Upstream leakage and intake gate problem

	5
	Rengali
	# 1
	10.10.18 to 31.10.18
	Oil leakage of TGB housing

	6
	TTPS
	# 5
	29.10.18 to 4.11.18
	Boiler license renewal


OHPC / SLDC may deliberate. 
E.8: Generation Program for the month of October’18.
Generation schedule for the month of October’18 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.09.18
	Reservoir Level as on 01.09.17
	MDDL
	High Flood    Reservoir Level

	
	Oct’18
(1st fortnight)
	Oct’18
(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	80
	80
	623.45
	620.15
	590 ft.
	630 ft.

	HPS-II, Chiplima
	20
	20
	-
	-
	-
	-

	Balimela
	330
	330
	1512.20
	1480.40
	1440 ft.
	1516 ft.

	Rengali
	250
	250
	121.40
	120.94
	109.72mtr 
	123.5 mtr.

	U.Kolab
	240
	240
	856.11
	851.69
	844 mtr 
	858 mtr.

	U. Indravati
	600
	600
	640.01
	635.21
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2748.00
	2735.80
	2685 ft.
	2750 ft.

	TOTAL
	1550
	1550
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

OHPC / SLDC may deliberate & Members may discuss. 
E.9: Anticipated power generation and demand for the month of October’2018.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1200
	1400

	2
	WESCO
	1100
	1250

	3
	NESCO
	850
	1000

	4
	SOUTHCO
	450
	550

	6
	Total Discom
	3600
	4200

	
	System Loss & others
	150
	200

	
	Total Demand
	3750
	4400

	Availability
	
	

	1
	Hydro
	1550  
	1600

	2
	State Thermal
	650
	650

	3
	IPP, small hydro &RE
	300
	450

	4
	ISGS share (including OA& purchase)
	1000
	1400

	5
	CGP support (OA)
	300
	300

	6
	Total availability
	3800
	4400

	7
	Surplus / Deficit
	50
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (126th) PSOC meeting.
PAGE  

