                                                                                                                  
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image1.png]PTC




Agenda

for

126th Power System Operational Co-ordination Meeting

Date: 27.10.2018
Venue: Power Training Center, Chandaka, Bhubaneswar 

Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 126th PSOC Meeting to be held on 27.10.2018 at OPTCL Power Training Center, Chandaka, Bhubaneswar
Item no. 1: Confirmation of the minutes of the 125th PSOC Meeting held on 20.09.2018
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2017/3158 (47) dated 06.10.2018 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   :  Grid Performance for the month of September’2018
C.1:  Over drawal/under injection by ER Entities 
C. 2: Status of projects funded under PSDF scheme 
C.3: By passing arrangement of LILO of 400kV Lines at Angul-OPTCL
C.4:  Establishment of Renewable Energy Management Centre (REMC) in Eastern Region---GRIDCO
C.5: Certification of OPTCL lines as non-ISTS lines carrying ISTS power. 
C.6: Long Outage of transmission elements in Eastern Region

C.7:  Review of Cyber Security Works/Activities 

C.8: Data for preparation Load Generation Balance Report (LGBR) of ER for the year 2019-20 

C.9:  Status of Emergency Restoration system (ERS)of respective Transmission Licencees

C.10: Delay in furnishing information to ERLDC/ERPC regarding of Commissioning of new Transmission Elements/ Generating Units within State

C.11: Status of Implementation of islanding schemes in ER- Islanding scheme at IbTPS- OPGC 

C.12: Implementation of Automatic Demand Management Scheme

C.13: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s
C.14: Update on status of telemetry  

C.15: Mock Black start exercises in Eastern Region 

C.16: PSS tuning of Generators in Eastern region 

C.17: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

C.18: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

C.19: Data for GEOSPATIAL energy portal of Neeti Aayog-CEA

C.20: Providing relevant data by Power Utilities / Stations in National Power Portal.

C.21: Agenda point related to load forecasting by SLDC   

D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Communication issues. 
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.
D.4: DISCOM agenda.
E.1: Commissioning status of New Transmission elements. 

E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
E.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.

E.4: Major Events in the month of September’18
E.5: Important grid incidences during the month of September’18.

E.6: Outage of major transmission Elements during the month September’18. (above 10 hrs).
E.7: Review of Outage Program of State Generators for the month of November’2018
E.8: Generation Program for the month of November’2018.
E.9: Anticipated power generation and demand for the month of November’2018.

F.1:  Date and Venue of the next (127th) PSOC meeting
PART B: GRID PERFORMANCE
Review of Grid Performance for the month of September’18.

A. Frequency:

Hourly frequency variation for the month of September’18.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	July’18
	0.00
	0.05
	6.90
	72.04
	21.02
	49.98

	Aug’18
	0.00
	0.04
	5.30
	72.12
	22.54
	49.97

	Sept’18
	0.00
	0.11
	8.09
	75.23
	16.57
	49.97


Maximum & Minimum frequency during the month of August& Sept’18.
	Month
	Freq (Hz)
	Date
	Time

	Aug’18
	Maximum –50.12
	13.08.18
	13:00 Hrs

	
	Minimum – 49.70
	04.08.18
	19:00 Hrs

	Sept’18
	Maximum –50.10
	25.09.18
	13:00 Hrs

	
	Minimum – 49.63
	24.09.18
	18:15 Hrs



Grid Demand up to the month of September’18
	 Month
	Max. Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	Apr’18
	92.65
	23.04.18
	2400
	3334
	4430
	22.04.18
	21:00
	2348
	01.04.18
	24:00

	May’18
	98.61
	24.05.18
	2735
	3798
	4692
	07.05.18
	21.00
	2113
	14.05.18
	12.00

	June18
	98.45
	01.06.18
	2497
	3455
	4729
	01.06.18
	02:00
	2173
	29.06.18
	14:00

	July’18
	94.27
	29.07.18
	2572
	3457
	4498
	28.07.18
	22:00
	2010
	16.07.18
	13:00

	Aug’18
	114.57
	24.08.18
	3165
	4254
	5428
	23.08.18
	21:00
	3313
	28.08.18
	14:00

	Sept’18
	108.58
	30.09.18
	2857
	3968
	4973
	30.09.18
	21:00
	2881
	21.09.18
	05:00

	Sept’17
	93.49
	16.09.17
	2566
	3567
	4375
	26.09.17
	21:00
	2523
	12.09.17
	17:00


B. Voltage Profile of 220 kV Buses in OPTCL system for the month of: Sept’18

	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Atri
	233.24
	21
	14:15
	214.83
	30
	20:30

	2
	Balasore
	232.55
	21
	6:00
	208.42
	28
	20:00

	3
	Barkote
	231.91
	21
	14:30
	223.20
	29
	18:30

	4
	Bhadrak
	234.57
	21
	6:00
	210.50
	30
	20:00

	5
	Bhanjanagar
	235.15
	21
	14:15
	220.48
	4
	18:45

	6
	Bidanasi
	232.55
	21
	14:15
	212.98
	9
	11:15

	7
	Bolangir
	231.86
	21
	6:00
	212.52
	30
	18:15

	8
	Budhipadar
	227.58
	21
	6:00
	219.50
	29
	20:15

	9
	Chandaka
	234.34
	21
	14:15
	214.77
	28
	18:15

	10
	Cuttack
	232.26
	21
	14:15
	212.17
	28
	18:15

	11
	Duburi(O)
	234.74
	21
	6:00
	220.43
	18
	18:45

	12
	Duburi (N)
	223.89
	21
	6:00
	209.75
	19
	19:45

	13
	Jayanagar
	234.40
	21
	5:00
	228.34
	30
	21:30

	14
	Joda
	230.76
	21
	5:45
	219.39
	3
	19:30

	15
	Katapalli
	232.09
	21
	6:00
	197.56
	30
	18:15

	16
	Lapanga
	231.51
	21
	6:00
	204.72
	30
	18:00

	17
	Laxmipur
	234.80
	21
	14:15
	226.55
	30
	18:15

	18
	Mendhasal
	235.21
	21
	14:15
	215.98
	28
	18:15

	19
	Meramundali
	227.41
	7
	2:15
	219.62
	13
	19:30

	20
	Narendrapur
	233.82
	21
	2:00
	211.82
	28
	18:15

	21
	Nayagarh
	233.70
	21
	14:15
	216.90
	13
	19:15

	22
	Paradeep
	232.49
	20
	13:00
	206.86
	28
	20:15

	23
	Tarkera
	231.86
	21
	14:30
	222.16
	29
	18:30

	24
	Theruvali
	231.45
	21
	14:15
	214.83
	30
	18:30

	25
	Samangara
	232.90
	21
	14:15
	214.65
	28
	18:15


The maximum Voltage of 235.21 kV occurred at Mendhasal 220 kV bus, while Katapali 220 kV bus has experienced the minimum Voltage of 197.56 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Mendhasal, Meramundali  and New Duburi bus during the month of Sept’2018 are indicated. 
[image: image2.png]VOLTAGE PROFILE OF NARENDRAPUR 220 kV Bus

For September 2018

Time In Hrs





[image: image3.emf]210

215

220

225

230

235

240

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OGF JAYANAGAR 220 kV BUS

For SEPTEMBER2018


[image: image4.emf]360

365

370

375

380

385

390

395

400

405

410

415

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MENDHASAL 400 kV BUS

FOR SEPTEMBER 2018


[image: image5.emf]390

395

400

405

410

415

420

425

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MERAMUNDALI 400 kV BUS

FOR SEPTEMBER2018 


[image: image6.emf]390

392

394

396

398

400

402

404

406

408

410

412

414

416

418

420

422

424

426

428

430

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NEW DUBURI 400 kV BUS

FOR SEPTEMBER2018 


Members may discuss.
C. Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of Sept-2018 [image: image7.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  SEPTEMBER'2018

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

38.20 5 08:30 3.80 4 13:00

44.12 19 12:00 3.76 4 13:00

88.20 29 20:00 5.72 3 11:15

98.64 3 11:30 29.00 16 17:45

100.24 3 01:30 29.32 16 16:45

1x100 38.40 12 22:30 6.32 14 16:00

1x160 71.40 21 19:15 3.48 29 19:15

1x160 71.56 21 19:15 3.60 29 19:15

1x160 74.16 15 19:00 15.16 16 17:00

1x160 65.52 15 19:00 13.16 16 17:00

1x160 34.68 27 18:00 5.92 1 07:30

1x100 24.28 27 18:00 3.96 1 07:30

1x100 24.24 27 18:00 4.16 1 07:30

130.28 28 19:30 7.48 20 21:15

136.96 25 18:45 7.44 17 19:30

94.52 30 20:45 6.28 5 08:30

110.88 8 19:30 35.80 7 03:45

1x100 50.56 30 19:00 12.60 21 14:15

1x160 87.20 30 19:00 21.64 21 14:15

1x100 54.28 30 19:00 13.24 21 14:15

1x160 83.88 30 19:00 20.48 21 14:15

CUTTACK 1x160

93.60

24 12:00 8.68 11 17:15

1x160 57.32 10 18:15 7.88 3 19:00

1x100 36.08 10 18:15 4.64 3 19:00

1x100 34.44 10 18:15 4.36 3 19:00

1x160 58.28 13 18:30 11.04 11 12:45

1x160 58.52 13 18:30 11.08 11 12:45

56.24 7 07:30 18.96 20 12:15

56.68 9 13:00 8.00 7 00:15

56.52 9 13:00 18.76 20 12:00

1x100 38.04 30 20:00 4.72 10 03:30

1x100 38.08 30 20:00 4.64 10 03:30

1x160 57.40 30 20:00 4.24 9 14:15

62.40 9 09:45 9.24 30 17:30

62.12 9 19:45 17.20 17 14:45

34.44 9 11:15 4.52 26 03:00

34.12 9 11:15 4.52 26 03:00

32.80 9 11:30 3.88 26 16:15

26.40 11 09:45 7.20 21 12:00

42.60 11 10:15 4.20 21 12:00

108.28 10 20:00 35.44 21 02:00

108.68 10 20:15 35.80 21 02:00

1x100 62.20 10 20:15 20.00 21 02:00

1x160 123.80 12 21:15 19.48 6 05:00

1x100 76.04 12 21:15 11.84 6 05:00

1x50

4x100  53.84 7 19:45 3.52 1 21:45

55.60 7 19:45 4.20 1 21:45

54.20 7 19:45 3.66 1 21:45

52.08 29 20:30 4.08 1 21:45

2x100 84.32 25 20:45 19.16 16 12:45

79.44 25 20:45 14.92 14 19:00

1x160  51.22 21 03:45 0.00 22 01:30

1x160 51.22 21 03:45 0.00 22 01:30

2x100 61.60 11 21:45 5.68 21 01:15

79.76 29 12:15 5.68 21 01:15

2x160

2x160

2x160 LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 

BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & 

Katapali area load.}

2x100

2x160



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

BIDANASI 220/132 KV

{Bidanasi, Khurda }

3x100 



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }

JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]



"*" - Alternate P/S from 

Kuchei.



DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, 

Jajpur Road, Kalarangi, Jajpur Town}

Mendhasal { Part area load of Khurda S/S}

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100



SAMANGARA                                          

{ Puri, Nimapara & Konark}

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, 

Digapahandi, Mohana.}

THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), 

MCL, Sundergarh,Brajarajnagar, 

Rajgangpur}

2x160 

Rayagada & Paralakhemundi 

can be fed from Machhkund 

system.

Supported by Burla & 

Chipilima power.

PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 



BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

Drawal details

Maximum Minimum



BHADRAK 220/132 KV

{Bhadrak area load, Bhadrak(T),Soro,  

FACOR (I), Dhamra Port}

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}

3x160 

ATRI                                                     

{Banki, Khurda, Chandpur & Argul}


D. DISCOM Drawal up to the month of September’18
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	Apr’18
	745.479
	734.495
	770.403
	19.655
	750.748
	16.253

	
	May’18
	770.329
	819.87
	850.674
	20.004
	830.67
	10.8

	
	June’18
	745.480
	836.254
	848.445
	14.721
	833.724
	-2.53

	
	July’18
	770.329
	805.001
	823.135
	16.707
	806.428
	1.427

	
	Aug’18
	770.329
	825.849
	833.67
	17.428
	816.242
	-9.607

	
	Sept’18
	745.480
	741.752
	784.029
	5.113
	778.916
	37.164

	WESCO
	Apr’18
	585.205
	636.576
	689.137
	57.318
	631.819
	-4.757

	
	May’18
	604.712
	636.024
	1042.2
	362.004
	680.194
	44.17

	
	June’18
	585.205
	640.766
	995.128
	359.629
	635.499
	-5.267

	
	July’18
	604.712
	612.348
	767.095
	160.722
	606.373
	-5.975

	
	Aug’18
	604.712
	586.549
	1,152.89
	561.626
	591.265
	4.716

	
	Sept’18
	585.205
	606.175
	976.932
	365.889
	611.043
	4.868

	NESCO
	Apr’18
	504.658
	418.945
	528.936
	105.079
	423.857
	4.912

	
	May’18
	521.4799
	480.187
	576.819
	102.344
	474.475
	-5.712

	
	June’18
	504.658
	488.448
	598.361
	113.554
	484.807
	-3.641

	
	July’18
	521.4799
	481.593
	581.864
	95.907
	485.957
	4.364

	
	Aug’18
	521.4799
	494.386
	644.557
	138.545
	506.012
	11.626

	
	Sept’18
	504.658
	467.35
	575.488
	99.903
	475.585
	8.235

	SOUTHCO
	Apr’18
	300.822
	298.76
	298.778
	0
	298.778
	0.018

	
	May’18
	310.849
	321.453
	323.114
	0
	323.114
	1.661

	
	June’18
	300.822
	316.746
	315.514
	0.57
	314.944
	-1.802

	
	July’18
	310.849
	316.309
	313.076
	0.574
	312.502
	-3.807

	
	Aug’18
	310.849
	322.184
	322.519
	0
	322.519
	0.235

	
	Sept’18
	300.822
	302.037
	309.512
	0
	309.512
	7.475


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
     Members may please discuss.

E. Energy Generation / Import up to the month of September’18
Figures in MU  
	Month
	Thermal

(TTPS+IbTPS)
	OHPC 
& MKD
	CGP Support
	IPP Inj.
	RE
	ISGS
	Total

	April’18
	535.100
	421.700
	362.530
	198.950
	9.690
	872.260
	2400.240

	May’18
	567.940
	573.520
	313.169
	199.230
	14.390
	1066.640
	2734.893

	June’18
	485.813
	481.601
	219.983
	203.230
	11.897
	1084.870
	2487.390

	July’18
	440.179
	421.582
	213.953
	193.928
	10.102
	1292.141
	2571.886

	Aug’18
	473.390
	689.310
	163.300
	202.940
	13.680
	1621.990
	3164.600

	Sept’18
	454.183
	1037.515
	203.086
	136.688
	13.196
	1012.434
	2857.102

	Total
	2956.605
	3625.228
	1476.021
	1134.966
	72.955
	6950.335
	16216.111


F.  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of Sept’18 are as detailed:
	Month
	Total Generation
	Odisha Drawl
	AP Drawl

	
	MU
	Avg (MW)
	MU
	Avg (MW)
	MU
	Avg (MW)

	Apr’18
	37.162
	51.610
	18.613
	25.851
	16.943
	25.532

	May’18
	48.888
	65.700
	22.424
	30.140
	24.492
	32.919

	June’18
	43.185
	59.980
	19.692
	27.350
	21.635
	30.048

	July’18
	45.146
	60.680
	20.894
	28.083
	22.148
	29.769

	Aug’18
	51.319
	68.977
	23.507
	31.595
	25.708
	34.554

	Sept’18
	45.449
	63.123
	20.039
	27.032
	23.324
	32.394

	Total
	271.149
	
	125.169
	
	134.250
	


Drawl of State share power from Machhakund is decreasing for the past 5 months. Southco may add more feeders to Podagada S/s. 
SLDC/ SOUTHCO may deliberate.
G. Under Frequency Relay operation in OPTCL System during the month of Sept’18.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of Sept’18.
H. Status of Open Access applications up to the month of Sept’2018
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’18
	26
	79
	0
	31
	136
	26
	76
	0
	31
	133
	3

	2
	May’18
	59
	90
	0
	26
	175
	59
	89
	0
	26
	174
	1

	3
	June’18
	14
	57
	0
	30
	101
	14
	57
	0
	30
	101
	0

	4
	July’18
	18
	145
	0
	26
	189
	18
	145
	0
	26
	189
	0

	5
	Aug’18
	26
	90
	0
	37
	153
	26
	90
	0
	37
	153
	0

	6
	Sept’18
	25
	97
	0
	32
	154
	25
	97
	0
	32
	154
	0

	
	Total
	168
	558
	0
	182
	908
	168
	554
	0
	182
	904
	4


PART C – Issues discussed in the 150th  OCC meeting of ERPC held on 11.10.2018
C1: ER Grid performance during September, 2018

The average consumption of Eastern Region for September-2018 was 441.4 Mu. Eastern Region achieved maximum energy consumption of 478 Mu on 29thSep -2018. Total Export schedule of Eastern region for September -2018 was 1205 Mu, whereas actual export was 809Mu. The under export of Eastern Region is mainly due to over drawl of DVC, West Bengal and Odisha 
Over drawal/under injection by ER Entities 

Over drawl figure of West Bengal and Odisha from 01-10-2018 to 07-10-2018 are shown below: 

	 
	DVC
	Odisha
	West Bengal

	
	OD (MU)
	Max OD (MW)
	OD (MU)
	Max OD (MW)
	OD (MU)
	Max OD (MW)

	01-10-2018
	3.66
	435.408
	8.35
	794.12
	1.59
	564.38

	02-10-2018
	7.05
	602.08
	7.16
	921.24
	3.70
	528.83

	03-10-2018
	5.66
	568.76
	9.30
	832.40
	3.38
	459.42

	04-10-2018
	6.20
	562.21
	8.70
	926.09
	4.66
	622.79

	05-10-2018
	10.06
	622.93
	10.26
	791.06
	0.13
	440.95

	06-10-2018
	7.98
	784.57
	2.87
	614.76
	0.83
	373.14

	07-10-2018
	1.29
	271.92
	3.60
	675.19
	1.88
	693.69


 It may be seen that for the month of the October till date,  

· West Bengal over drawl was in the range of 1 to 5 MU on daily basis while maximum over drawl touched 4.66 mu on 04-10-18 and 693 mw maximum deviation on 07-10-18. 
· Odisha over drawl was in the range of 3 to 11mu while maximum over drawl touched 10.26mu on 05-10-18 and 926 mw maximum deviation on 04-10-18. 
· DVC over drawl was in the range of 1 to 10mu while maximum over drawl touched 10.06 mu on 05-10-18 and 785 mw maximum deviation on 06-10-18. 

In 149th OCC persistent overdraw matter of West Bengal, Odisha and DVC was discussed, where in all parties were agreed to take corrective measures to avoid such persistent over-drawl. During the meeting, DVC expressed during October month their over drawl shall reduce substantially due to change on STOA sell profile and expected improvement in coal supply. Odisha also informed that due to increase in hydro generation, they would manage their drawl as per schedule during October month and west Bengal also assured to improved their internal generation and purchase profile in coming month to avoid such huge over drawl. However, for the month of September and till date October-2018 as shown above, appreciable improvement to avoid over drawal of West Bengal, DVC and Odisha was not observed. 

West Bengal, DVC and Odisha may please deliberate the reason of continuous overdrawal and future action plan to mitigate such contingency situation.  

DVC may please furnish action plan taken for improvement of coal supply issues and schedule date for restoration of plants out on coal shortage.  

Beneficiaries are also advised to maximize their internal generation and increase their power purchase quantum in STOA/Power Exchange or from any other source to maintain their drawl as per schedule.  

In case of repetitive non-compliance of ERLDC instruction to curtail over drawal during real time operation continues in future, ERLDC will have no other option but to approach appropriate commission with respect to erring entities. 

SLDC/ GRIDCO may deliberate
C.2: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
149th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	30.11.18
	162.5 Cr.


	38.09Cr. Requisition for 11.00 Cr placed.
	90% equipment installed and commissioned. Stn Tfr and some measuring instruments are under tendering process.



	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.22 Cr
	Request for 10% grant already submitted. Agreement  signed
	Tender floated

	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov18
Chiplima

Dec 2018
	22.35 Cr.
	
	Placed work order for Balimele

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 


	28-08-17
	
	31.94 Cr
Ested. Cost. Approved amount 30.26 Cr. Grant amount 27.23 Cr.
	
	Appraisal committee recommends for project cost of 30.23 Cr and 27.23 Cr grant by monitoring committee. Agreement signed and sent to NLDC for signature. Tender floated.

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost. 2.93 Cr recommended by Appraisal committee.
	
	Recommendation by Appraisal committee already forwarded to CERC for concurrence.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	20.02.2018  Date of submission 
	
	41.1 Cr

Estt cost
	
	Compliance to TSEG observation submitted. Audit observation has been sent to NLDC indicating justification of requirement


   CGM (O&M) / OHPC/ SLDC may please update the status.
C.3: By passing arrangement of LILO of 400kV Lines at Angul-OPTCL

LILO of Meramundali-Bolangir/Jeypore 400 kV S/C line and LILO of one Ckt of Talcher-Meramundali 400 kV D/C line has been done at Angul 765/400kV Sub-station.

In 18th Standing Committee it was decided that Power grid would establish a switching arrangement at Angul substation such that, the above 400 kV LILO may be operated either by – passing Angul sub-station or terminating at Angul sub-station as and when required depending upon the power flow condition.

In 19th Standing Committee, it was inferred that LILOs of the above two lines needs to be by -passed to maintain the fault level at Meramundali S/S under normal operating conditions.

The necessary arrangement to be done by Powergrid for by-pass arrangement is under implementation and will be commissioned shortly.

The fault level at Meramundali will further increase after the commissioning of Meramundali​-Mendhasal 2ndckt of D/C line.

Odisha wants for normally closed arrangement at Angul so as to relieve the fault level problem at Meramundali.  Odisha further agrees that as and when the situation demands the isolator may be put in open condition.

The following standard operating procedure may be approved by the OCC for implementation of by-pass arrangement.
• The isolator will be normally closed so as to ensure the fault level at Meramundali stays within the permissible limits of 40 kA.

• Under severe contingencies like line outage or generator outage ERLDC In consultation with SLDC will open the isolator i.e.to restore the LILO of the above two lines.

Members may discuss. 

C.4:  Establishment of Renewable Energy Management Centre (REMC) in Eastern Region---GRIDCO

Implementation of the state-of-the-art Renewable Energy forecasting & Monitormg systems is now a global best practice. For the same, it is proposed By Ministry of Power, Govt of India to establish Renewable Energy Management Centres (REMC) to address the intermittency, variability and uncertainty issues of Renewable power integration to the grid. Renewable Energy Management Centre (REMC) is part of the 'Green Energy Corridor Scheme dealt by MNRE, Gol. 
In order to facilitate integration of the targeted 175 GW of Renewable capacity by 2022, a comprehensive transmission plan is chalked out comprising of intra state and inter-state transmission system strengthening infrastructure as well as Control infrastructure i.e. establishment of REMCs at SLDC/RLDC/NLDC level.

The REMC scheme will help the grid operator to effectively manage power system operations with economy, reliability & security with an objective to forecast of RE generation on different levels such as State/ region, aggregated pooling station wise etc. based on information from Forecast Service Provider (FSP) as well as Weather Service Prov1der (WSP), Renewable Generation Scheduling, real time tracking of generation of RE sources, integration with REMC SCADA & its Visualization & close coordination with respective LDC for RE generation & integration with existing SCADA. Owner of REMC will be the existing SLDCs, RLDCs & NLDC.

At present, the REMC scheme is proposed for the Renewable rich States / regions i.e. Tamil Nadu, Andhra Pradesh & Karnataka in Southern Region. Gujrat, Madhya Pradesh & Maharastra in Western Region and Rajasthan in Northern Region co-located with SRLDC, WRLDC, NRLDC & NLDC. No REMC has been decided yet for Eastern Region & North Eastern Region. The Scheme is proposed to be financed from 100 % Gross Budgetary Support. No financial component / support is involved from the State Govts./State Discoms. 

PGCIL, the CTU will be implementing the scheme and will hand over the REMC to respective states / POSOCO upon commissioning. From the tentative State wise break up of RE generation by 2022, it can be seen that in Eastern Region also, there will be RE capacity addition of around 12, 500 MW by 2022 in Bihar, Jharkhand, Odisha, West Bengal & Sikkim.

To address the issues of RE power integration, commissioning of REMC is a necessary step. GRIDCO is proposing REMC under the 'Green Energy Corridor scheme' for Eastern Region States (to be established in ER state LDCs & at ERLDC), which need to be placed before MNRE, Govt. of India through ERPC In a relevant forum, GRIDCO has already appealed to MNRE for establishment of REMC in Odisha and MNRE has also confirmed the concern of Odisha. A combined proposal is to be submitted from ERPC to MNRE for the ER states.

GRIDCO may deliderate/ Members may discuss. 

C.5: Certification of OPTCL lines as non-ISTS lines carrying ISTS power.

OPTCL vide no. RT&C-NON-ISTS/2017/281 dated 21.08.2018 had sought the Certification of non-ISTS line carrying ISTS power as per the direction of CERC in ROP dated 08.08.2018 under Petition No. 25/TT/2018. 
Accordingly, in line with 34th TCC decision, ERPC Secretariat and ERLDC conducted the load flow study using Web-Net software for all the quarters of 2014-15, 2015-16, 2016-17, 2017-18 & 2018-19 (upto Q2). 
Also, in 129th OCC held on 17.01.2017 it was decided that STU lines carrying ISTS power greater than 50% of the total power as per the Web-Net software of the validated data for each quarter will be considered as non-ISTS line carrying ISTS power. The same was also approved by 35th TCC/ERPC.

Accordingly, as per the study result it is clear that the following OPTCL lines are mostly being utilized more than 50% for carrying ISTS power, hence these elements may be considered as non-ISTS line carrying ISTS power for the tariff period 2014-19. 
	Sl.No
	Name of Line


	Remarks

	1
	400 kV Indravati-Indravati S/C
	

	2
	400 kV Rengali-Keonjhar S/C
	

	3
	400 kV Keonjhar-Baripada
	

	4
	400 kV Baripada-Kharagpur S/C
	Natural ISTS

	5
	220 kV Jeypore-Jaynagar D/C
	

	6
	220 kV Rengali-Rengali D/C
	

	7
	220 kV Balimela-U.Sileru S/C
	Natural ISTS

	8
	220 Joda-Jindal S/C
	

	9
	132 kV Joda-Kenduposi S/C
	Natural ISTS


Members may discuss.

C.6: Long Outage of transmission elements in Eastern Region

e) Breakers at 400/220kV Indravati (OHPC) S/s  

In 141st OCC, it was explained that 3x105 MVA 400/220kV ICT-I tie breaker, 220kV Bus coupler and transfer bus breakers are not in service at 400/220kV Indravati (OHPC) S/s.  

In 142nd OCC, OHPC submitted the action plan as follows: 

1. 220kV Bus Coupler: CB and CT needed to be replaced. They would restore the Bus coupler by August 2018.  

2. 220kV Bus tie: CB and CT needed to be replaced. They would restore the Bus Tie by November 2018. 

3. 400kV Tie-1 Breaker: CB and CT needed to be replaced. They would restore the 400kV  Tie-I by January 2019.  
In 149thOCC, OHPC informed that 220kV Bus Coupler had been installed and the same would be put in service inSeptember2018.
In the 124th PSOC meeting OHPC stated that 220 kV Bus coupler CB is in operational condition. Spare CT is not available for restoration of Bus coupler. Tendering for 220 kV Bus tie and 400 kV Tie –I are expected to be done by January’2019. It was suggested that OHPC may borrow CTs from OPTCL for restoration of 220 kV Bus coupler. 

In the 125th PSOC meeting OHPC stated that the CB is in service. OHPC shall coordinate with O&M for CTs.

OHPC may deliberate the status

C.7:  Review of Cyber Security Works/Activities 

CEA vide letter informed that Secretary (Power) is going to review the cyber security related works /activities being carried out in Power Sector. In this regard, it is requested to provide the State wise status on following action points pertaining to cyber security at the earliest: 

 
1. Appointment of organization-wise Chief Information Security Officers and its status 

2. Identification of organization-wise Critical Infrastructure and its status 

3. Preparation of organization-wise Crisis Management Plan and its status 

4. Status of Cyber Security Mock Drill activity in coordination with CERT-In 

5. Status of Training / Workshops on Cyber Security organized / participated by power sector entities

6. Status of action taken on CERT-In / NCIIPC advisories 

In 148thOCC, all the constituents were advised to send the latest status to mserpc-power@nic.in within a week. The same has been received from WBSETCL only. 

In the 125th PSOC meeting it was deliberated that IT may request CEA to make a presentation in the PSOC meeting. 

IT may deliberate the status.

C.8: Data for preparation Load Generation Balance Report (LGBR) of ER for the year 2019-20 

As per the IEGC, RPC Secretariat is responsible for finalization of the Annual Load Generation Balance Report (LGBR) for Peak as well as Off-peak scenarios and the annual outage plan for the respective region  

To facilitate the preparation of LGBR of Eastern Region by ERPC Secretariat within the schedule period, the following data/information for the year 2019-20 in respect of the constituents/utilities of Eastern Region is urgently required: 

i) The unit wise and station wise monthly energy generation proposed from existing units during 2019-20 (thermal/hydro/RES).

ii) Annual maintenance programme for each of the generating units (thermal and hydro both).

iii)  Generating units under R&M / long outage indicating date of outage and reasons of outage and expected date of return (thermal and hydro both). 

iv) Partial and forced outage figures (in %) of generating units for the last 3 years.                                  

v) Month wise peak demand (MW) – restricted and unrestricted peak demand. i) Month wise off-peak demand (MW).  

vi) Month wise energy requirement (in MU). 

vii) Month wise & source wise power (both MU & MW) purchase and/or sale plan. ix) Schedule of commissioning of new generating units during 2019-20 and unit-wise monthly generation programme (in MU).

viii) Allocation of power from new generating units. 

ix) Month wise and annual planned outage of transmission system (Transmission lines 220kV and above / ICTs / Reactors/ other elements. 

Information may please also be submitted in the form of soft copy through email (mail ID: mserpcpower@nic.in / erpcjha@yahoo.co.in). 

In the 125th PSOC meeting all the Utilities were requested to furnish the required information to SLDC. SLDC may write a letter to all the utilities in this regard and to convene a meeting.

All Generators/GRIDCO/O&M/SLDC may furnish the above data at the earliest
C.9:  Status of Emergency Restoration system (ERS)of respective Transmission Licencees

CEA vide mail dated 28-09-2018 has requested to provide Status of Emergency Restoration system (ERS) of respective Transmission Licensees in respective Regions as per the format given below:
	State-wise Emergency Restoration system

	Transmission Licensee


	Requirement of Total

no of ERS in State


	Number of ERS

available in state


	No of ERS to

Be Procured


	Remark if any

	
	
	
	
	


Transmission Licensees may submit the details as per the format.
O&M may take necessary action

C.10: Delay in furnishing information to ERLDC/ERPC regarding of Commissioning of new Transmission Elements/ Generating Units within State

The above matter was deliberated in various OCC meetings and data submission format was also circulated. All states and transmission licensees agreed to submit the list of transmissions elements synchronized for the first time during last month within 7thday of the current month to ERLDC through mail. 

For the Month of September-2018, states and transmission licensees did not submit their List of Transmission element and generators synchronised in the previous month and List of Transmission element and generators expected to be synchronised during next month.

Members may please note. 

C.11: Status of Implementation of islanding schemes in ER- Islanding scheme at IbTPS- OPGC 

2. Islanding scheme at IbTPS- OPGC 

The islanding scheme was discussed in 68th PCC Meeting held on 18-06-2018.  PCC opined that the draft scheme submitted by Odisha was three years old and the draft scheme is needed to be reviewed with existing network configuration.   

PCC decided to discuss the islanding scheme in next PCC Meeting and advised OPTCL to submit all the relevant details to ERPC and ERLDC.  

In 69th PCC Meeting, it was decided that ERLDC and ERPC would study and finalize the islanding scheme in next PCC Meeting.
In the 124th PSOC meeting SLDC stated that PCC sought data from SLDC to finalize the quantum of load i.e max, min and avg to be considered for islanding scheme. It was decided to convene a meeting with IBTPS, SLDC and O&M to discuss and finalize.

In the 125th PSOC meeting it was decided that O&M slall convene a meeting with IBTPS, SLDC to finalize the issue.

     O&M / IbTPS may discuss
C.12: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

***************************************************************************

The latest status along with proposed logic as follows:
[image: image8.emf]
[image: image9.emf]
In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 123rd PSOc meeting SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval

In the 124th PSOC meeting SLDC stated that the revised estimate has been approved in the BoD.

In the 125th PSOC meeting SLDC stated that CERC approval is awaited for tendering.

SLDC may deliberate the status

C.13: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 125th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by Dec’18. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by Dec’18.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Keonjhar S/S (220/33 kV) by September’18.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	December 2018 


CGM (Cont) / CGM (O&M) may update
C.14: Update on status of telemetry  

CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed  NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action.

In the 149th OCC, ERLDC stated that status of Breaker & isolator of NALCO & JITPL are not available.

In the 125th PSOC meeting NALCO stated that their RTU will be restored within 2-3 months. Telecom stated that Narsingpur data will be received after laying of optical fibre.

Telecom & NALCO may deliberate.  
C.15: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2018-19 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2018
	Done on 28.06.2018
	Last week of January 2019
	

	3
	Rengali
	2nd week of June 2018
	Done on 18.08.2018
	Last week of November 2018
	

	4
	U. Indravati
	3rd week of June 2018
	October’18
	2nd week of February 2019
	

	6
	Balimela
	3rd week of October  2018
	October’18
	1st week of March 2019
	

	9
	Burla
	Last week of June 2018
	Done on 07.06.2018
	Last week of February 2019
	


Mock black start exercise for Upper Kolab was been done again at the time of workshop conducted by ERPC at Upper Kolab on dated 28th Sept’18 in presence of Member Secretary, ERPC ERPC and members from ERLDC.

SLDC / OHPC may deliberate

C.16: PSS tuning of Generators in Eastern region 

Several Cases of Low frequency Oscillations have been observed in the Eastern Region. In view of this, it is desirable to have the PSS tuning of Generators in Eastern region to improve the system damping. It is mandatory as per existing CERC and CEA regulation to tune 100 MW and above generating units.  

In view of that, Generating station may kindly update the following details to ERLDC/ERPC: 

 Name of Generating Power Plant:  

	Unit

No
	Type of Excitation  System  (Static/ Brushless /Other)
	IEEE Model (IEEET1/ ESST1A/ Other)
	Name of Excitation System Vendor (ABB/GE /Hitachi/ other)
	Whether PSS is Tuned of not (If tuned Date of tuning)
	Whether Report of tuning Submitted or not

	
	
	
	
	
	


In line with regulations, all generating power plant to take up the PSS tuning activities at earliest with their vendors and submit the report after PSS tuning for verification. The response data with PSS tuning also to be shared with ERLDC/ERPC for validation in either excel or .csv format. This will be monitored in OCC on regular basis.  

OCC advised all the generators to submit the relevant data as per the format to ERLDC and ERPC. 

In the 125th PSOC meeting all Generators are requested to submit the details and inform the tentative plan for PSS Tuning to SLDC and ERPC.

Generators may submit the details and inform the tentative plan for PSS Tuning.

C.17: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

The activity of the preparation of Crisis Management Plan for countering the cyber-attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA. 

In 142nd OCC, ERLDC informed that, in line with Enquiry Committee Recommendation, cyber security audit is being conducted on regular basis for SCADA system installed at ERLDC and SLDC as well but cyber security audit for telecom infrastructure installed in Eastern Region is not being carried out.  

OCC advised all the constituents to conduct the cyber security audit on telecom infrastructure installed in Eastern Region. It is further advised that compliance / mitigation of the points observed during the audit should also be completed for improvement of the telecom infrastructure in ER. 

In 37th TCC meeting, it was decided that a workshop would be conducted by CEA at ERPC for further benefit of ER Constituents.  

In 144th OCC, ERLDC informed that they have already conducted a workshop with the help of NPTI, Durgapur on 21st March 2018. 

A workshop on cyber security was conducted by CEA at ERPC, Kolkata on 09-05-2018.  

As suggested by CEA, a format would be circulated among ER constituents for furnishing the information of their respective systems for discussion in OCC Meeting. The format is enclosed at Annexure-E2. 

OCC advised all the constituents to submit the information to ERPC as per Annexure-E2.  

In the 123rd PSOC meeting IT stated that the Audit report has already been received. After depositing the required charges, audit for FY 2018-19 will be started. It was suggested that IT shall furnish the information as sought by ERPC in the required format.

In the 124th PSOC meeting IT stated that the Audit team has arrived on 27.08.18 to impart training.  

In the 125th PSOC meeting CGM (IT) stated that training has already been imparted. The required information will be submitted to ERPC.

IT may deliberate the status

C.18: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.  

· As per the information received from the constituents the following generators certified with IS 18001:  

· All NTPC stations in Eastern Region  

· Teesta, NHPC 

· All OHPC generating units  

· All CESC generating units  

· All units of WBPDCL 

· DGPC units 

In the 117th PSOC meeting CGM (O&M) stated that draft project report for Mendhasal S/S has been submitted to BIS. The report will be approved in the meeting to be conducted by them.

In the 122nd PSOC meeting CGM (O&M) stated that Audit team is expected soon.

In the 123rd PSOC meeting CGM (O&M) stated that the report is yet to be received.

In the 124th PSOC meeting O&M stated that program for imparting training has been scheduled   during 1st week of September’2018. Audit will be done after completion of training.
In the 125th PSOC meeting Sr.G.M (O&M) stated that training has been completed. Mendhasal S/S audit in under progress. After compliance of the observations, certificate may be issued. 
O&M may update the status

C.19: Data for GEOSPATIAL energy portal of Neeti Aayog-CEA
NITI Aayog is developing a user friendly GIS based Energy Map of India, which would provide true locations of all energy resources in India including power plants, coal and oil reserves, transmission lines etc.  

CEA sought the information of name, voltage level, capacity, longitude and latitude of 33kV and 66 kV substations and lines.  

The information may be shared with CEA vide email: cedpd-cea@gov.in.  

All primary S/Ss data in respect of CESU, NESCO, WESCO & SOUTHCO has been received.

In the 125th PSOC meeting all the Discoms were requested to share the data with CEA vide email: cedpd-cea@gov.in.

DISCOMs may deliberate

C.20: Providing relevant data by Power Utilities / Stations in National Power Portal.

CEA vide letter dated 26th June 2018 informed that National Power Portal (NPP) (URL: npp.gov.in), has been launched by Hon'ble Minister of Power on 14th November, 2017. NPP is modified and more user-friendly data portal than the existing Information Management System (IMS) in CEA. Reports prepared from NPP are of vital importance for Power Sector data analytics in order to frame policies, regulations, future road-map for Power Sector etc. at Central as well as at State level. Accordingly, all power utilities have been issued user ID and password, either organisation-wise or station-wise, based on their request , for providing their data on NPP.

NPP has replaced IMS since 1st June, 2018. A Circular (which is available in Circular Section of CEA Website, i.e. cea.nic.in) has been issued by CEA to all power utilities/stations on 14.06.2018 for providing their data online in NPP only. 

In this regard, letters/mails have been issued to Utilities to provide their data online through NPP. 

A letter dated 20.06.2018 was also issued to all SLDC, requesting them to direct the power utilities I stations under their purview for providing data on NPP. 

Any issue/problem faced by utilities may kindly be communicated to itcea@nic.in, npp.support@gov.in, ceopm-cea@gov.in and if required, IT Division, CEA may be contacted on 011-26732368 or 011-26732303

CEA requested to pursue the power utilities / stations under their purview for providing data on NPP. 
Further, a workshop/presentation may be arranged if required in each region in which IT Division, CEA will provide a brief demonstration regarding data entering process and report generation into NPP.
Members may comply.

C.21: Load forecasting by SLDC   
For better grid management and shutdown planning, RLDCs needs to do short term load forecasting. Accuracy and effectiveness of load forecasting depend on input data. As per current practice, day ahead load forecasting is being done at ERLDC by analyzing trend previous days demand. However, for further tuning and better accuracy of load forecasting result, demand estimation from SLDCs are to be done at their end and same need to be shared with ERLDC for estimation of Eastern Region demand. 

In the 123rd PSOC meeting SLDC stated that the State demand forecasting is being done as per the drawal forecast by all the DISCOMs. The DISCOMs were requested to share their forecast methodology for intimation to ERLDC.
In the 124th PSOC meeting SLDC requested all the DISCOMs to forward their load forecast methodology by 1st week of September’2018.

In the 125th PSOC meeting Discoms stated that they are preparing their day ahead drawl forecast basing on past three days drawal with some adjustments manually. Director (Commercial), GRIDCO stated that GRIDCO will make a presentation on load forecast methodology in the next PSOC meeting. WESCO has forwarded the methodology adopted for load forecasting of WESCO. 

GRIDCO / DISCOMs may deliberate.
C.22: Agenda of items to be discussed in the 72nd PCC meeting of ERPC

1. Disturbance at Bolangir (N) S/S dated 17.09.2018

2. Non operation of Auto-Recloser in the following S/S end during tripping in the month of September

a. 220 kV Joda-RC Pur

b. 220 kV Pandiabili-Samangara-II

c. 400 kV Meramundali-JSPL-I

d. 220 kV Baripada (PG)-Balasore-I 

O&M may deliberate
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of August’18:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	37.164
	5.010

	2
	WESCO
	0
	4.868
	0.803

	3
	NESCO
	0
	8.235
	1.762

	4
	SOUTHCO
	0
	7.475
	2.474

	
	Total
	0
	57.742
	


It is noticed that all the DISCOMs were over drawn during the month. CESU has deviated 5.01% followed by SOUTHCO 2.474% from the scheduled energy while NESCO 1nd WESCO have deviated marginally. DISCOMs may forecast their drawal in realistic approach to minimise deviation.

SLDC/ Discoms may please deliberate.
D.2: Communication issues 
The status of data communication from CGPs as deliberated in the 124rd PSOC meeting meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	2
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. 
In the 123rd PSOC meeting it was deliberated that RT&C have sought some information from Telecom wing which will be intimated. NALCO stated that due to problem in their internal communication system, data communication to SLDC is being interrupted.
In the 124th PSOC meeting Telecom stated that communication system for Paradeep area industries will be completed by September’2018. Telecom was advised to give a reply to the information sought by RT&C. 

In the 125th PSOC meeting Telecom stated that the information sought by RT&C will be forwarded soon.

Telecom/GCC / RT&C may deliberate 
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 119th PSOC meeting IT stated that Parameters of 16 Nos meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
In the 120th PSOC meeting IT stated that M/s Secure Meter is not responding to them. It was decided that O&M shall convene a meeting with M/s Secure meters to resolve the issue.  
In the 121st PSOC meeting it was decided that SLDC shall write CPC and OPTCL to convene a meeting with TCS and Secure meters to discuss the issue. 
In the 123rd PSOC meeting IT stated that out of 840 Nos interface meters connected with AMI, 750 Nos are reporting at present. The newly replaced meters are not reporting. 2 Nos. of meters has sent to M/s SECURE meters for study.

In the 124th PSOC meeting O&M stated that SLDC may intimate the list of defective energy meters to O&M on monthly basis for necessary action. IT may ask TCS to co-ordinate with Secure meters and develop a driver data extraction  
In the 125th PSOC meeting IT stated that they have already handed over the Meters to M/S TCS.

IT/ SLDC may deliberate
D.4: Furnishing of energy meter data for Cross Subsidy Charge billing- SLDC agenda

It is noticed that CESU is not furnishing the actual energy drawal meter data to SLDC in respect of customers importing power through inter / intra state open access transactions, ever after repeated reminder from SLDC. In absence of the said data the Cross Subsidy Charge billing could not be done by SLDC in time. CESU may instruct their field engineers to furnish the data by end of 1st week of succeeding month.

SLDC / CESU may deliberate

D.5: DISCOM Agenda

CESU 

1. To connect 132/33KV Argul Grid S/s to 132/33KV Ranasinghpur GRID s/s in order to get stand by supply from Atri Grid S/s in case of power supply failure from Chandaka Grid or any fault in 132/33KV Chandaka – Ranasinghpur feeder, which will cater power supply to Kalinga Nagar, AIIMS, Nayapalli, Baramunda, old town, Khanadagiri area and Bhimtangi area etc.

2. Earlier 15minute actual drawl data was provided by SLDC, which was very much vital for giving the day ahead schedule forecast. But after stopping the DSM bill by SLDC as per order of APTEL dated 7.5.2018 passed in Appeal No.55/2015, the 15minute actual drawl data are not provided by SLDC. So, it is requested to provide the month wise actual drawl data in 15minutes block basis for giving more accurate day ahead schedule forecast by CESU.

Members may discuss
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by Dec’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Expected by Dec’2018.

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	Oct’18

	4
	400/220 kV, 2x315 MVA Lapanga S/S
	Sept’18

	5
	220/33 kV, 2x20 MVA Baliguda S/S
	July’19

	6
	220/33 kV, 2x20 MVA Kalimela S/S
	March’19

	7
	220/33 kV, 2x20 MVA Kasipur S/S
	Oct’18

	8
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	September’18

	9
	220/33 kV, 2x20 MVA Narasinghpur S/S
	Charged on 24th August’18

	10
	220/132 /33 kV, 2x100 MVA Aska S/S
	March’19

	11
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	Charged during March’18

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’19

	13
	220/132/33 kV Jayapatana S/S(320 MVA)
	March’19

	14
	220/132 kV Pratapsasan S/S(320 MVA)
	Dec’19

	15
	220/132 kV Kesinga S/S (320 MVA)
	March’19

	16
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	September’18

	17
	132/33 kV Ghense S/S
	Charged during April’18

	18
	132/33 kV Dhenkikote S/S 
	Charged on 24.02.2018

	19
	132/33 kV Betanati S/S
	March’19

	20
	132/33 kV Kantabanji S/S
	Charged on 28.02.18 

	21
	132/33 kV R.Udyagiri S/S
	December’18

	22
	132/33 kV Chikiti S/S
	October’18 (Bus charged on 11.09.18)

	23
	132/33 kV Athagarh S/S
	Charged on 31.05.2018

	24
	132/33 kV Udala S/S
	Charged on 16.09.2018


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement.
CGM (Construction) / DISCOMs may please deliberate the status.
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC

As per the provision in the Act, SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators will record 15 min block energy injection,   the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the 119th PSOC meeting CGM (O&M) stated that Ib TPS may deposit the required amount to release meters (for check meter).

In the 122nd PSOC meeting Ib TPS stated that this has already been approved by their Authority. The required amount will be deposited soon.

In the 123rd PSOC meeting O&M stated that the required amount is yet to be deposited by IB TPS. Ib TPS have not sent their representative to the meeting for deliberation.

In th 125th PSOC meeting O&M stated that IBTPS have already deposited the required amount with O&M. O&M will release the meters soon.

 O&M/ IBTPS may up date
E.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same.
A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.

M/S Secura Meters Ltd has shown a demo for the pilot project on dated 09.07.2018. However, the data integration with SLDC VPS was not elaborated in the said demo. 
In the 123rd PSOC meeting Telecom stated that M/S Secure meters could not complete the Demo, as M/S Chemtrol requires Rs. 3.5 lacs to allow firewall access to them. M/s Chemtrol also interested to take up the work. GRIDCO may allow them for the pilot project. OPTCL may examine for Firewall access to avoid burden to the Solar projects.

In the 124th PSOC meeting it was suggested that GRIDCO may write a letter to Chemtrol for the pilot project.
In the 125th PSOC meeting GRIDCO had agreed to write a letter to M/s Chemtrol. It was decided that a committee shall be constituted with representatives of GRIDCO, O&M, Telecom & SLDC to take a decision.

SLDC/GRIDCO/ O&M may deliberate
E.4: Major Events in the month of September’18
09.09.18: At 17:08 Hrs, 132 kV Digapahandi-Chikiti D/C line & on 11.09.18: Chikiti Bus charged.
16.09.18: At 14:30 Hrs 132/33 kV Udala S/S charged with LILO arrangement of 132 kV  Baripada-Balasore line.  

Members may note

E.5: Important Grid Incidences during the month of September’18.
On 17.09.2018 at 10:34 hrs  220 kV New Bolangir-New Bargarh Ckt tripped at both ends. (At New Bargarh –LBB. At New Bolangir-D/P, Zn-I, dist-5.32 km,  fault current IL1-151 amp, IL2-5360 amp, IL3-5369 amp, O/C). At 10:59 hrs while charging the above Ckt from New Bolangir end the line tripped pulling out 220 kV New Bolangir-Bolangir PG Ckt at New Bolangir on O/C, E/F, IL1-0.38 kA, IL2-0.43 kA, IL3-1.42 kA.
O&M & concern EM&R may analyze the incident for deliberation in the PCC meeting of ERPC. 
O&M may deliberate
E.6: Outage of major transmission Elements during the month of September’18. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration

Dt/time
	Reason

	1
	132 kV Joda-Kenduposi Ckt
	04.09.18

20:38
	05.09.18

13:23
	‘R’ ph jumper snapped at Loc. No-276. 

	2 
	220/132 kV, 160 MVA Auto-I at Budhipadar
	08.09.18

07:10
	10.09.18

10:53
	 220 kV side ‘B’ ph CT burst.

	3
	132 kV Balasore-Soro Ckt
	12.09.18

20:56
	13.09.18

17:46
	‘B’ ph conductor snapped between Loc. No-181 and 182

	4
	132 kV Baripada PG-Bhograi Ckt
	20.09.18

19:16
	22.09.18

13:11
	‘R’ ph jumper snapped at Loc. No-143

	5
	220 kV New Duburi-Paradeep Ckt-I
	22.09.18

01:56
	22.09.18

13:13
	‘R’ ph insulator damaged at Loc. No-280

	6
	220 kV Bhanjanagar-Mendhasal Ckt
	23.09.18

10:55
	24.09.18

19:40
	‘R’ ph conductor snapped at Loc. No-238

	7
	132 kV Joda-Kenduposi Ckt
	28.09.18

12:20
	29.09.18

18:51
	‘B’ ph insulator damaged at Loc. No-212


O&M may discuss
E.7:  Review of Outage Program of State Generators / Transmission elements for the month of November’18:
Tentative Outage programme for State Generators for the month of November’2018 
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 2

# 5

# 6
# 7
	14.03.18 to 30.10.18
25.05.18 to 25.10.18

25.10.16 to continue

16.10.15 to continue
01.11.18 to 30.11.18
	T&G coupling cover water leakage
Shaft seal problem

Under R,M & U

Under R, M & U
Annual Maintenance

	2
	Chiplima
	# 1
# 3
	22.07.18 to 29.10.18

15.10.15 to continue
	Flood water inrush to turbine 

Under R,M & U

	3
	Balimela
	# 1
# 2
# 3
# 5
	05.08.16 to continue
20.11.17 to continue
26.10.18 to 20.12.18

26.08.18 to 25.10.18
	Under R,M & U

Programming for R&M
Shaft alignment & Oil leakage
PMG problem & Annual Maintenance

	4
	Rengali
	# 2
	01.11.18 to 30.04.19
	Replacement of Runner disc.

	5
	Upper Kolab
	# 2
	28.05.17 to 31.12.18
	Upstream leakage and intake gate problem

	5
	U. Indravati
	# 2
	15.11.18 to 09.12.18
	Replacement of FCB & Thyristor bridge


[Action: OHPC / SLDC] 
E.8: Generation Program for the month of November’18.
Generation schedule for the month of November’18 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.10.18
	Reservoir Level as on 01.10.17
	MDDL
	High Flood    Reservoir Level

	
	Nov’18
(1st fortnight)
	Nov’18
(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	30
	30
	629.56
	630.15
	590 ft.
	630 ft.

	HPS-II, Chiplima
	20
	20
	-
	-
	-
	-

	Balimela
	150
	150
	1515.30
	1479.70
	1440 ft.
	1516 ft.

	Rengali
	40
	40
	121.61
	122.97
	109.72mtr 
	123.5 mtr.

	U.Kolab
	80
	80
	857.11
	852.63
	844 mtr 
	858 mtr.

	U. Indravati
	200
	200
	641.081
	636.02
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2748.10
	2745.00
	2685 ft.
	2750 ft.

	TOTAL
	550
	550
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

SLDC / OHPC may deliberate

E.9: Anticipated power generation and demand for the month of November’2018.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1100
	1300

	2
	WESCO
	1000
	1250

	3
	NESCO
	800
	900

	4
	SOUTHCO
	400
	450

	6
	Total Discom
	3300
	3900

	
	System Loss & others 
	150
	200

	
	Total Demand
	3450
	4100

	Availability
	
	

	1
	Hydro
	550  
	1000

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	300
	450

	4
	ISGS share (including OA& purchase)
	1200
	1350

	5
	CGP support (OA)
	300
	300

	6
	Total availability
	3100
	3850

	7
	Surplus / Deficit
	350
	250


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (127th) PSOC meeting.
PAGE  

