                                                                                                                  
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image1.png]PTC




Agenda

for

128th Power System Operational Co-ordination Meeting

Date: 18.12.2018
Venue: Power Training Center, Chandaka, Bhubaneswar 

Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 128th PSOC Meeting to be held on 18.12.2018 at OPTCL Power Training Center, Chandaka, Bhubaneswar
A. Confirmation of the minutes of the 127th PSOC Meeting held on 24.11.2018
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2017/3815 (47) dated 10.12.2018 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   :  Grid Performance for the month of November’2018
C.1: Over drawal/under injection by ER Entities
C.2: Status of projects funded under PSDF scheme 
C.3:  Requirement of 132kV bay at 400/220/132kV Baripada S/s---OPTCL
C.4: Use of Polymer Insulators in the transmission lines--CEA
C.5:  Review of Cyber Security Works/Activities 

C.6: Submission of static data for preparation of a report on coal fired stations in the country--ERLDC
C.7: Status of UFR healthiness installed in Eastern Region

C.8: Implementation of Automatic Demand Management Scheme

C.9: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s
C.10: Update on status of telemetry  

C.11: Mock Black start exercises in Eastern Region 

C.12: Irregularity of data punching to web based PSP portal--ERLDC
C.13: Submission of Thermal Loading of Transmission line and associated terminal equipment by ISTS licensee.

C.14: Flexibility in generation & scheduling of thermal Power Stations to reduce emission-MOP, GOI Order

C.15: Prolong Outage of transmission elements in Eastern Region

C.16: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Communication issues. 
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.
D.4: DISCOM agenda.
E.1: Commissioning status of New Transmission elements. 

E.2: Major Events in the month of November’18
E.3: Important grid incidences during the month of November’18.

E.4: Outage of major transmission Elements during the month November’18. (above 10 hrs).
E.5: Review of Outage Program of State Generators for the month of January’2019
E.6: Generation Program for the month of January’2019.
E.7: Anticipated power generation and demand for the month of January’2019.
F.1: Date and Venue of the next (129th) PSOC meeting
PART B: GRID PERFORMANCE
B. Review of Grid Performance for the month of November’18.

A. Frequency:

Hourly frequency variation for the month of November’18.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	Sept’18
	0.00
	0.11
	8.09
	75.23
	16.57
	49.97

	Oct’18
	0.00
	0.00
	7.78
	74.06
	18.17
	49.95

	Nov’18
	0.00
	0.00
	8.47
	79.04
	12.49
	49.95


Maximum & Minimum frequency during the month of Oct & Nov’18.
	Month
	Freq (Hz)
	Date
	Time

	Oct’18
	Maximum –50.11
	11.10.18
	13:00 Hrs

	
	Minimum – 49.75
	20.10.18
	17:15 Hrs

	Nov’18
	Maximum –50.12
	22.11.18
	21:45 Hrs

	
	Minimum – 49.79
	30.11.18
	06:30 Hrs



Grid Demand up to the month of November’18
	 Month
	Max. Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	Apr’18
	92.65
	23.04.18
	2400
	3334
	4430
	22.04.18
	21:00
	2348
	01.04.18
	24:00

	May’18
	98.61
	24.05.18
	2735
	3798
	4692
	07.05.18
	21.00
	2113
	14.05.18
	12.00

	June18
	98.45
	01.06.18
	2497
	3455
	4729
	01.06.18
	02:00
	2173
	29.06.18
	14:00

	July’18
	94.27
	29.07.18
	2572
	3457
	4498
	28.07.18
	22:00
	2010
	16.07.18
	13:00

	Aug’18
	114.57
	24.08.18
	3165
	4254
	5428
	23.08.18
	21:00
	3313
	28.08.18
	14:00

	Sept’18
	108.58
	30.09.18
	2857
	3968
	4973
	30.09.18
	21:00
	2881
	21.09.18
	05:00

	Oct’18
	116.85
	05.10.18
	3147
	4230
	5270
	02.10.18
	19:00
	3033
	12.10.18
	07:00

	Nov’18
	92.71
	06.11.18
	2615
	3632
	4522
	08.11.18
	19:00
	2959
	26.11.18
	03:00

	Nov’17
	79.46
	28.11.17
	2116
	2938
	4158
	01.11.17
	19:00
	2231
	24.11.17
	15:00


B. Voltage Profile of 220 kV Buses in OPTCL system for the month of: November’18

	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Atri
	230.93
	30
	3:00
	216.50
	16
	15:45

	2
	Balasore
	230.93
	2
	8:30
	216.90
	9
	18:00

	3
	Barkote
	230.76
	30
	23:45
	211.65
	29
	7:00

	4
	Bhadrak
	237.69
	2
	8:30
	216.10
	14
	17:00

	5
	Bhanjanagar
	233.07
	30
	23:45
	221.35
	8
	18:15

	6
	Bidanasi
	233.36
	30
	2:30
	219.39
	20
	17:45

	7
	Bolangir
	225.74
	25
	17:45
	212.57
	5
	17:00

	8
	Budhipadar
	231.16
	30
	23:45
	222.16
	29
	10:00

	9
	Chandaka
	232.03
	30
	3:15
	217.42
	9
	18:00

	10
	Cuttack
	230.30
	30
	3:00
	215.58
	9
	18:00

	11
	Duburi(O)
	232.55
	30
	3:15
	222.10
	9
	18:00

	12
	Duburi (N)
	231.28
	30
	3:15
	219.91
	9
	18:00

	13
	Jayanagar
	237.23
	24
	0:15
	223.02
	26
	18:00

	14
	Joda
	231.63
	15
	17:00
	216.38
	16
	9:00

	15
	Katapalli
	228.74
	30
	23:30
	219.16
	6
	18:45

	16
	Lapanga
	230.13
	30
	23:30
	223.77
	6
	18:45

	17
	Laxmipur
	236.19
	24
	3:00
	225.62
	10
	17:45

	18
	Mendhasal
	233.42
	30
	3:00
	219.10
	9
	18:00

	19
	Meramundali
	227.30
	30
	23:45
	218.98
	8
	17:30

	20
	Narendrapur
	230.82
	30
	23:45
	209.75
	6
	17:45

	21
	Nayagarh
	231.68
	30
	23:45
	218.12
	9
	13:45

	22
	Paradeep
	230.07
	30
	2:15
	212.63
	6
	9:15

	23
	Tarkera
	230.13
	30
	2:15
	223.60
	16
	11:15

	24
	Theruvali
	231.91
	24
	3:00
	219.79
	10
	17:45

	25
	Samangara
	230.01
	26
	2:45
	215.75
	20
	17:45


The maximum Voltage of 237.23 kV & 237.69 kV occurred at Jayanagar & Bhadrak 220 kV bus, while Narendrapur 220 kV bus has experienced the minimum Voltage of 209.75 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Mendhasal, Meramundali  and New Duburi bus during the month of November’2018 are indicated. 
[image: image2.emf]200

205

210

215

220

225

230

235

240

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NARENDRAPUR 220 kV Bus

FOR NOVEMBER 2018


[image: image3.emf]210

215

220

225

230

235

240

245

250

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF JAYANAGAR 220 KV BUS

FOR NOVEMBER 2018


[image: image4.emf]360

365

370

375

380

385

390

395

400

405

410

415

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MENDHASAL 400 KV BUS

FOR THE MONTH OF NOVEMBER 2018


[image: image5.emf]390

395

400

405

410

415

420

425

00:0000:3001:0001:3002:0002:3003:0003:3004:0004:3005:0005:3006:0006:3007:0007:3008:0008:3009:0009:3010:0010:3011:0011:3012:0012:3013:0013:3014:0014:3015:0015:3016:0016:3017:0017:3018:0018:3019:0019:3020:0020:3021:0021:3022:0022:3023:0023:30

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MERAMUNDALI 400 kV BUS

FOR NOVEMBER 2018


[image: image6.emf]390

395

400

405

410

415

420

425

430

00:0000:3001:0001:3002:0002:3003:0003:3004:0004:3005:0005:3006:0006:3007:0007:3008:0008:3009:0009:3010:0010:3011:0011:3012:0012:3013:0013:3014:0014:3015:0015:3016:0016:3017:0017:3018:0018:3019:0019:3020:0020:3021:0021:3022:0022:3023:0023:30

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF New DUBURI 400 kV BUS

FOR NOVEMBER 2018


Members may discuss.
C. Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of Nov-2018 [image: image7.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  NOVEMBER'2018

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

38.24 15 17:30 3.92 26 01:30

38.32 15 17:30 3.84 26 01:30

76.36 8 18:45 7.84 28 08:15

88.68 28 16:15 7.64 28 08:15

122.32 28 07:45 11.16 9 07:15

1x100 66.96 8 17:45 4.64 3 19:00

1x160 66.96 8 17:45 4.48 3 19:00

1x160 95.48 13 10:30 3.92 26 12:30

1x160 72.96 9 18:00 22.28 25 13:15

1x160 64.44 9 18:00 19.36 25 13:45

1x160 48.16 21 17:45 4.08 2 13:30

1x100 32.88 21 18:00 3.64 1 04:15

1x100 32.84 21 18:00 3.64 1 04:15

124.34 6 19:00 14.32 22 12:30

131.24 6 19:00 15.04 22 12:30

91.56 20 19:30 47.60 26 14:00

90.96 20 19:30 47.36 26 14:00

1x100 52.84 6 17:45 10.64 9 14:30

1x160 91.56 6 17:45 6.40 8 11:45

1x100 56.12 2 12:30 4.88 2 15:45

1x160 87.80 6 17:45 14.68 2 09:45

CUTTACK 1x160

48.88

5 11:00 5.92 29 15:45

1x160 58.52 5 17:45 5.36 17 16:30

1x100 43.32 20 12:15 3.04 17 16:30

1x100 45.40 20 12:15 3.20 17 16:30

1x160 80.52 27 19:30 9.36 29 18:45

1x160 82.28 30 18:30 16.20 18 15:15

59.76 12 12:15 31.28 5 14:00

60.32 12 12:45 30.32 5 14:00

56.16 7 17:45 30.64 5 14:00

1x100 24.92 19 19:30 1.28 27 09:30

1x100 25.52 10 08:30 1.20 27 09:30

1x160 38.36 10 08:30 2.00 27 09:30

62.36 25 08:45 21.72 16 17:45

64.36 24 16:30 836.00 4 04:15

37.48 19 17:45 6.32 11 15:45

36.84 5 10:48 6.32 11 15:45

35.84 5 09:00 6.12 11 15:30

21.00 3 08:45 10.20 3 12:00

33.60 2 06:00 5.40 5 12:00

100.64 11 18:30 28.16 15 13:30

100.64 11 18:15 28.24 15 13:30

1x100 57.72 11 18:15 15.92 15 13:30

1x160 103.96 5 18:30 10.60 5 11:30

1x100 68.64 5 11:30 20.92 30 14:45

1x50 38.20 5 11:30:00 11.72 30.00 14:45

4x100  57.28 28 17:15 17.88 23 03:15

58.52 28 17:00 23.44 25 14:45

57.00 28 17:00 6.96 25 06:30

57.04 28 17:00 23.00 25 14:45

2x100 52.84 18 17:15 3.60 27 08:15

50.24 18 17:15 7.88 22 12:30

1x160 82.16 18 17:15 11.40 22 12:30

1x160  82.83 23 14:15 0.00 2 12:00

1x160 82.83 23 14:15 0.00 2 12:00

2x100 79.36 20 19:45 15.64 12 15:30

79.56 20 19:45 15.64 12 15:30

2x160

2x160

2x160 LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 

BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & 

Katapali area load.}

2x100

2x160



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

BIDANASI 220/132 KV

{Bidanasi, Khurda }

3x100 



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }

JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]



"*" - Alternate P/S from 

Kuchei.



DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, 

Jajpur Road, Kalarangi, Jajpur Town}

Mendhasal { Part area load of Khurda S/S}

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100



SAMANGARA                                          

{ Puri, Nimapara & Konark}

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, 

Digapahandi, Mohana.}

THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), 

MCL, Sundergarh,Brajarajnagar, 

Rajgangpur}

2x160 

Rayagada & Paralakhemundi 

can be fed from Machhkund 

system.

Supported by Burla & 

Chipilima power.

PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 



BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

Drawal details

Maximum Minimum



BHADRAK 220/132 KV

{Bhadrak area load, Bhadrak(T),Soro,  

FACOR (I), Dhamra Port}

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}

3x160 

ATRI                                                     

{Banki, Khurda, Chandpur & Argul}


D. DISCOM Drawal up to the month of November’18
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	Apr’18
	745.479
	734.495
	770.403
	19.655
	750.748
	16.253

	
	May’18
	770.329
	819.87
	850.674
	20.004
	830.67
	10.8

	
	June’18
	745.48
	836.254
	848.445
	14.721
	833.724
	-2.53

	
	July’18
	770.329
	805.001
	823.135
	16.707
	806.428
	1.427

	
	Aug’18
	770.329
	825.849
	833.67
	17.428
	816.242
	-9.607

	
	Sept’18
	745.48
	741.752
	784.029
	5.113
	778.916
	37.164

	
	Oct’18
	770.329
	728.178
	783.342
	9.693
	773.649
	45.471

	
	Nov’18
	745.48
	608.066
	665.861
	14.026
	651.835
	43.769

	WESCO
	Apr’18
	585.205
	636.576
	689.137
	57.318
	631.819
	-4.757

	
	May’18
	604.712
	636.024
	1042.2
	362.004
	680.194
	44.17

	
	June’18
	585.205
	640.766
	995.128
	359.629
	635.499
	-5.267

	
	July’18
	604.712
	612.348
	767.095
	160.722
	606.373
	-5.975

	
	Aug’18
	604.712
	586.549
	1,152.89
	561.626
	591.265
	4.716

	
	Sept’18
	585.205
	606.175
	976.932
	365.889
	611.043
	4.868

	
	Oct’18
	604.712
	676.465
	1,293.38
	600.136
	693.24
	16.77

	
	Nov’18
	585.205
	547.993
	965.032
	350.615
	614.417
	66.424

	NESCO
	Apr’18
	504.658
	418.945
	528.936
	105.079
	423.857
	4.912

	
	May’18
	521.48
	480.187
	576.819
	102.344
	474.475
	-5.712

	
	June’18
	504.658
	488.448
	598.361
	113.554
	484.807
	-3.641

	
	July’18
	521.48
	481.593
	581.864
	95.907
	485.957
	4.364

	
	Aug’18
	521.48
	494.386
	644.557
	138.545
	506.012
	11.626

	
	Sept’18
	504.658
	467.35
	575.488
	99.903
	475.585
	8.235

	
	Oct’18
	521.48
	494.564
	594.427
	108.007
	486.42
	-8.144

	
	Nov’18
	504.658
	403.449
	536.939
	101.478
	435.461
	32.012

	SOUTHCO
	Apr’18
	300.822
	298.76
	298.778
	0
	298.778
	0.018

	
	May’18
	310.849
	321.453
	323.114
	0
	323.114
	1.661

	
	June’18
	300.822
	316.746
	315.514
	0.57
	314.944
	-1.802

	
	July’18
	310.849
	316.309
	313.076
	0.574
	312.502
	-3.807

	
	Aug’18
	310.849
	322.184
	322.519
	0
	322.519
	0.235

	
	Sept’18
	300.822
	302.037
	309.512
	0
	309.512
	7.475

	
	Oct’18
	310.849
	295.91
	298.996
	0
	298.996
	3.086

	
	Nov’18
	300.822
	248.651
	292.634
	0
	292.634
	43.983


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
     Members may please discuss.

E. Energy Generation / Import up to the month of November’18
Figures in MU  
	Month
	Thermal

(TTPS+IbTPS)
	OHPC 
& MKD
	CGP Support
	IPP Inj.
	RE
	ISGS
	Total

	April’18
	535.100
	421.700
	362.530
	198.950
	9.690
	872.260
	2400.240

	May’18
	567.940
	573.520
	313.169
	199.230
	14.390
	1066.640
	2734.893

	June’18
	485.813
	481.601
	219.983
	203.230
	11.897
	1084.870
	2487.390

	July’18
	440.179
	421.582
	213.953
	193.928
	10.102
	1292.141
	2571.886

	Aug’18
	473.390
	689.310
	163.300
	202.940
	13.680
	1621.990
	3164.600

	Sept’18
	454.183
	1037.515
	203.086
	136.688
	13.196
	1012.434
	2857.102

	Oct’18
	483.538
	927.724
	227.618
	191.329
	13.269
	1303.948
	3147.426

	Nov’18
	500.555
	406.963
	242.821
	255.937
	12.645
	1196.275
	2615.196

	Total
	3940.698
	4959.915
	1946.46
	1582.232
	98.869
	9450.558
	21978.733


F.  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of November’18 are as detailed:
	Month
	Total Generation
	Odisha Drawl
	AP Drawl

	
	MU
	Avg (MW)
	MU
	Avg (MW)
	MU
	Avg (MW)

	Apr’18
	37.162
	51.610
	18.613
	25.851
	16.943
	25.532

	May’18
	48.888
	65.700
	22.424
	30.140
	24.492
	32.919

	June’18
	43.185
	59.980
	19.692
	27.350
	21.635
	30.048

	July’18
	45.146
	60.680
	20.894
	28.083
	22.148
	29.769

	Aug’18
	51.319
	68.977
	23.507
	31.595
	25.708
	34.554

	Sept’18
	45.449
	63.123
	20.039
	27.032
	23.324
	32.394

	Oct’18
	50.184
	69.700
	22.268
	30.927
	25.721
	35.726

	Nov’18
	49.688
	69.011
	21.964
	30.506
	25.621
	 35.585

	Total
	371.021
	63.357
	169.401
	28.928
	185.592
	31.693


Drawl of State share power from Machhakund is decreasing for the past 7 months. Southco may add more feeders to Podagada S/s. 
SLDC/ SOUTHCO may deliberate.
G. Under Frequency Relay operation in OPTCL System during the month of Nov’18.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of November’18.
H. Status of Open Access applications up to the month of November’2018
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’18
	26
	79
	0
	31
	136
	26
	76
	0
	31
	133
	3

	2
	May’18
	59
	90
	0
	26
	175
	59
	89
	0
	26
	174
	1

	3
	June’18
	14
	57
	0
	30
	101
	14
	57
	0
	30
	101
	0

	4
	July’18
	18
	145
	0
	26
	189
	18
	145
	0
	26
	189
	0

	5
	Aug’18
	26
	90
	0
	37
	153
	26
	90
	0
	37
	153
	0

	6
	Sept’18
	25
	97
	0
	32
	154
	25
	97
	0
	32
	154
	0

	7
	Oct’18
	45
	60
	0
	28
	133
	45
	60
	0
	28
	133
	0

	8
	Nov’18
	39
	95
	0
	35
	132
	39
	95
	0
	35
	132
	0

	
	Total
	252
	713
	0
	245
	1210
	252
	709
	0
	245
	1206
	4


PART C – Issues discussed in the 152th  OCC meeting of ERPC held on 17.12.2018
C.1: Over drawal/under injection by ER Entities 

Odisha over drawl was in the range of 1 to 3MUwhile maximum over drawl touched 3.51MU on 05-12-18 and 395MW maximum on 05-12-18.
There is little improvement of load generation management observed in west Bengal and DVC but Odisha is still overdrawing in to the tune of 2 to 3 mu on daily basis. However, this reduction in quantum of over drawl occurred may be due to natural reduction of demand during winter season.
SLDC / GRIDCO may deliberate  

.
C.2: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
149th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	30.11.18
	162.5 Cr.


	38.09Cr. Requisition for 11.00 Cr placed.
	90% equipment installed and commissioned. Stn Tfr and some measuring instruments are under tendering process.



	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.22 Cr
	Request for 10% grant already submitted. Agreement  signed
	Tender floated

	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov18
Chiplima

Dec 2018
	22.35 Cr.
	2.235 Cr
	Placed work order for Balimele

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 


	27-07-18
	
	31.94 Cr
Ested. Cost. Approved amount 30.26 Cr. Grant amount 27.23 Cr.
	27.23 Cr.
	Agreement signed and sent to NLDC for signature. Tender floated.

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost. 2.93 Cr recommended by Appraisal committee.
	
	Approved by Appraisal committee. Forwarded to CERC for concurrence.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	12.03.2018  Date of submission 
	
	41.1 Cr

Estt cost
	
	Compliance to TSEG observation submitted. Audit observation has been sent to NLDC. 


      CGM (O&M) / OHPC/ SLDC may please update the status.
C.3: Requirement of 132kV bay at 400/220/132kV Baripada S/s---OPTCL 

OPTCL informed that at present two no. of 132 kV Bays are available at Kuchei. The Kuchei­ Rairangpur 132 kV S/C line is LILO at Bangiripushi. The loads of connected substation are as follows:  Bangiriposi-8 MW, Rairangpur-28 MW, Karanjia-21 MW, Dhenkikote-10 MW. Thus the 132 kV S/C line is loaded 67 MW. In case of outage at Joda the Polasponga load which is around 40 MW is catered through this line breaching the thermal limit of the line. 

OPTCL requested for a new 132 kV Bay at Kuchei for 132KV Kuchei­ Bangiripushi line to limit the line loading as well as to meet the n-1 contingency. 

In 151st OCC, OPTCL was advised to give a presentation in next OCC Meeting for detailed discussion.  

OCC advised Powergrid to check the feasibility of providing 132kV bay at 400/220/132kV Baripada S/s.  

CGM (O&M) / CGM (Const) may deliberate.
C.4: Use of Polymer Insulators in the transmission lines--CEA 

CEA vide letter dated 28th November 2018 informed that many representations have been received in CEA as well as VIP references from Ministry of Power from various manufacturers and associations highlighting the issue of use indiscriminate use of polymer insulators which are mostly imported from China leading to closure of indigenous porcelain manufacturing industry. To resolve the issue, a meeting was held in CEA on 25.5.2018 with various stakeholders to deliberate on the issue. 

PGCIL vide letter no. C/CTU/E/02/TBCB dated 24.10.2018, indicated that on the directions of RPC's, only polymer type insulators are being used in the new transmission lines of PGCIL traversing through states in Northern and eastern Regions. Moreover, PGCIL is replacing the porcelain insulators with polymer insulators in the existing transmission lines of the region. PGCIL has categorically mentioned that the same has been done in accordance with the decision taken in the meetings with Regional Power Committees. 

It is to mention that CEA has issued the Regulations and there are specific provisions regarding use of porcelain (disc type I long rod) and polymer insulators. Regulation Clause No. 89(1)(f)(i) of CEA (Technical Standards for Construction of Electrical Plants and Electric Lines) Regulations 201 0, may be referred in this regard. 

It may be clarified whether decision of use of polymer insulation in place of porcelain insulator was taken for some particular lines or locations. Considering the sensitiveness of issue, the same may also be discussed in respective RPC meetings and a balanced approach may be adopted for all future lines. 

O&M may deliberate.
C.5: Review of Cyber Security Works/Activities- CEA 

CEA vide letter informed that Secretary (Power) is going to review the cyber security related works /activities being carried out in Power Sector. In this regard, it is requested to provide the State wise status on following action points pertaining to cyber security at the earliest: 

1. Appointment of organization-wise Chief Information Security Officers and its status
2. Identification of organization-wise Critical Infrastructure and its status 
3. Preparation of organization-wise Crisis Management Plan and its status 
4. Status of Cyber Security Mock Drill activity in coordination with CERT-In 
5. Status of Training / Workshops on Cyber Security organized / participated by power sector entities 
6. Status of action taken on CERT-In / NCIIPC advisories 

In 148th OCC, all the constituents were advised to send the latest status to mserpc-power@nic.in within a week.   

The same has been received from WBSETCL and OPTCL only.
In the 127th PSOC meeting POWERGRID made a presentation on Cyber Security.
IT may update 
C.6: Submission of static data for preparation of a report on coal fired stations in the country--ERLDC 

One internal committee has been formed by POSOCO to prepare a report on coal fired stations in the country, which will be submitted to the FOLD &FOR, at a later stage. Similar reports have already been prepared by POSOCO for hydro, gas and RES plants, which has been widely appreciated in different forums like FOLD & FOR.  

To prepare this report, some static data (commercial, technical, environmental & general) in proper format for all coal fired stations (ISGS, IPP and State Generators) of capacity >= 200 MW need to be submitted to ERLDC so that the compilation and subsequent analysis of data of thermal generators on an all India basis could be made within stipulated time period. 

The format for data submission was intimated to all generators and state SLDCs via email. Till date only GMR, Adhunik, MPL and Sagardighi have submitted their static data. 

ISGS (NTPC), IPP and State Generators of Eastern Region are requested to kindly accord high priority for submitting the static data to ERLDC in erldcso@posoco.in for preparation of the report within stipulated period. 

Nodal coordinators for this Process from ERLDC are: 

1. Shri Biswajit Mondal, Sr. Engineer, Mob No: 9903329271 2. Shri Chandan Mallick, Sr. Engineer, Mob No: 9007059660 

All Thermal Generators may comply.

C.7: Status of UFRs healthiness installed in Eastern Region 

UFR Healthiness Certification for the month of November, 2018 has been received from CESC, WBSETCL, DVC, BSPTCL and JUSNL. 

OPTCL informed that all UFRs healthy except Sadepalli feeder which would be replaced by 15th November 2018.  

OPTCL may update.
C.8: Implementation of Automatic Demand Management Scheme

The latest status along with proposed logic as follows: 
	Sl. No
	State /Utility
	Logic for ADMS operation
	Implementation status/target
	Proposed logic (if different from under implementation logic

	1
	Odisha
	1. System Frequency < 49.9 Hz 
2. Odisha over-drawl > 150 MW
3. DISCOM over-drawl > (40 MW) 
	10 Months

Sent for PSDF approval
	Logic 2 and 3 is AND or OR, in case it is AND then ADMS may not operate when DISCOMs are in schedule but GRIDCO is over drawing due to less generation at State embedded generators.


In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 123rd PSOc meeting SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval

In the 124th PSOC meeting SLDC stated that the revised estimate has been approved in the BoD.

In the 126th PSOC meeting SLDC stated that CERC approval is awaited for tendering.

SLDC may deliberate the status

C.9: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 127th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by Dec’18. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by March’19.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Keonjhar S/S (220/33 kV) by December’18. All work completed.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	March’2019 


CGM (Cont) / CGM (O&M) may update

C.10: Update on status of telemetry  

CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed  NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action.

In the 149th OCC, ERLDC stated that status of Breaker & isolator of NALCO & JITPL are not available.

In the 126th PSOC meeting Telecom stated that Service engineer of the company provided NALCO internal SCADA has arrived but could not rectified the data communication of NALCO to SLDC. Telecom suggested that NALCO may go for optical fibre for uninterrupted data communication instead of PLCC.

In the 127th PSOC meeting Telecom stated that the data communication is not consistent. NALCO stated that they are agreeing to go for optical fiber. Telecom may forward their suggestion and offer for taking necessary action by NALCO. It was suggested that NALCO may coordinate with Telecom in this regard.
Telecom / NALCO may update the status

C.11: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2018-19 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2018
	Done on 28.06.2018
	Last week of January 2019
	

	3
	Rengali
	2nd week of June 2018
	Done on 18.08.2018
	Last week of November 2018
	

	4
	U. Indravati
	3rd week of June 2018
	December’18
	2nd week of February 2019
	

	6
	Balimela
	3rd week of October  2018
	December’18
	1st week of March 2019
	

	9
	Burla
	Last week of June 2018
	Done on 07.06.2018
	Last week of February 2019
	


Schedule for demonstration of black start exercise as follows: 

Balimela HEP of OHPC:21st December 2018 in presence of ERPC and ERLDC engineers

SLDC / OHPC may deliberate

C.12: Irregularity of data punching to web based PSP portal--ERLDC 

ERLDC has successfully migrated to web based PSP reporting system since 9th September 2018 in which constituents have access to furnish their respective daily energy consumption/generation through web based portal using their own user ids. The report generated based on such punched data, is used by MOP, CEA, NLDC and other various organizations. The success of preparation and publication of error free Web PSP report in time is totally dependent on the active cooperation ofall the constituents filling the data during night hours. As per the recent practice for report preparation, data filled within 04:00 Hrs are considered for report preparation. In case data is not filled by the user for a particular field within 04:00 Hrs during night then SCADA data for that field is used for report preparation. 

Some observations regarding submission of data in Web PSP are follows: 

1. Users viz: Adhunik (APNRL), KBUNL. DMTCL, BRBCL, Tashiding, Barh and FSTPP are not filling data in Web PSP regularly. 2. Regular mismatch of 4 to 6 mu in 765kV Dharamjaigarh-Jharsuguda-Q/D energy data as declared by RTAMC ER – II and SCADA data of same link is observed. Same also verified from SEM data. 

In this regard all the users are requested to kindly attach due seriousness to fill their own data in Web PSP portal by 04:00 Hrs. Powergrid RTAMC ER – II is requested to check the data of 765kV Dharamajaigarh-Jharsuguda-Q/Dbefore publishing during night hour. 

In 151st OCC, Powergrid RTAMC ER – II agreed to look into the matter of 765 kV DharamjaigarhJharsuguda-Q/D energy data; however till date energy data submitted by ER-II RTAMC during night hour differ from SCADA and SEM energy data. 

Odisha and West Bengal are requested to elaborate the mythology followed for submission of CPP net energy data. 

Members may please note and comply.
C.13: Submission of Thermal Loading of Transmission line and associated terminal equipment by ISTS licensee  

In line with the MoM of 4th NRCE Meeting dt.03-11-14 and “Operational Guidelines for determination Of TTC, ATC and TRM for the Short-Term Horizon (0-3 Months)” published by NRCE dt.20-02-15, thermal limit for transmission line has to be used for calculation of ATC/TTC. However, the thermal loading of transmission line depend on the Maximum Conductor Temperature, End equipment thermal rating. This has to be submitted by the Owner of the equipment. Further, the equipment owner also has to confirm that relay setting has been aligned so that the line can be operated up to its thermal limit. In the absence of complete details, ERLDC is utilising the data from the CEA Planning Criteria  for thermal rating as given below : 

	Conductor Type 


	Ampacity per 

conductor(A)* 


	Thermal loading 

limit of line (MVA) 



	765 kV Quad ACSR_Bersimis
	732
	3880

	765 kV HexaACSR_Zebra
	560
	4452

	400 kV Twin ACSR_Moose
	631
	874

	400 kV Quad ACSR_Moose 
	631
	1749

	400 kV Quad ACSR_Bersimis 
	732
	2029

	400 kV Triple Snowbird
	630
	1309

	400 kV Twin ACSR_Lapwing
	773
	1071

	220 kV Single AAAC_Zebra
	557
	212

	220 kV Single ACSR_Zebra 
	560
	213

	220 kV Twin ACSR_Moose 
	631
	481

	132 kV Single ACSR_Zebra 
	560
	128

	132 kV Single ACSR_Panther 
	366
	84

	
	
	


*Ambient and Maximum conductor temperature are taken as 45°C and 75°C respectively. Apart from above specifically mentioned in CEA transmission planning criteria following loading limit is considered for HTLS line while calculating ATC/TTC 

	Conductor Type 


	Ampacity per 

conductor(A)* 


	Thermal loading 

limit of line (MVA) 



	400 kV Twin HTLS
	1262 
	1750

	220 kV Single HTLS 
	1020 
	390

	132 kV Single HTLS
	732
	168


In view of this, it is desired that all ISTS Licensee and STU (for 400 kV and important 220 kV lines) may kindly submit the following details to ERLDC for utilization in ATC/TTC calculation: 
a) Transmission line wise Ampacity and Thermal loading along with Maximum Conductor Temperature and conductor type.
b) End Equipment Rating and 
c) Confirmation whether the relay setting has been adopted in line with the thermal rating of the line 

d) Any constraint during thermal loading of line  

OCC advised all the ISTS licensees and STUs to submit the relevant data to ERLDC and ERPC. 
Members may note and comply.  
C.14: Flexibility in generation & scheduling of thermal Power Stations to reduce emission-MOP, GOI Order

CEA vide letter dated 18th July 2018 informed that a committee has been constituted in CEA under Chief Engineer (TPRM) to develop a road map to enable flexible operation of thermal power stations for smooth integration of intermittent RES generation. 

CEA requested for plant performance data as per the format enclosed at Annexure-C18. CEA requested to submit the hard copy and softcopy (in excel) to cetrmcea@yahoo.com.  

OCC advised all the Generators to submit the plant performance data as per the format to CEA.  

Members may note and comply.
C.15: Prolonged outage of Power System elements in Eastern Region
Thermal Generating units

	Sl. No
	Station
	Location
	Owner
	Unit No
	Capacity (MW)
	Reason
	Outage date

	1
	Vedanta
	Odisha
	GRIDCO
	2
	600
	Turbine bearing vibration
	23.11.18

	2
	Burla
	Odisha
	OHPC
	1
	37.5
	R&M
	25.10.16

	3
	Burla
	Odisha
	OHPC
	2
	37.5
	R&M
	16.10.15

	4
	Burla
	Odisha
	OHPC
	4
	37.5
	Annual Maintenance
	25.10.18

	5
	Burla
	Odisha
	OHPC
	6
	37.5
	R&M
	16.10.15

	6
	Balimela
	Odisha
	OHPC
	1
	60
	R&M
	05.08.16

	7
	Balimela
	Odisha
	OHPC
	2
	60
	R&M
	20.11.17

	8
	Balimela
	Odisha
	OHPC
	5
	60
	Annual Maintenance
	12.10.17

	9
	U. Kolab
	Odisha
	OHPC
	2
	80
	Repair of MIV & DT gate
	25.08.17

	10
	U. Kolab
	Odisha
	OHPC
	3
	80
	Problem in bypass valve
	

	11
	Chipilima
	Odisha
	OHPC
	1
	24
	Flood water in rush
	21.07.18

	12
	Rengali
	Odisha
	OHPC
	1
	50
	Annual Maintenance
	31.10.18

	13
	Indravati
	Odisha
	OHPC
	4
	150
	Sheer pin failure
	


Vedanta & OHPC may deliberate
C.16: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.  

· As per the information received from the constituents the following generators certified with IS 18001:  

· All NTPC stations in Eastern Region  

· Teesta, NHPC 

· All OHPC generating units  

· All CESC generating units  

· All units of WBPDCL 

· DGPC units 

In the 117th PSOC meeting CGM (O&M) stated that draft project report for Mendhasal S/S has been submitted to BIS. The report will be approved in the meeting to be conducted by them.

In the 122nd PSOC meeting CGM (O&M) stated that Audit team is expected soon.

In the 123rd PSOC meeting CGM (O&M) stated that the report is yet to be received.

In the 126th PSOC meeting O&M stated that training has been completed. After compliance of the observations, certificate will be issued. 
In the 127th PSOC meeting O&M stated that internal Audit will be started in the month of December.

O&M may update the status

PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of October’18:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	43.769
	7.198

	2
	WESCO
	0
	66.424
	12.121

	3
	NESCO
	0
	32.012
	7.934

	4
	SOUTHCO
	0
	43.983
	17.688

	
	Total
	0
	186.188
	


It is noticed that all the DISCOMs were over drawn during the month. SOUTHCO has deviated 17.688% followed by WESCO 12.121 % from the scheduled energy while NESCO and CESU have deviated 7.938 % & 7.198 % respectively. DISCOMs may forecast their drawal in realistic approach to minimise deviation.

SLDC/ Discoms may please deliberate.
D.2: Communication issues 
The status of data communication from CGPs as deliberated in the 124rd PSOC meeting meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	2
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. 
In the 123rd PSOC meeting it was deliberated that RT&C have sought some information from Telecom wing which will be intimated. NALCO stated that due to problem in their internal communication system, data communication to SLDC is being interrupted.
In the 124th PSOC meeting Telecom stated that communication system for Paradeep area industries will be completed by September’2018. Telecom was advised to give a reply to the information sought by RT&C. 

In the 125th PSOC meeting Telecom stated that the information sought by RT&C will be forwarded soon.
In the 126th PSOC meeting it was decided that SLDC shall convene a meeting with Telecom, GCC & RT&C and discuss the issue for filing case before the OERC.

In the 127th PSOC meeting SLDC stated that the meeting will be convened during the month of January’18

SLDC/ Telecom/GCC / RT&C may deliberate 
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 119th PSOC meeting IT stated that Parameters of 16 Nos meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
In the 123rd PSOC meeting IT stated that out of 840 Nos interface meters connected with AMI, 750 Nos are reporting at present. The newly replaced meters are not reporting. 2 Nos. of meters has sent to M/s SECURE meters for study.

In the 124th PSOC meeting O&M stated that SLDC may intimate the list of defective energy meters to O&M on monthly basis for necessary action. IT may ask TCS to co-ordinate with Secure meters and develop a driver data extraction  
In the 127th PSOC meeting IT stated that TCS is demanding Rs. 6.5 lacs for developing the required software. The proposal is placed before the management for approval

IT/ SLDC may deliberate
D.4: DISCOM Agenda

CESU 

1. Installation of 2x20 MVA Transformer at Hind Metal S/W stn. for feeding to 33/11 kV S/S already commissioned under ODSSP scheme.

2. Installation of 2x20 MVA Transformer at Grid Steel S/W St. for diversion of load from Athagarh feeder. 
3. Earlier 15minute actual drawl data was provided by SLDC, which was very much vital for giving the day ahead schedule forecast. But after stopping the DSM bill by SLDC as per order of APTEL dated 7.5.2018 passed in Appeal No.55/2015, the 15minute actual drawl data are not provided by SLDC. So, it is requested to provide the month wise actual drawl data in 15minutes block basis for giving more accurate day ahead schedule forecast by CESU.

Members may discuss
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Expected to be completed by Dec’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Completed

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	December’18

	4
	220/33 kV, 2x20 MVA Baliguda S/S
	July’19

	5
	220/33 kV, 2x20 MVA Kalimela S/S
	July’19

	6
	220/33 kV, 2x20 MVA Kasipur S/S
	December’18

	7
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	November’18

	8
	220/132 /33 kV, 2x100 MVA Aska S/S
	March’19

	9
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’19

	10
	220/132/33 kV Jayapatana S/S(320 MVA)
	July’19

	11
	220/132 kV Pratapsasan S/S(320 MVA)
	Dec’19

	12
	220/132 kV Kesinga S/S (320 MVA)
	March’19

	13
	132/33 kV Betanati S/S
	March’19

	14
	132/33 kV R.Udyagiri S/S
	March’19

	15
	132/33 kV Chikiti S/S
	(Bus test charged on 11.09.18)


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement.
CGM (Construction) / DISCOMs may please deliberate the status.
E.2: Major Events in the month of November’18
31.10.18:  At 13:24 Hrs, 220/132 kV, 160 MVA Auto-3 at Theruvali S/s charged.
03.11.18: 400 kV IbTPS-Lapanga DC line charged.

05.11.18: 400 kV Meramundali-Vedanta DC line made LILO at Lapanga.

23.11.18: At 14:25 Hrs 132/33 kV, 40 MVA Tfr test charged at Bolangir (New) S/S and loaded on 27.11.2018 at 21:25 hrs.
Members may note

E.3: Important Grid Incidences during the month of November’18.
On 29.11.18 at 07:22 hrs, during hand tripping of 220 kV Meramundali ckt-1 for availing shut down, one limb of breaker struck up which lead to LBB relay operation at TTPS end. All feeders connected to main bus –II tripped. Main bus was isolated condition at that time.

O&M may deliberate
E.4: Outage of major transmission Elements during the month of November’18. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration

Dt/time
	Reason

	1
	220 kV Mendhasal-Bidanasi  Ckt
	17.11.18

18:07
	18.11.18

11:10
	Snapping of R-Phase conductor at Loc-12

	2
	132 kV Meramundali-Dhenkanal Ckt
	21.11.18

17:48
	22.11.18

14:49
	Tripped at Meramundali on R-Ph E/F.

	3
	220/132 kV, 100 MVA Auto-1
	22.11.18

03:50
	23.11.18

17:50
	Buchholtz relay operated


O&M may discuss
E.5:  Review of Outage Program of State Generators / Transmission elements for the month of January’19:
Tentative Outage programme for State Generators for the month of January’2019 
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 4
# 5

# 6
	14.03.18 to 30.11.18
01.01.19 to 31.01.19
25.10.16 to continue

16.10.15 to continue
	T&G coupling cover water leakage
Annual Maintenance

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 2

# 3
	01.01.19 to 31.01.19

15.10.15 to continue
	Annual Maintenance

Under R,M & U

	3
	Balimela
	# 1
# 2
# 8
	05.08.16 to continue
20.11.17 to continue
21.12.18 to 20.01.19
	Under R,M & U

Programming for R&M
Annual Maintenance

	4
	Rengali
	# 2

# 4
	12.12.18 to continue
17.12.18 to 15.01.19
	Replacement of Runner disc.

A.M & DVR replacement

	5
	Upper Kolab
	# 1
# 2
# 4
	02.01.19 to 31.01.19
28.05.17 to 11.01.19
15.01.19 to 15.07.19
	Annual Maintenance
Upstream leakage and intake gate problem
Capital maintenance work


E.6: Generation Program for the month of January’19.
Generation schedule for the month of January’19 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.12.18
	Reservoir Level as on 01.12.17
	MDDL
	High Flood    Reservoir Level

	
	Jan’19
(1st fortnight)
	Jan’19
 (2nd fortnight)
	
	
	
	

	HPS-I, Burla
	20
	20
	625.56 ft.
	628.04 ft.
	590 ft.
	630 ft.

	HPS-II, Chiplima
	10
	10
	-
	-
	-
	-

	Balimela
	200
	200
	1510.00 ft.
	1483.80 ft.
	1440 ft.
	1516 ft.

	Rengali
	40
	40
	118.15 mtr.
	122.99 mtr.
	109.72mtr 
	123.5 mtr.

	U.Kolab
	100
	100
	855.49 mts.
	853.97 mtr.
	844 mtr 
	858 mtr.

	U. Indravati
	200
	200
	638.42 mtr.
	636.11 mtr.
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2744.40 ft.
	2748.80 ft.
	2685 ft.
	2750 ft.

	TOTAL
	600
	600
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

SLDC / OHPC may deliberate

E.7: Anticipated power generation and demand for the month of January’2019.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1050
	1200

	2
	WESCO
	1000
	1150

	3
	NESCO
	700
	800

	4
	SOUTHCO
	300
	350

	6
	Total Discom
	3050
	3500

	
	System Loss & others 
	150
	200

	
	Total Demand
	3200
	3700

	Availability
	
	

	1
	Hydro
	600  
	1050

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	400
	400

	4
	ISGS share (including OA& purchase)
	1100
	1200

	5
	CGP support (OA)
	350
	300

	6
	Total availability
	3200
	3700

	7
	Surplus / Deficit
	0
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (129th) PSOC meeting.
PAGE  

