Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 129th PSOC Meeting to be held on 29.01.2019 at OPTCL Power Training Center, Chandaka, Bhubaneswar
A. Confirmation of the minutes of the 128th PSOC Meeting held on 18.12.2018
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2017/59 (47) dated 05.01.2019 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   :  Grid Performance for the month of December’2018
C.1: Status of projects funded under PSDF scheme 
C.2: Evacuation of Power from OPGC expansion project-modification of network configuration-GRIDCO   

C.3: Islanding Scheme of IB-TPS 

C.4: Crossing of OPTCL transmission line under 400kV DC BaripadaDubri/Pandiabili (Earlier Baripada-Mendhasal line) without taking approval from POWERGRID--Powergrid 

C.5: Load Generation Balance Report (LGBR) for the year 2019-20 

C.6: Requirement of 132kV bay at 400/220/132kV Baripada S/s---OPTCL 

C.7: Use of Polymer Insulators in the transmission lines--CEA
C.8:  Review of Cyber Security Works/Activities 

C.9: Submission of static data for preparation of a report on coal fired stations in the country--ERLDC
C.10: Operation Eastern Regional grid from ERLDC back up control Centre at, NLDC, New Delhi as a part of Disaster Management: ERLDC 

C.11: Updation of Restoration procedure of  Eastern Region--ERLDC 

C.12: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC 
C.13: Status of UFRs healthiness installed in Eastern Region 

C.14: Implementation of Automatic Demand Management Scheme

C.15: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s
C.16: Update on status of telemetry  

C.17: Mock Black start exercises in Eastern Region 

C.18: Submission of Thermal Loading of Transmission line and associated terminal equipment by ISTS licensee  

C.19: Prolong Outage of transmission elements in Eastern Region

C.20: Restricted Governor /Free Governor Mode Operation of generators in ER 

C.21: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

C.22: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Communication issues. 
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.
D.4: Commissioning of 220 kV Tarkera-RSP 2nd D/C line-RSP agenda.
E.1: Commissioning status of New Transmission elements. 

E.2: Major Events in the month of December’18
E.3: Important grid incidences during the month of December’18.

E.4: Outage of major transmission Elements during the month December’18. (above 10 hrs).
E.5: Review of Outage Program of State Generators for the month of February’2019
E.6: Generation Program for the month of February’2019.
E.7: Anticipated power generation and demand for the month of February’2019.
F.1: Date and Venue of the next (130th) PSOC meeting
PART B: GRID PERFORMANCE
B. Review of Grid Performance for the month of December’18.

A. Frequency:

Hourly frequency variation for the month of December’18.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	Oct’18
	0.00
	0.00
	7.78
	74.06
	18.17
	49.95

	Nov’18
	0.00
	0.00
	8.47
	79.04
	12.49
	49.95

	Dec’18
	0.00
	0.02
	11.78
	76.66
	11.54
	49.98


Maximum & Minimum frequency during the month of Nov & Dec’18.
	Month
	Freq (Hz)
	Date
	Time

	Nov’18
	Maximum –50.12
	22.11.18
	21:45 Hrs

	
	Minimum – 49.79
	30.11.18
	06:30 Hrs

	Dec’18
	Maximum –50.14
	23.12.18
	14:00 Hrs

	
	Minimum – 49.72
	21.12.18
	07:30 Hrs



Grid Demand up to the month of December’18
	 Month
	Max. Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	Apr’18
	92.65
	23.04.18
	2400
	3334
	4430
	22.04.18
	21:00
	2348
	01.04.18
	24:00

	May’18
	98.61
	24.05.18
	2735
	3798
	4692
	07.05.18
	21.00
	2113
	14.05.18
	12.00

	June18
	98.45
	01.06.18
	2497
	3455
	4729
	01.06.18
	02:00
	2173
	29.06.18
	14:00

	July’18
	94.27
	29.07.18
	2572
	3457
	4498
	28.07.18
	22:00
	2010
	16.07.18
	13:00

	Aug’18
	114.57
	24.08.18
	3165
	4254
	5428
	23.08.18
	21:00
	3313
	28.08.18
	14:00

	Sept’18
	108.58
	30.09.18
	2857
	3968
	4973
	30.09.18
	21:00
	2881
	21.09.18
	05:00

	Oct’18
	116.85
	05.10.18
	3147
	4230
	5270
	02.10.18
	19:00
	3033
	12.10.18
	07:00

	Nov’18
	92.71
	06.11.18
	2615
	3632
	4522
	08.11.18
	19:00
	2959
	26.11.18
	03:00

	Dec’18
	81.98
	01.12.18
	2188
	2941
	4038
	01.12.18
	19:00
	1698
	18.12.18
	03:00

	Dec’17
	77.95
	28.12.17
	2171
	2919
	4230
	27.12.17
	21:00
	2057
	09.12.17
	04:00


B. Voltage Profile of 220 kV Buses in OPTCL system for the month of: December’18

	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Atri
	235.78
	18
	3:45
	220.48
	12
	19:15

	2
	Balasore
	234.11
	18
	3:00
	220.37
	12
	18:00

	3
	Barkote
	232.49
	20
	14:00
	226.03
	12
	18:45

	4
	Bhadrak
	237.34
	18
	3:00
	222.27
	12
	18:00

	5
	Bhanjanagar
	237.69
	18
	3:45
	223.25
	12
	16:45

	6
	Bidanasi
	239.88
	30
	22:00
	225.68
	12
	18:15

	7
	Bolangir
	230.99
	18
	3:00
	216.73
	13
	8:30

	8
	Budhipadar
	233.53
	18
	3:30
	215.93
	26
	11:15

	9
	Chandaka
	235.32
	18
	3:45
	221.29
	12
	19:15

	10
	Cuttack
	234.92
	18
	3:45
	219.73
	12
	19:15

	11
	Duburi(O)
	237.75
	18
	3:45
	226.37
	28
	7:45

	12
	Duburi (N)
	226.72
	18
	3:45
	216.38
	12
	18:00

	13
	Jayanagar
	239.77
	17
	5:30
	228.85
	12
	19:15

	14
	Joda
	234.34
	18
	6:00
	217.31
	12
	18:45

	15
	Katapalli
	232.49
	18
	3:30
	219.68
	26
	8:30

	16
	Lapanga
	233.70
	17
	13:15
	214.01
	2
	8:45

	17
	Laxmipur
	237.86
	17
	23:45
	226.89
	12
	19:15

	18
	Mendhasal
	238.27
	18
	4:00
	223.31
	12
	19:15

	19
	Meramundali
	229.37
	17
	3:45
	221.00
	12
	18:30

	20
	Narendrapur
	237.23
	18
	2:45
	217.60
	24
	10:15

	21
	Nayagarh
	236.24
	18
	3:45
	221.00
	12
	19:00

	22
	Paradeep
	234.97
	18
	4:30
	219.44
	10
	18:15

	23
	Tarkera
	230.93
	18
	3:30
	224.24
	6
	10:00

	24
	Theruvali
	234.51
	18
	3:45
	220.43
	7
	16:30

	25
	Samangara
	236.36
	18
	3:00
	219.27
	12
	19:15


The maximum Voltage of 239.77 kV occurred at Jayanagar 220 kV bus, while Lapanga 220 kV bus has experienced the minimum Voltage of 214.01 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Mendhasal, Meramundali  and New Duburi bus during the month of December’2018 are indicated. 
[image: image1.emf]200

205

210

215

220

225

230

235

240

00:0000:3001:0001:3002:0002:3003:0003:3004:0004:3005:0005:3006:0006:3007:0007:3008:0008:3009:0009:3010:0010:3011:0011:3012:0012:3013:0013:3014:0014:3015:0015:3016:0016:3017:0017:3018:0018:3019:0019:3020:0020:3021:0021:3022:0022:3023:0023:30

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NARENDRAPUR 220 kV BUS

FOR DECEMBER 2018


[image: image2.emf]210

215

220

225

230

235

240

245

250

00:0000:3001:0001:3002:0002:3003:0003:3004:0004:3005:0005:3006:0006:3007:0007:3008:0008:3009:0009:3010:0010:3011:0011:3012:0012:3013:0013:3014:0014:3015:0015:3016:0016:3017:0017:3018:0018:3019:0019:3020:0020:3021:0021:3022:0022:3023:0023:30

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF JAYANAGAR 220 KV BUS

FOR DECEMBER'2018


[image: image3.emf]380

385

390

395

400

405

410

415

420

425

430

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MENDHASAL 400 KV BUS

FOR DECEMBER'2018


[image: image4.emf]390

395

400

405

410

415

420

425

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MERAMUNDALI 400 KV BUS

FOR DECEMBER' 2018


[image: image5.emf]390

395

400

405

410

415

420

425

430

00:0000:3001:0001:3002:0002:3003:0003:3004:0004:3005:0005:3006:0006:3007:0007:3008:0008:3009:0009:3010:0010:3011:0011:3012:0012:3013:0013:3014:0014:3015:0015:3016:0016:3017:0017:3018:0018:3019:0019:3020:0020:3021:0021:3022:0022:3023:0023:30

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF New DUBURI 400 KV BUS

FOR DECEMBER' 2018


Members may discuss.
C. Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of Dec-2018 [image: image6.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  DECEMBER'2018

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

53.40 21 12:30 1.12 25 02:45

63.76 20 10:30 1.04 25 02:45

72.56 31 07:30 29.24 18 04:00

72.52 8 18:30 3.88 20 08:15

73.72 31 06:30 29.76 18 03:00

1x100 51.20 28 17:45 2.48 25 19:00

1x160 63.04 28 17:45 2.32 6 10:00

1x160 62.92 28 17:45 2.24 6 10:00

1x160 121.56 28 08:15 10.40 29 12:30

1x160 112.92 31 08:30 9.16 28 08:15

1x160 38.04 10 12:15 2.56 14 03:45

1x100 19.72 31 19:00 2.00 15 23:30

1x100 28.16 31 19:00 3.12 15 23:30

122.12 28 18:45 3.72 31 12:45

128.72 28 18:45 13.64 17 06:00

107.76 26 08:15 21.96 9 04:00

108.56 26 08:15 38.04 17 06:15

1x100 40.32 19 08:45 9.08 22 15:45

1x160 69.64 19 08:45 19.08 5 03:15

1x100 43.16 19 08:45 11.80 5 03:15

1x160 66.72 19 08:45 18.16 5 03:15

2x160

50.44

9 17:30 7.12 18 04:15

44.24

5 11:15 6.16 13 14:15

1x160 59.20 8 08:00 5.96 17 04:15

1x100 37.40 8 08:00 3.48 17 04:15

1x100 35.60 8 08:00 2.84 21 16:00

1x160 77.56 11 18:15 7.44 6 11:30

1x160 115.08 27 18:00 17.72 18 01:45

54.40 15 19:00 20.36 6 18:15

54.48 15 19:00 20.04 6 13:30

54.32 15 19:00 20.24 6 21:00

1x100 26.72 13 07:30 1.52 13 22:45

1x100 26.68 13 07:30 1.04 13 22:45

1x160 40.08 13 07:30 1.72 13 22:45

61.20 4 10:30 16.36 3 11:45

60.56 14 10:48 17.48 17 06:00

43.68 12 17:45 4.44 31 01:15

42.92 12 17:45 4.52 31 01:15

41.56 12 19:15 1.52 17 11:15

20.40 19 04:00 5.40 8 12:00

27.60 1 10:00 6.60 13 12:00

123.68 27 10:15 6.52 6 09:00

110.36 7 10:15 6.76 27 08:30

1x100 71.36 27 10:15 4.84 12 08:15

1x160 95.68 9 18:30 12.64 10 06:00

1x100 77.72 10 07:15 11.80 29 14:30

1x50 43.52 10 07:15:00 6.76 29.00 14:30

4x100  58.52 29 08:00 3.04 8 05:15

69.04 18 10:30 9.28 17 03:30

67.84 18 10:30 7.80 6 09:30

59.48 8 07:30 1.88 18 04:00

2x100 44.76 22 18:15 5.76 28 11:15

42.60 13 18:00 8.68 4 12:45

1x160 69.32 13 18:00 12.88 4 12:45

1x160  86.64 14 04:00 0.00 31 08:45

1x160 86.64 14 04:00 0.00 31 08:45

2x100 69.24 18 11:00 9.84 18 02:45

69.40 18 11:00 9.76 18 04:00



BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

Drawal details

Maximum Minimum



BHADRAK 220/132 KV

{Bhadrak area load, Bhadrak(T),Soro,  

FACOR (I), Dhamra Port}

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}

3x160 

ATRI                                                     

{Banki, Khurda, Chandpur & Argul}

SAMANGARA                                          

{ Puri, Nimapara & Konark}

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, 

Digapahandi, Mohana.}

THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), 

MCL, Sundergarh,Brajarajnagar, 

Rajgangpur}

2x160 

Rayagada & Paralakhemundi 

can be fed from Machhkund 

system.

Supported by Burla & 

Chipilima power.

PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 



"*" - Alternate P/S from 

Kuchei.



DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, 

Jajpur Road, Kalarangi, Jajpur Town}

Mendhasal { Part area load of Khurda S/S}

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

BIDANASI 220/132 KV

{Bidanasi, Khurda }

3x100 



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }

JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]

2x160

2x160

2x160 LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 

BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & 

Katapali area load.}

2x100

2x160

CUTTACK


D. DISCOM Drawal up to the month of December’18
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	Apr’18
	745.479
	734.495
	770.403
	19.655
	750.748
	16.253

	
	May’18
	770.329
	819.87
	850.674
	20.004
	830.67
	10.8

	
	June’18
	745.48
	836.254
	848.445
	14.721
	833.724
	-2.53

	
	July’18
	770.329
	805.001
	823.135
	16.707
	806.428
	1.427

	
	Aug’18
	770.329
	825.849
	833.67
	17.428
	816.242
	-9.607

	
	Sept’18
	745.48
	741.752
	784.029
	5.113
	778.916
	37.164

	
	Oct’18
	770.329
	728.178
	783.342
	9.693
	773.649
	45.471

	
	Nov’18
	745.48
	608.066
	665.861
	14.026
	651.835
	43.769

	
	Dec’18
	770.329
	582.852
	600.916
	14.372
	586.544
	3.692

	WESCO
	Apr’18
	585.205
	636.576
	689.137
	57.318
	631.819
	-4.757

	
	May’18
	604.712
	636.024
	1042.2
	362.004
	680.194
	44.17

	
	June’18
	585.205
	640.766
	995.128
	359.629
	635.499
	-5.267

	
	July’18
	604.712
	612.348
	767.095
	160.722
	606.373
	-5.975

	
	Aug’18
	604.712
	586.549
	1,152.89
	561.626
	591.265
	4.716

	
	Sept’18
	585.205
	606.175
	976.932
	365.889
	611.043
	4.868

	
	Oct’18
	604.712
	676.465
	1,293.38
	600.136
	693.24
	16.77

	
	Nov’18
	585.205
	547.993
	965.032
	350.615
	614.417
	66.424

	
	Dec’18
	604.712
	568.413
	686.294
	114.336
	571.958
	3.545

	NESCO
	Apr’18
	504.658
	418.945
	528.936
	105.079
	423.857
	4.912

	
	May’18
	521.48
	480.187
	576.819
	102.344
	474.475
	-5.712

	
	June’18
	504.658
	488.448
	598.361
	113.554
	484.807
	-3.641

	
	July’18
	521.48
	481.593
	581.864
	95.907
	485.957
	4.364

	
	Aug’18
	521.48
	494.386
	644.557
	138.545
	506.012
	11.626

	
	Sept’18
	504.658
	467.35
	575.488
	99.903
	475.585
	8.235

	
	Oct’18
	521.48
	494.564
	594.427
	108.007
	486.42
	-8.144

	
	Nov’18
	504.658
	403.449
	536.939
	101.478
	435.461
	32.012

	
	Dec’18
	521.48
	412.703
	528.254
	91.205
	437.049
	24.346

	SOUTHCO
	Apr’18
	300.822
	298.76
	298.778
	0
	298.778
	0.018

	
	May’18
	310.849
	321.453
	323.114
	0
	323.114
	1.661

	
	June’18
	300.822
	316.746
	315.514
	0.57
	314.944
	-1.802

	
	July’18
	310.849
	316.309
	313.076
	0.574
	312.502
	-3.807

	
	Aug’18
	310.849
	322.184
	322.519
	0
	322.519
	0.235

	
	Sept’18
	300.822
	302.037
	309.512
	0
	309.512
	7.475

	
	Oct’18
	310.849
	295.91
	298.996
	0
	298.996
	3.086

	
	Nov’18
	300.822
	248.651
	292.634
	0
	292.634
	43.983

	
	Dec’18
	310.849
	255.345
	276.639
	0
	276.639
	21.294


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
     Members may please discuss.

E. Energy Generation / Import up to the month of December’18
Figures in MU  
	Month
	Thermal

(TTPS+IbTPS)
	OHPC 
& MKD
	CGP Support
	IPP Inj.
	RE
	ISGS
	Total

	April’18
	535.100
	421.700
	362.530
	198.950
	9.690
	872.260
	2400.240

	May’18
	567.940
	573.520
	313.169
	199.230
	14.390
	1066.640
	2734.893

	June’18
	485.813
	481.601
	219.983
	203.230
	11.897
	1084.870
	2487.390

	July’18
	440.179
	421.582
	213.953
	193.928
	10.102
	1292.141
	2571.886

	Aug’18
	473.390
	689.310
	163.300
	202.940
	13.680
	1621.990
	3164.600

	Sept’18
	454.183
	1037.515
	203.086
	136.688
	13.196
	1012.434
	2857.102

	Oct’18
	483.538
	927.724
	227.618
	191.329
	13.269
	1303.948
	3147.426

	Nov’18
	500.555
	406.963
	242.821
	255.937
	12.645
	1196.275
	2615.196

	Dec’18
	554.605
	322.626
	266.526
	179.021
	16.591
	852.921
	2188.461

	Total
	4495.303
	5282.541
	2212.986
	1761.253
	115.46
	10303.479
	24167.194


F.  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of December’18 are as detailed:
	Month
	Total Generation
	Odisha Drawl
	AP Drawl

	
	MU
	Avg (MW)
	MU
	Avg (MW)
	MU
	Avg (MW)

	Apr’18
	37.162
	51.610
	18.613
	25.851
	16.943
	25.532

	May’18
	48.888
	65.700
	22.424
	30.140
	24.492
	32.919

	June’18
	43.185
	59.980
	19.692
	27.350
	21.635
	30.048

	July’18
	45.146
	60.680
	20.894
	28.083
	22.148
	29.769

	Aug’18
	51.319
	68.977
	23.507
	31.595
	25.708
	34.554

	Sept’18
	45.449
	63.123
	20.039
	27.032
	23.324
	32.394

	Oct’18
	50.184
	69.700
	22.268
	30.927
	25.721
	35.726

	Nov’18
	49.688
	69.011
	21.964
	30.506
	25.621
	 35.585

	Dec’18
	52.772
	70.930
	24.878
	33.438
	25.653
	34.479

	Total
	423.793
	
	194.279
	
	211.245
	


Drawl of State share power from Machhakund is decreasing for the current Financial Year. Southco may add more feeders to Podagada S/s. In the last PSOC meeting Southco stated that the contractor is not turning up for the work. 
SOUTHCO may deliberate.
G. Under Frequency Relay operation in OPTCL System during the month of Dec’18.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of December’18.
H. Status of Open Access applications up to the month of December’2018
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’18
	26
	79
	0
	31
	136
	26
	76
	0
	31
	133
	3

	2
	May’18
	59
	90
	0
	26
	175
	59
	89
	0
	26
	174
	1

	3
	June’18
	14
	57
	0
	30
	101
	14
	57
	0
	30
	101
	0

	4
	July’18
	18
	145
	0
	26
	189
	18
	145
	0
	26
	189
	0

	5
	Aug’18
	26
	90
	0
	37
	153
	26
	90
	0
	37
	153
	0

	6
	Sept’18
	25
	97
	0
	32
	154
	25
	97
	0
	32
	154
	0

	7
	Oct’18
	45
	60
	0
	28
	133
	45
	60
	0
	28
	133
	0

	8
	Nov’18
	39
	95
	0
	35
	169
	39
	95
	0
	35
	169
	0

	9
	Dec’18
	36
	68
	0
	28
	132
	36
	67
	0
	27
	130
	2

	
	Total
	288
	781
	0
	273
	1342
	288
	776
	0
	272
	1336
	6


PART C – Issues discussed in the 153th  OCC meeting of ERPC held on 21.01.2019
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
149th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	30.11.18
	162.5 Cr.


	38.09Cr. Requisition for 11.00 Cr placed.
	90% equipment installed and commissioned. Stn Tfr and some measuring instruments are under tendering process.



	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.22 Cr
	Request for 10% grant already submitted. Agreement  signed
	Tender floated

	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov18
Chiplima

Dec 2018
	22.35 Cr.
	2.235 Cr
	Placed work order for Balimele

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 


	27-07-18
	
	31.94 Cr
Ested. Cost. Approved amount 30.26 Cr. Grant amount 27.23 Cr.
	27.23 Cr.
	Agreement signed and sent to NLDC for signature. Tender floated.

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost. 2.93 Cr recommended by Appraisal committee.
	
	Approved by Appraisal committee. Forwarded to CERC for concurrence.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	12.03.2018  Date of submission 
	
	41.1 Cr

Estt cost
	
	Compliance to TSEG observation submitted. Audit observation has been sent to NLDC. 


      CGM (O&M) / OHPC/ SLDC may please update the status.
C.2: Evacuation of Power from OPGC expansion project-modification of network configuration-GRIDCO   
Two units of Odisha Power Generation Corporation (OPGC) with 660 MW capacityeach are going to be commissioned shortly. Both the generating units are under advanced commissioning stage and most likely attain COD within April-2019. Entire capacity (2 x 660 MW) is meant for the State of Odisha as per the Government of Odisha notification. OPGC & GRIDCO are in the process of executing the PPA for entire capacity. Under such arrangement OPGC Station shall become State embedded unit. 

Power evacuation scheme has been proposed with SPLIT BUS arrangement at IbTPS (OPGC) switchyard with one unit (Unit # 3) connected to STU system at Lapanga Sub-station through 400 kV D/C line and the other unit (Unit # 4) shall be connected to 765 kV / 400 kV Jharsuguda PG through 400 kV D/C line. 

Presently, both transmission systems are already charged under SPLIT BUS condition.  

In view of the above, it is felt necessary to operate both units (2 x 660 MW) in COMMON BUS mode having connectivity with both STU & CTU system for a reliable, efficient, secured & stable grid. 

In the above common bus arrangement as proposed the 400 kV IbTPS-Jharsuguda PG D/C line needs to be declared as the interstate tie lines of Odisha. 

OPTCL has conducted the System Study (Short Circuit & Load Flow Analysis) under COMMON BUS mode and found technically suitable within permissible limits. 

The Committee may deliberate and finalize the common bus arrangement for evacuation of power from OPGC (2 x 660 MW) new plant.
It was decided in the OCC meeting that the matter shall be referred to Standing Committee of CEA for technical approval 

GRIDCO may explain.  
C.3: Islanding Scheme of IB-TPS 

Special Meeting on Islanding Scheme of IB-TPS held at ERPC, Kolkata on 12th December 2018 at 11:00hrs. Minutes of the meeting are enclosed at Annexure-B7. In the meeting, OPTCL and OPGC were advised to present final islanding scheme in the OCC Meeting of January 2019.
OPTCL deliberated to complete all work by February’2019. OPGC stated that they will fine tune the scheme during shut down of their unit in the month of June’2019.  

OPTCL and OPGC may deliberate.   
C.4:  Crossing of OPTCL transmission line under 400kV DC Baripada-Dubri/Pandiabili (Earlier Baripada-Mendhasal line) without taking approval from POWERGRID--Powergrid 

M/s OPTCL has sent a letter ref no:Tech-303-11 date 03.01.2018 regarding approval for passing of 132kV Udala LILO line  under 400kV Baripada-Mendhasal D/C between Location 112-113-114 near Manitri, Dist. Mayurbhanja. 

Accordingly, mail was sent to M/s OPTCL on dt 24/04/2018 for clarification before giving consent for stringing of the line. But without further communication M/s OPTCL has constructed the line which pass on both side of TOWER Loc 113.The distance of the Conductor from the Tower is barely 10mtrs. Because of this maintenance activity of the line at the Tower Loc. 113 will be extremely difficult. Therefore, it is requested to M/s OPTCL to take up the matter seriously and divert the line in such a way that there should not be any hindrance to POWERRID during maintenance activity. After getting due approval from POWERGRID, OPTCL is requested to divert the line. OCC suggested that Powergrid may write to OPTCL for a reply.
O&M may deliberate

C.5: Load Generation Balance Report (LGBR) for the year 2019-20 

The draft LGBR has been prepared by ERPC after the detailed discussion with the constituents of Eastern Region in the meeting on finalization of draft Load Generation Balance Report (LGBR) for the year 2019-20, which was held at ERPC, Kolkata on 18.12.2018. Major observations are given below:  

1. The following major thermal units shutdown were deferred from summer months considering strong reservations by a no. of distribution utilities, which have their major share: 

· NTPC Barh STPSU#4(660MW)(01.03.19to 04.05.19)to 01.11.19 to 04.01.20 (65 days continuous) 
· NTPC Barh STPS U#5 (660MW)(01.03.20 to 04.05.20) to 15.01.20 to 19.03.20 (65 days continuous)
· NTPC FSTPSU#6(500 MW)(01.06.19 to 05.07.19) to 01.11.19 to 05.12.19 (35 days continuous) 
· NTPC TSTPS      U#1 (500 MW)(22.07.19 to 25.08.19) to 01.12.19 to 04.01.20(35 days continuous)   
· DVC KodermaU#1(500 MW)(01.04.19 to 06.05.19 to 16.01.20 to19.02.20 (35 days continuous) 
· MPL   Unit # 1 (525 MW)   (25.05.19 to 07.06.19) to 01.11.19 to 14.11.19 (14 days continuous) 

Besides, the above revised outage programme, some of the NTPC units of Farakka, Kahalgoan STPS and Kolaghat & Santaldih TPS of WBPDCL due to Boiler licence renewal were allowed to shift 10-15 days as per deliberations. The maintenance schedule of thermal generating units in ER during 2019-20 as agreed and finalised in the LGBR meeting is shown in Annexure-B10.1.  

Thereafter, NTPC has requested for changes in the planned maintenance in LGBR. 

2. ABSTRACT OF SYSTEMWISE UNRESTRICTED PEAK DEMAND (MW)                       

  The month wise demand (MW) (unrestricted) of the constituents as projected considering the actual demands is being met during the current months, were analysed and corrected during the meeting. The demand forecast of the constituents and cumulative regional demand based on generation availability and diversity factor were worked out and assessed in the range of 21550 MW to 24820 MW. The regional monthly peak surplus or deficit taking into account of export to neighbour countries worked out to be in the range of600 MW to700 MW. However, Bihar and Jharkand states remained in deficit peak demand on monthly basis due to less generation availability from their own sources.  

3 ABSTRACT OF SYSTEMWISE UNRESTRICTED ENERGY REQUIREMENT  (MU)   

The expected monthly energy requirement (MU) of the constituents against energy availability indicated that, except Bihar and Jharkand states, most of the constituents would meet the energy requirement and there would be surplus of energy in ER on monthly basis. The energy availability from the new units of NTPC and constituents as indicated have been considered. This would lead to energy surplus in ER. The energy availability would vary in between 13800  to 16700 MU on monthly basis considering monthly scheduled maintenances of generating units. 

4 SCHEDULE OF COMMISSIONING OF NEW GENERATING UNITS IN THE CONSTITUENT SYSTEMS 

The following units are expected to commission during 2019-20 and their energy availability (MU) have been taken into consideration as agreed by the constituents: 

SYSTEM  
THERMAL UNITS  
CAPACITY(MW)  
EXPECTED DATE COD 
NTPC 

DARLIPALLI # 1            
800 


01.04.2019  
DARLIPALLI #2            
800  


01.10.2019 
BRBCL
NABINAGAR
 
U#3            

250 


01.04.2019 
ODISHA 
IB TPS U# 3            

660    


01.04.2019  
IB TPS U#4            

660 


01.04.2019 
BIHAR 
BARUNI 
U#8            


250 


01.07.2019 
TOTAL             



3420  

The final LGBR of ER would be subsequently prepared and published on receipt of Annual Generation Target from CEA/MOP.   

Members may discuss.  

C.6: Requirement of 132kV bay at 400/220/132kV Baripada S/s---OPTCL 

OPTCL informed that at present two no. of 132 kV Bays are available at Kuchei. The Kuchei­ Rairangpur 132 kV S/C line is LILO at Bangiripushi. The loads of connected substation are as follows:  

Bangiriposi-8  MW, Rairangpur-28 MW, Karanjia-21 MW, Dhenkikote-10 MW. Thus the 132 kV S/C line is loaded 67 MW. In case of outage at Joda the Polasponga load which is around 40 MW is catered through this line breaching the thermal limit of the line. 

OPTCL requested for a new 132 kV Bay at Kuchei for 132KV Kuchei­ Bangiripushi line to limit the line loading as well as to meet the n-1 contingency. 

In 152nd OCC, OPTCL explained the requirement of 132kV bay at 400/220/132kV Baripada S/s with a detailed presentation. OPTCL requested for a new 132 kV Bay at Baripada for 132KV Kuchei­ Bangiripushi line to limit the line loading as well as to meet the n-1 contingency. OPTCL informed that sufficient space is available at 400/220/132kV Baripada S/s for construction of two 132kV bays.  

Powergrid informed that space is available but it is allotted for construction of bays for new 220/132kV Transformer.  

OCC advised OPTCL and Powergrid to visit the site and place the details in next OCC Meeting. However OPTCL may approach the Standing Committee of CEA for approval.    

CGM (O&M) / CGM (Const) may deliberate.
C.7: Use of Polymer Insulators in the transmission lines--CEA 

CEA vide letter dated 28th November 2018 informed that many representations have been received in CEA as well as VIP references from Ministry of Power from various manufacturers and associations highlighting the issue of use indiscriminate use of polymer insulators which are mostly imported from China leading to closure of indigenous porcelain manufacturing industry. To resolve the issue, a meeting was held in CEA on 25.5.2018 with various stakeholders to deliberate on the issue. 

PGCIL vide letter no. C/CTU/E/02/TBCB dated 24.10.2018, indicated that on the directions of RPC's, only polymer type insulators are being used in the new transmission lines of PGCIL traversing through states in Northern and eastern Regions. Moreover, PGCIL is replacing the porcelain insulators with polymer insulators in the existing transmission lines of the region. PGCIL has categorically mentioned that the same has been done in accordance with the decision taken in the meetings with Regional Power Committees. 

It is to mention that CEA has issued the Regulations and there are specific provisions regarding use of porcelain (disc type I long rod) and polymer insulators. Regulation Clause No. 89(1)(f)(i) of CEA (Technical Standards for Construction of Electrical Plants and Electric Lines) Regulations 201 0, may be referred in this regard. 

It may be clarified whether decision of use of polymer insulation in place of porcelain insulator was taken for some particular lines or locations. Considering the sensitiveness of issue, the same may also be discussed in respective RPC meetings and a balanced approach may be adopted for all future lines. 
In 152nd OCC, Powergrid informed that they are following the “Regulation Clause No. 89(1)(f)(i) of CEA (Technical Standards for Construction of Electrical Plants and Electric Lines) Regulations 2010”.  

After detailed deliberation, OCC decided the following: 

· Powergrid should submit the details of the progress made towards insulator replacement work and quantity of polymer insulators received till date 

· Powergrid should submit the details of order placed for the polymer insulators, which are scheduled to be delivered in near future 

· The issue would be placed in TCC/ERPC Meeting for detailed discussion

Powergrid should not place any fresh order for polymer insulators till further decision by TCC/ERPC 

Reply received from Powergrid Odisha Projects is enclosed at Annexure-B13.  

In the 128th PSOC meeting OPTCL suggested to use polymer insulators in saline effected areas.

O&M may deliberate.
C.8: Review of Cyber Security Works/Activities- CEA 

CEA vide letter informed that Secretary (Power) is going to review the cyber security related works /activities being carried out in Power Sector. In this regard, it is requested to provide the State wise status on following action points pertaining to cyber security at the earliest: 

1. Appointment of organization-wise Chief Information Security Officers and its status
2. Identification of organization-wise Critical Infrastructure and its status 
3. Preparation of organization-wise Crisis Management Plan and its status 
4. Status of Cyber Security Mock Drill activity in coordination with CERT-In 
5. Status of Training / Workshops on Cyber Security organized / participated by power sector entities 
6. Status of action taken on CERT-In / NCIIPC advisories 

In 148th OCC, all the constituents were advised to send the latest status to mserpc-power@nic.in within a week.   

The same has been received from WBSETCL and OPTCL only.
In the 127th PSOC meeting POWERGRID made a presentation on Cyber Security. 
In the 128th PSOC meeting IT stated that audit will be started from January’2019.

IT may update 
C.9: Submission of static data for preparation of a report on coal fired stations in the country--ERLDC 

One internal committee has been formed by POSOCO to prepare a report on coal fired stations in the country, which will be submitted to the FOLD &FOR, at a later stage. Similar reports have already been prepared by POSOCO for hydro, gas and RES plants, which has been widely appreciated in different forums like FOLD & FOR.  

To prepare this report, some static data (commercial, technical, environmental & general) in proper format for all coal fired stations (ISGS, IPP and State Generators) of capacity >= 200 MW need to be submitted to ERLDC so that the compilation and subsequent analysis of data of thermal generators on an all India basis could be made within stipulated time period. 

The format for data submission was intimated to all generators and state SLDCs via email. Till date only GMR, Adhunik, MPL and Sagardighi have submitted their static data. 

ISGS (NTPC), IPP and State Generators of Eastern Region are requested to kindly accord high priority for submitting the static data to ERLDC in erldcso@posoco.in for preparation of the report within stipulated period. 

Nodal coordinators for this Process from ERLDC are: 

1. Shri Biswajit Mondal, Sr. Engineer, Mob No: 9903329271 2. Shri Chandan Mallick, Sr. Engineer, Mob No: 9007059660 

In 152nd OCC, ERLDC updated the following generating stations have not submitted static data for preparation of report on coal firing stations: 

1.    IB thermal stage -1 

2.    TTPS (Odisha) 

3.    Talcher STPP

 4.    Santaldih TPP

 5.    Budge-Budge TPP 

6.    Tenughat TPP 

OCC advised above thermal generators to submit the relevant information to ERLDC at the earliest.
All Thermal Generators may comply.

C.10: Operation Eastern Regional grid from ERLDC back up control Centre at, NLDC, New Delhi as a part of Disaster Management: ERLDC 

As a part of disaster Management preparedness, the control room shift operation of ERLDC is planned to be operated from its back up control Centre at NLDC, New Delhi tentatively on 08th February, 2019 (one shift only). During this process all control room shift operation regular activities viz. real time supervision and monitoring of Eastern Region system, switching/ outage co-ordination of transmission elements, all scheduling activities and preparation of different reports shall be performed from back up ERLDC Control Centre from NRLDC, New Delhi.  

The contact numbers of back-up ERLDC would be informed to all ER constituents prior to such exercise. 

Members may please note. 
C.11: Updation of Restoration procedure of Eastern Region--ERLDC 

In compliance with clause 5.8 (a) and (b) of the present IEGC, The regional Restoration Procedure has to be developed and updated annually by RLDC in consultation with NLDC, all users, STU, SLDC, CTU, RPC Secretariat of the region. For fulfillment of same, Draft copy of “Black Start and Restoration Procedure” was mailed on 11th Jan 2019 for review and feedback from stake holders. Based on feedback and updated information same will be finalized by 31st Jan 2019. 

All regional entities of Eastern Region are therefore requested to furnish their observations (if any) positively by 25-01-19.
Members may discuss 

C.12: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC 

As a National Grid operator, POSOCO is continuously working for ensuring reliability and security of the Grid. With penetration of more and more renewable energy source the task is becoming complicated day by day.  An accurate dynamic modeling of the National Grid needs modeling of conventional as well as renewable / distributed generation sources. World Bank has engaged Digsilent as consultant for assisting POSOCO for building dynamic model of the Grid. A guideline for dynamic data collection has been developed in consultation with Digsilent Pacific team.    All the utilities are requested to collect data from the grid scale renewable power plants as well as from conventional power plants under their jurisdiction and submit the same to ERLDC/ERPC as early as possible. 

Members may discuss.
C.13: Status of UFRs healthiness installed in Eastern Region 

UFR Healthiness Certification for the month of December, 2018 has been received from CESC, WBSETCL, DVC, BSPTCL and JUSNL. 

OPTCL may update.
C.14: Implementation of Automatic Demand Management Scheme

The latest status along with proposed logic as follows: 
	Sl. No
	State /Utility
	Logic for ADMS operation
	Implementation status/target
	Proposed logic (if different from under implementation logic

	1
	Odisha
	1. System Frequency < 49.9 Hz 
2. Odisha over-drawl > 150 MW
3. DISCOM over-drawl > (40 MW) 
	10 Months

Sent for PSDF approval
	Logic 2 and 3 is AND or OR, in case it is AND then ADMS may not operate when DISCOMs are in schedule but GRIDCO is over drawing due to less generation at State embedded generators.


In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 123rd PSOc meeting SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval

In the 124th PSOC meeting SLDC stated that the revised estimate has been approved in the BoD.

In the 126th PSOC meeting SLDC stated that CERC approval is awaited for tendering.

SLDC stated that CERC approval is awaited for tendering.

SLDC may deliberate the status

C.15: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 128th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by Dec’18. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by March’19.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	220 kV S.C line and Keonjhar S/S (220/33 kV) charged on 31.12.2019.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	March’2019 


CGM (Cont) / CGM (O&M) may update

C.16: Update on status of telemetry  

CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed  NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action.

In the 149th OCC, ERLDC stated that status of Breaker & isolator of NALCO & JITPL are not available.

In the 126th PSOC meeting Telecom stated that Service engineer of the company provided NALCO internal SCADA has arrived but could not rectified the data communication of NALCO to SLDC. Telecom suggested that NALCO may go for optical fibre for uninterrupted data communication instead of PLCC.

In the 127th PSOC meeting Telecom stated that the data communication is not consistent. NALCO stated that they are agreeing to go for optical fiber. Telecom may forward their suggestion and offer for taking necessary action by NALCO. It was suggested that NALCO may coordinate with Telecom in this regard.
In the 128th PSOC meeting SLDC stated that data communication from Narsingpur S/s is not in place. Telecom stated that provision for laying optical fibre in Bhanjanagar-Meramundali line has been kept in PSDF scheme. However, if wave trap foundation will be done at Narsingpur S/S, the data communication can be established. It was suggested that construction wing may intimate the installation of new projects to the Sr. G.M (Telecom) as well as SCADA group of Telecom in advance. NALCO representative was not present to deliberate their communication status.

Const./Telecom / NALCO may update the status

C.17: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2018-19 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2018
	Done on 28.06.2018
	Last week of January 2019
	January’2019

	3
	Rengali
	2nd week of June 2018
	Done on 18.08.2018
	Last week of November 2018
	January’2019

	4
	U. Indravati
	3rd week of June 2018
	December’18
	2nd week of February 2019
	

	6
	Balimela
	3rd week of October  2018
	Done on 21st Dec’18
	1st week of March 2019
	

	9
	Burla
	Last week of June 2018
	Done on 07.06.2018
	Last week of February 2019
	


SLDC / OHPC may deliberate

C.18: Submission of Thermal Loading of Transmission line and associated terminal equipment by ISTS licensee  

In line with the MoM of 4th NRCE Meeting dt.03-11-14 and “Operational Guidelines for determination Of TTC, ATC and TRM for the Short-Term Horizon (0-3 Months)” published by NRCE dt.20-02-15, thermal limit for transmission line has to be used for calculation of ATC/TTC. However, the thermal loading of transmission line depend on the Maximum Conductor Temperature, End equipment thermal rating. This has to be submitted by the Owner of the equipment. Further, the equipment owner also has to confirm that relay setting has been aligned so that the line can be operated up to its thermal limit. In the absence of complete details, ERLDC is utilising the data from the CEA Planning Criteria  for thermal rating as given below : 

	Conductor Type 


	Ampacity per 

conductor(A)* 


	Thermal loading 

limit of line (MVA) 



	765 kV Quad ACSR_Bersimis
	732
	3880

	765 kV HexaACSR_Zebra
	560
	4452

	400 kV Twin ACSR_Moose
	631
	874

	400 kV Quad ACSR_Moose 
	631
	1749

	400 kV Quad ACSR_Bersimis 
	732
	2029

	400 kV Triple Snowbird
	630
	1309

	400 kV Twin ACSR_Lapwing
	773
	1071

	220 kV Single AAAC_Zebra
	557
	212

	220 kV Single ACSR_Zebra 
	560
	213

	220 kV Twin ACSR_Moose 
	631
	481

	132 kV Single ACSR_Zebra 
	560
	128

	132 kV Single ACSR_Panther 
	366
	84


*Ambient and Maximum conductor temperature are taken as 45°C and 75°C respectively. Apart from above specifically mentioned in CEA transmission planning criteria following loading limit is considered for HTLS line while calculating ATC/TTC 

	Conductor Type 


	Ampacity per 

conductor(A)* 


	Thermal loading 

limit of line (MVA) 



	400 kV Twin HTLS
	1262 
	1750

	220 kV Single HTLS 
	1020 
	390

	132 kV Single HTLS
	732
	168


In view of this, it is desired that all ISTS Licensee and STU (for 400 kV and important 220 kV lines) may kindly submit the following details to ERLDC for utilization in ATC/TTC calculation: 
a)Transmission line wise Ampacity and Thermal loading along with Maximum Conductor Temperature and conductor type.
b) End Equipment Rating and 
c) Confirmation whether the relay setting has been adopted in line with the thermal rating of the line 

d) Any constraint during thermal loading of line  

In 152nd OCC, ERLDC informed they received the details only from DVC. 

OCC advised all the other ISTS licensees and STUs to submit the relevant data to ERLDC and ERPC. 
In the 128th PSOC meeting it was suggested that Corporate Planning wing may intimate the required data to ERPC/ERLDC.

Sr. G.M (CP) may deliberate

C.19: Prolonged outage of Power System elements in Eastern Region
Thermal Generating units

	Sl. No
	Station
	Location
	Owner
	Unit No
	Capacity (MW)
	Reason
	Outage date

	1
	Vedanta
	Odisha
	GRIDCO
	2
	600
	Turbine bearing vibration
	23.11.18

	2
	Burla
	Odisha
	OHPC
	1
	37.5
	R&M
	25.10.16

	3
	Burla
	Odisha
	OHPC
	2
	37.5
	R&M
	16.10.15

	4
	Burla
	Odisha
	OHPC
	4
	37.5
	Annual Maintenance
	25.10.18

	5
	Burla
	Odisha
	OHPC
	6
	37.5
	R&M
	16.10.15

	6
	Balimela
	Odisha
	OHPC
	1
	60
	R&M
	05.08.16

	7
	Balimela
	Odisha
	OHPC
	2
	60
	R&M
	20.11.17

	8
	Balimela
	Odisha
	OHPC
	5
	60
	Annual Maintenance
	12.10.17

	9
	U. Kolab
	Odisha
	OHPC
	2
	80
	Repair of MIV & DT gate
	25.08.17

	10
	U. Kolab
	Odisha
	OHPC
	3
	80
	Problem in bypass valve
	

	11
	Chipilima
	Odisha
	OHPC
	1
	24
	Flood water in rush
	21.07.18

	12
	Rengali
	Odisha
	OHPC
	1
	50
	Annual Maintenance
	31.10.18

	13
	Indravati
	Odisha
	OHPC
	4
	150
	Sheer pin failure
	


In the 128th PSOC meeting OHPC stated that # 5 of Balemela and # 2 of Upper Kolab is expected to be synchronized by end of December’2018 & January’2019 respectively, while # 4 of Upper Indravati by end of December’2018.

OHPC may deliberate
C.20: Restricted Governor /Free Governor Mode Operation of generators in ER 

CERC vide their letter dated 05-06-2017 desired to know the present status of RGMO/FGMO response of all eligible thermal and hydro units. Accordingly ERLDC vide letter no.ERLDC/SS/FGMO/2017 dated 07-06-17 requested all concerned power stations and SLDCs to provide updated status of FGMO/ RGMO of units under their control. 

The latest status of the RGMO/FGMO of ER generators is enclosed in Annexure-E1. 

Generators may update. 

C.21: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA. 

In 142nd OCC, ERLDC informed that, in line with Enquiry Committee Recommendation, cyber security audit is being conducted on regular basis for SCADA system installed at ERLDC and SLDC as well but cyber security audit for telecom infrastructure installed in Eastern Region is not being carried out.  

OCC advised all the constituents to conduct the cyber security audit on telecom infrastructure installed in Eastern Region. It is further advised that compliance / mitigation of the points observed during the audit should also be completed for improvement of the telecom infrastructure in ER. 

In 37th TCC meeting, it was decided that a workshop would be conducted by CEA at ERPC for further benefit of ER Constituents.  

In 144th OCC, ERLDC informed that they have already conducted a workshop with the help of NPTI, Durgapur on 21st March 2018. 

A workshop on cyber security was conducted by CEA at ERPC, Kolkataon 09-05-2018.  

As suggested by CEA, a format would be circulated among ER constituents for furnishing the information of their respective systems for discussion in OCC Meeting. The format is enclosed at Annexure-E2. 

OCC advised all the constituents to submit the information to ERPC as per Annexure-E2.  

C.22: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.  

· As per the information received from the constituents the following generators certified with IS 18001:  

· All NTPC stations in Eastern Region  

· Teesta, NHPC 

· All OHPC generating units  

· All CESC generating units  

· All units of WBPDCL 

· DGPC units 

In the 117th PSOC meeting CGM (O&M) stated that draft project report for Mendhasal S/S has been submitted to BIS. The report will be approved in the meeting to be conducted by them.

In the 122nd PSOC meeting CGM (O&M) stated that Audit team is expected soon.

In the 123rd PSOC meeting CGM (O&M) stated that the report is yet to be received.

In the 126th PSOC meeting O&M stated that training has been completed. After compliance of the observations, certificate will be issued. 
In the 127th PSOC meeting O&M stated that internal Audit will be started in the month of December.

In the 128th PSOC meeting O&M stated that first stage of audit completed for 6 Nos. of S/Ss.
O&M may update

PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of December’18:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	3.692
	0.633

	2
	WESCO
	0
	3.545
	0.623

	3
	NESCO
	0
	24.346
	5.899

	4
	SOUTHCO
	0
	21.294
	8.339

	
	Total
	0
	52.877
	


It is noticed that all the DISCOMs were over drawn during the month. SOUTHCO has deviated 8.339% followed by NESCO 5.899% from the scheduled energy while WESCO and CESU have deviated 0.623 % & 0.633 % respectively. DISCOMs may forecast their drawal in realistic approach to minimise deviation.

SLDC/ Discoms may please deliberate.
D.2: Communication issues 
The status of data communication from CGPs as deliberated in the 124rd PSOC meeting meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	2
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. 
In the 123rd PSOC meeting it was deliberated that RT&C have sought some information from Telecom wing which will be intimated. NALCO stated that due to problem in their internal communication system, data communication to SLDC is being interrupted.
In the 124th PSOC meeting Telecom stated that communication system for Paradeep area industries will be completed by September’2018. Telecom was advised to give a reply to the information sought by RT&C. 

In the 125th PSOC meeting Telecom stated that the information sought by RT&C will be forwarded soon.
In the 126th PSOC meeting it was decided that SLDC shall convene a meeting with Telecom, GCC & RT&C and discuss the issue for filing case before the OERC.

A meeting was convened between SLDC, Telecom, GCC, RT&C, NINL & IRE Ltd on dt.15.01.2019 at SLDC conference hall to discuss the communication issue. Representative of IRE, SLDC, GCC and Telecom were attended the meeting. IRE deliberated that presently CB, CT & CVT are not installed at their end. Tendering for procurement of CB, CT & CVT have already been done, which will be expected by end of April’2019. Due to space constraint at IRE Switch yard, installation of the equipment may not be possible, unless the Switchyard is modified. For modification they may need the help of OPTCL. It was suggested by SLDC that IRE may approach Sr. G.M (O&M), Zone-1, OPTCL in this regard. Simultaneously, they also to write Sr. G.M (Telecom), OPTCL for preparing estimate for extending data communication from their end.

NINL was not present in the meeting.  

Members may discuss 
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 119th PSOC meeting IT stated that Parameters of 16 Nos meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
In the 123rd PSOC meeting IT stated that out of 840 Nos interface meters connected with AMI, 750 Nos are reporting at present. The newly replaced meters are not reporting. 2 Nos. of meters has sent to M/s SECURE meters for study.

In the 124th PSOC meeting O&M stated that SLDC may intimate the list of defective energy meters to O&M on monthly basis for necessary action. IT may ask TCS to co-ordinate with Secure meters and develop a driver data extraction  
In the 127th PSOC meeting IT stated that TCS is demanding Rs. 6.5 lacs for developing the required software. The proposal is placed before the management for approval

In the 128th PSOC meeting IT stated that the memorandum has been placed before the PSC

IT may update the status
D.4: Commissioning of 220 kV Tarkera-RSP 2nd D/C line-RSP Agenda

Construction work of 220 kV 2nd D/C line from Tarkera to RSP in under progress and expected to be completed by mid of April’2019. OPTCL and other involving utilities are requested to provide necessary guideline for commissioning / charging of the line.

RSP may deliberate  
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Expected to be completed by Dec’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	January’2019

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	December’18

	4
	220/33 kV, 2x20 MVA Baliguda S/S
	July’19

	5
	220/33 kV, 2x20 MVA Kalimela S/S
	July’19

	6
	220/33 kV, 2x20 MVA Kasipur S/S
	January’2019

	7
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	Charged on 31.12.2019 with 2x20 MVA Trf.

	8
	220/132 /33 kV, 2x100 MVA Aska S/S
	March’19

	9
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’19

	10
	220/132/33 kV Jayapatana S/S(320 MVA)
	July’19

	11
	220/132 kV Pratapsasan S/S(320 MVA)
	Dec’19

	12
	220/132 kV Kesinga S/S (320 MVA)
	March’19

	13
	132/33 kV Betanati S/S
	March’19

	14
	132/33 kV R.Udyagiri S/S
	March’19

	15
	132/33 kV Chikiti S/S
	(Bus test charged on 11.09.18)


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement.
CGM (Construction) / DISCOMs may please deliberate the status.
E.2: Major Events in the month of December’18
1.   On 22.12.2018 at 04:05 Hrs 132 KV Solar Bay & 132 KV Tentulikhunti - Charamula fdr charged for evacuation of power from 40 MW Solar  power plant developed by M/S Vento Energy Infra Pvt Ltd.
2.   On 29.12.2018 At 11:47 Hrs - 160 MVA Auto Trf - II  at 220/133 KV Grid S/S, New Bargarh charged.
3.   On 31.12.2018 At 19:15 Hrs -   220KV Keonjhar (PG) - 220 KV Keonjhar(OPTCL) ckt - I charged. 2 nos of 20MVA 220/ 33 KV Power Transformers at Keonjhar(OPTCL), GIS  S/S also charged.                     

Members may note

E.3: Important Grid Incidences during the month of December’18.
On 25.12.2018 at 12:46 Hrs-   Y-Phase of 220 KV Transfer Bus Conductor (between 220 KV Budhipadar - Tarkera Ckt-II & 220 KV Budhipadar - Bhusan Ckt-I)  fell on 220 KV Budhipadar - Lapanga Ckt-I & CKt-II  & TBC side Pipe Bus, due to disc insulator string failure resulting tripping of 220 kV incomer ckts. The bus bar protection is in OFF condition & only 220KV Main Bus – I in service. Main Bus –II is under shutdown since 24.12.2018 for Annual Maintenance. Unit #1 & #2 of IBTPS tripped due to over frequency . Total black out of 220 kV System occurred at Budhipadar. Power supply extended form Lapanga & Jharsuguda end through 132 kV system and met partial load.
O&M may deliberate
E.4: Outage of major transmission Elements during the month of December’18. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration

Dt/time
	Reason

	1
	132 KV Chhatrapur _ Balugaon feeder
	01.12.2018 / 02:00 
	01.12.2018/ 17:43
	Cross arm damage at Loc No - 369



	2
	132 KV Rajgangpur - OCL Feeder


	17.12.18 / 21:16


	25.12.19 / 16:29
	Heavy sparking at OCL switchyard 



	3
	Auto _I of Tarkera Grid S/S
	18.12.18

/ 03:47
	18.12.18

/ 16:49
	Buchholtz relay operated

	4
	220 KV Budhipadar - Lapanga-II
	25.12.18

/ 12:46
	26.12.18

/ 18:06
	Y-Phase of 220 KV Transfer Bus Conductor (between 220 KV Budhipadar - Tarkera Ckt-II & 220 KV Budhipadar - Bhusan Ckt-I)  fell on 220 KV Budhipadar - Lapanga Ckt-I & CKt-II Line  & TBC side Pipe Bus due to disc insulator string failure

	5
	220 KV Budhipadar - Lapanga -I
	25.12.18

/ 12:46
	26.12.18

/ 18:58
	


O&M may discuss
E.5:  Review of Outage Program of State Generators / Transmission elements for the month of February’19:
Tentative Outage programme for State Generators for the month of February’2019 
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 4
# 5

# 6
	14.03.18 to continue
25.10.18 to continue
25.10.16 to continue

16.10.15 to continue
	T&G coupling cover water leakage
Annual Maintenance

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to continue
	Under R,M & U

	3
	Balimela
	# 1
# 2
# 8
	05.08.16 to continue
20.11.17 to continue
21.01.19 to 21.02.19
	Under R,M & U

Programming for R&M
Annual Maintenance

	4
	Rengali
	# 2

# 4
	12.12.18 to continue
17.12.18 to 31.01.19
	Replacement of Runner disc.

A.M & DVR replacement

	5
	Upper Kolab
	# 1
# 2
# 4
	26.01.19 to 25.02.19
28.05.17 to 25.01.19
01.02.19 to continue
	Annual Maintenance
Upstream leakage and intake gate problem
Capital maintenance work

	6
	Upper Indravati
	# 3
	01.02.19 to 28.02.19
	Annual Maintenance


OHPC may deliberate
E.6: Generation Program for the month of February’19.
Generation schedule for the month of February’19 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.01.19
	Reservoir Level as on 01.01.18
	MDDL
	High Flood    Reservoir Level

	
	Feb’19
(1st fortnight)
	Feb’19
 (2nd fortnight)
	
	
	
	

	HPS-I, Burla
	20
	20
	625.02 ft.
	626.85 ft.
	590 ft.
	630 ft.

	HPS-II, Chiplima
	10
	10
	-
	-
	-
	-

	Balimela
	250
	250
	1507.70 ft.
	1479.00 ft.
	1440 ft.
	1516 ft.

	Rengali
	40
	40
	117.79 mtr.
	122.66 mtr.
	109.72mtr 
	123.5 mtr.

	U.Kolab
	100
	100
	855.07 mts.
	853.78 mtr.
	844 mtr 
	858 mtr.

	U. Indravati
	250
	250
	638.64 mtr.
	635.92 mtr.
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2743.40 ft.
	2747.40 ft.
	2685 ft.
	2750 ft.

	TOTAL
	700
	700
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

SLDC / OHPC may deliberate

E.7: Anticipated power generation and demand for the month of February’2019.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1100
	1250

	2
	WESCO
	1100
	1200

	3
	NESCO
	750
	850

	4
	SOUTHCO
	300
	350

	6
	Total Discom
	3250
	3650

	
	System Loss & others 
	150
	200

	
	Total Demand
	3400
	3850

	Availability
	
	

	1
	Hydro
	700  
	1150

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	500
	400

	4
	ISGS share (including OA& purchase)
	1100
	1200

	5
	CGP support (OA)
	350
	350

	6
	Total availability
	3400
	3850

	7
	Surplus / Deficit
	0
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (130th) PSOC meeting.
PAGE  

