                                                                                                                  
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image1.png]PTC




Agenda

for

130th Power System Operational Co-ordination Meeting

Date: 25.02.2019
Venue: Power Training Center, Chandaka, Bhubaneswar 
Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 130th PSOC Meeting to be held on 25.02.2019 at OPTCL Power Training Center, Chandaka, Bhubaneswar
A. Confirmation of the minutes of the 129th PSOC Meeting held on 29.01.2019
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2017/407 (48) dated 11.02.2019 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there is no comments, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   :  Grid Performance for the month of January’2019
C.1: Status of projects funded under PSDF scheme 
C.2: Implementation of Automatic Generation Control (AGC) in India (at Inter-State level)
C.3: Power Assistance at Kendposi GSS from OPTCL –JUSNL
C.4: Automatic Under Frequency Load Shedding (AUFLS) Scheme and Mapping of Feeders
C.5: Coal requirement for thermal power plants - MOP 

C.6: RGMO / FGMO and PSS tuning of generators in Eastern Region 

C.7: Information regarding details of existing transmission system (220 kV and above AC & DC voltage level) in Eastern Region as on 31.12.2018
C.8: Adequate measures to safeguard system(s) during planned shutdown – Proposal of POSOCO

C.9: Updation of Restoration procedure of Eastern Region--ERLDC

C.10: Ratification of projected Demand and generation for POC transmission charges and loss calculations for Q1 (2019-20)--ERLDC
C.11: Implementation of Automatic Demand Management Scheme
C.12: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s
C.13: Bypassing arrangement of LILO of 400kV Lines at Angul
C.14: Update on status of telemetry  

C.15: Replacement of non-functioning / defective meter -ERLDC

C.16: Mock Black start exercises in Eastern Region 

C.17: Submission of Thermal Loading of Transmission line and associated terminal equipment by ISTS licensee  

C.18: Delay in furnishing information to ERLDC/ERPC regarding of Commissioning of new Transmission Elements/ Generating Units within State--ERLDC
C.19: Review of Cyber Security Works/Activities- CEA
C.20: Submission of static data for preparation of a report on coal fired stations in the country--ERLDC
C.21: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC
C.22: Operation Eastern Regional grid from ERLDC back up control Centre at, NLDC, New Delhi as a part of Disaster Management--ERLDC
 C.23: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

C.24: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

C.25: Providing relevant data by Power Utilities /Stations in National Power Portal.

C.26: Commissioning of new transmission elements in Eastern Region

D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Communication issues. 
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.4: OPGC Agenda.
E.1: Commissioning status of New Transmission elements. 

E.2: Major Events in the month of January’19
E.3: Important grid incidences during the month of January’19.

E.4: Outage of major transmission Elements during the month January’19. (above 10 hrs).
E.5: Review of Outage Program of State Generators for the month of March’2019
E.6: Generation Program for the month of March’2019.

E.7: Anticipated power generation and demand for the month of March’2019.
F.1: Date and Venue of the next (131st) PSOC meeting
PART B: GRID PERFORMANCE
B. Review of Grid Performance for the month of January’19.

A. Frequency:

Hourly frequency variation for the month of January’19.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	Nov’18
	0.00
	0.00
	8.47
	79.04
	12.49
	49.95

	Dec’18
	0.00
	0.02
	11.78
	76.66
	11.54
	49.98

	Jan’19
	0.00
	0.06
	10.24
	69.48
	20.23
	49.98


Maximum & Minimum frequency during the month of Dec’18 & Jan’19.
	Month
	Freq (Hz)
	Date
	Time

	Dec’18
	Maximum –50.14
	23.12.18
	14:00 Hrs

	
	Minimum – 49.72
	21.12.18
	07:30 Hrs

	Jan’19
	Maximum –50.17
	26.01.19
	13:00 Hrs

	
	Minimum – 49.70
	04.01.19
	07:30 Hrs


Grid Demand up to the month of January’19
	 Month
	Max. Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	Apr’18
	92.65
	23.04.18
	2400
	3334
	4430
	22.04.18
	21:00
	2348
	01.04.18
	24:00

	May’18
	98.61
	24.05.18
	2735
	3798
	4692
	07.05.18
	21.00
	2113
	14.05.18
	12.00

	June18
	98.45
	01.06.18
	2497
	3455
	4729
	01.06.18
	02:00
	2173
	29.06.18
	14:00

	July’18
	94.27
	29.07.18
	2572
	3457
	4498
	28.07.18
	22:00
	2010
	16.07.18
	13:00

	Aug’18
	114.57
	24.08.18
	3165
	4254
	5428
	23.08.18
	21:00
	3313
	28.08.18
	14:00

	Sept’18
	108.58
	30.09.18
	2857
	3968
	4973
	30.09.18
	21:00
	2881
	21.09.18
	05:00

	Oct’18
	116.85
	05.10.18
	3147
	4230
	5270
	02.10.18
	19:00
	3033
	12.10.18
	07:00

	Nov’18
	92.71
	06.11.18
	2615
	3632
	4522
	08.11.18
	19:00
	2959
	26.11.18
	03:00

	Dec’18
	81.98
	01.12.18
	2188
	2941
	4038
	01.12.18
	19:00
	1698
	18.12.18
	03:00

	Jan’19
	83.50
	26.01.19
	2303
	3095
	4199
	29.01.19
	20:00
	2246
	02.01.19
	03:00

	Jan’18
	84.87
	29.01.18
	2311
	3107
	4251
	28.01.18
	20:00
	2244
	04.01.18
	04:00


B. Voltage Profile of 220 kV Buses in OPTCL system for the month of: January’19
	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Atri
	232.61
	14
	1:45
	221.12
	7
	17:45

	2
	Balasore
	231.57
	2
	3:00
	218.98
	3
	18:00

	3
	Barkote
	231.80
	21
	2:15
	226.37
	3
	9:15

	4
	Bhadrak
	235.03
	3
	4:00
	221.47
	24
	18:15

	5
	Bhanjanagar
	235.55
	22
	3:45
	224.24
	11
	17:15

	6
	Bidanasi
	238.50
	21
	3:15
	223.37
	29
	8:45

	7
	Bolangir
	225.62
	22
	3:30
	208.99
	8
	8:15

	8
	Budhipadar
	234.34
	16
	3:00
	227.93
	18
	18:45

	9
	Chandaka
	232.90
	21
	2:00
	220.60
	25
	10:45

	10
	Cuttack
	232.20
	11
	3:15
	219.39
	31
	9:00

	11
	Duburi(O)
	236.19
	30
	3:00
	226.08
	28
	19.45

	12
	Duburi (N)
	233.01
	2
	3:00
	224.24
	19
	10:15

	13
	Jayanagar
	237.17
	22
	3:45
	228.68
	31
	16:30

	14
	Joda
	231.51
	22
	4:45
	221.64
	11
	9:00

	15
	Katapalli
	230.07
	7
	16:00
	205.13
	7
	15:45

	16
	Lapanga
	232.72
	16
	2:15
	205.93
	7
	15:45

	17
	Laxmipur
	237.80
	22
	3:45
	227.07
	6
	16:30

	18
	Mendhasal
	234.63
	14
	1:45
	221.98
	7
	17:45

	19
	Meramundali
	228.10
	7
	2:00
	222.62
	19
	9:30

	20
	Narendrapur
	235.61
	22
	3:45
	210.26
	28
	17:00

	21
	Nayagarh
	233.82
	22
	3:45
	222.22
	31
	9:00

	22
	Paradeep
	234.28
	30
	3:00
	215.00
	18
	8:00

	23
	Tarkera
	231.74
	7
	2:00
	224.52
	3
	9:15

	24
	Theruvali
	234.63
	22
	3:45
	220.08
	6
	16:30

	25
	Samangara
	232.38
	14
	1:45
	219.50
	11
	10:45


The maximum Voltage of 238.50 kV occurred at Bidanasi 220 kV bus, while Katapali 220 kV bus has experienced the minimum Voltage of 205.13 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Mendhasal, Meramundali  and New Duburi bus during the month of January’2019 are indicated. 
[image: image2.emf]210

212

214

216

218

220

222

224

226

228

230

232

234

236

238

240

242

244

246

248

250

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF BIDANASI 220 KV BUS

For January 2019


[image: image3.emf]200

205

210

215

220

225

230

235

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE  PROFILE OF KATAPALI 220kV BUS 

FOR JANUARY 2019


[image: image4.emf]210

215

220

225

230

235

240

245

250

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF JAYANAGAR 220 KV BUS

For January 2019


[image: image5.emf]200

205

210

215

220

225

230

235

240

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NARENDRAPUR 220kV BUS

FOR JANUARY 2019


[image: image6.emf]200

205

210

215

220

225

230

235

240

245

250

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MENDHASAL  220 KV BUS 

For January 2019


[image: image7.emf]380

385

390

395

400

405

410

415

420

425

430

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE  PROFILE OF  MENDHASAL  400 KV BUS

For January'2019


[image: image8.emf]390

395

400

405

410

415

420

425

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MERAMUNDALI 400 KV BUS

For January 2019


[image: image9.emf]390

395

400

405

410

415

420

425

430

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NEW DUBURI 400 KV BUS

For January 2019


Members may discuss.
C. Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of Jan-2019 [image: image10.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  JANUARY'2019

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

33.56 11 08:45 2.24 8 01:00

33.56 11 08:45 2.20 8 01:00

105.40 21 10:45 36.28 27 15:45

92.24 17 10:30 20.60 15 10:15

106.88 21 09:45 9.64 17 09:15

1x100

Meter installed on 14th February'2019

1x160

Meter installed on 14th February'2019

1x100 60.88 25 07:15 1.76 9 02:45

1x160 75.72 24 18:15 14.08 7 08:15

1x160 75.72 24 18:15 13.88 7 08:00

1x160 101.44 8 08:30 12.32 1 06:00

1x160 89.08 8 08:30 10.44 1 06:00

1x160 33.24 24 09:30 1.52 25 10:48

1x100 26.00 22 08:15 1.60 25 23:45

1x100 36.92 22 08:15 2.56 25 23:45

128.04 19 18:45 16.26 30 13:15

135.12 19 18:45 4.52 22 11:15

132.44 7 11:00 8.44 18 15:00

132.28 7 10:45 12.68 5 09:15

1x100 44.92 25 17:45 3.88 31 10:45

1x160 71.32 28 11:00 3.20 25 12:15

1x100 48.32 25 17:45 18.84 13 15:45

1x160 74.12 25 17:45 9.72 16 11:30

1x160

75.12

11 09:45 3.28 24 16:45

1x100

29.84

22 09:30 3.20 8 15:30

1x160 80.12 19 10:15 7.00 3 02:45

1x100 50.84 19 10:15 4.48 13 02:15

1x100 42.44 26 12:00 4.00 3 02:45

1x160 86.20 11 18:30 17.12 6 12:00

1x160 86.32 11 18:30 17.24 6 12:00

56.88 29 19:15 23.88 5 14:00

56.80 27 08:00 23.24 5 13:45

56.44 29 18:15 23.56 5 13:45

1x100 54.28 7 17:45 2.24 1 17:45

1x100 54.32 7 17:45 2.24 1 17:45

1x160 57.44 7 12:15 1.24 2 21:15

67.44 6 08:45 29.96 1 06:00

67.24 6 08:45 26.00 10 17:30

36.64 30 09:00 2.28 7 00:30

44.68 29 17:30 2.44 7 00:30

43.96 29 17:45 1.72 7 02:30

21.00 23 04:03 3.00 7 12:00

33.60 23 04:30 8.40 21 12:00

126.24 8 10:15 32.12 21 00:30

114.32 12 07:45 9.84 8 08:45

1x100 65.36 12 07:45 4.28 8 08:45

1x160 109.00 15 18:30 4.36 11 09:30

1x100 69.60 26 12:00 8.28 25 10:45

1x50

4x100  67.12 18 08:45 14.44 6 08:45

68.92 18 08:45 17.52 6 08:45

65.44 17 09:00 25.68 7 02:15

66.88 18 08:45 13.80 30 16:30

2x100 51.80 7 18:15 7.20 22 12:15

49.24 7 18:15 7.48 22 12:15

1x160 80.48 7 18:15 10.96 22 12:15

1x160  86.49 3 14:45 0.01 15 18:30

1x160 86.49 3 14:45 0.01 15 18:30

2x160 68.16 1 08:15 15.24 24 15:15

68.24 1 08:15 8.44 18 11:15

Drawal details

Maximum Minimum

ATRI                                                     

{Banki, Khurda, Chandpur & Argul}

2x160

BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

3x160 



BARGARH 220/132 kV

BHADRAK 220/132 KV

{Bargarh, Ghensh}

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}



BIDANASI 220/132 KV

{Bidanasi, Khurda }



BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

2x160

BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), 

MCL, Sundergarh,Brajarajnagar, 

Rajgangpur}

2x160 



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }



CUTTACK

DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, 

Jajpur Road, Kalarangi, Jajpur Town}



JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

3x100 

"*" - Alternate P/S from 

Kuchei.

KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & 

Katapali area load.}

Supported by Burla & 

Chipilima power.

LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

2x160

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100

Mendhasal { Part area load of Khurda S/S} 2x100

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, 

Digapahandi, Mohana.}

2x160



PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



SAMANGARA                                          

{ Puri, Nimapara & Konark}

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 



THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

Rayagada & Paralakhemundi 

can be fed from Machhkund 

system.

TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 


D. DISCOM Drawal up to the month of January’19
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	Apr’18
	745.479
	734.495
	770.403
	19.655
	750.748
	16.253

	
	May’18
	770.329
	819.87
	850.674
	20.004
	830.67
	10.8

	
	June’18
	745.48
	836.254
	848.445
	14.721
	833.724
	-2.53

	
	July’18
	770.329
	805.001
	823.135
	16.707
	806.428
	1.427

	
	Aug’18
	770.329
	825.849
	833.67
	17.428
	816.242
	-9.607

	
	Sept’18
	745.48
	741.752
	784.029
	5.113
	778.916
	37.164

	
	Oct’18
	770.329
	728.178
	783.342
	9.693
	773.649
	45.471

	
	Nov’18
	745.48
	608.066
	665.861
	14.026
	651.835
	43.769

	
	Dec’18
	770.329
	582.852
	600.916
	14.372
	586.544
	3.692

	
	Jan’19
	770.329
	579.570
	614.936
	18.955
	595.981
	16.411

	WESCO
	Apr’18
	585.205
	636.576
	689.137
	57.318
	631.819
	-4.757

	
	May’18
	604.712
	636.024
	1042.2
	362.004
	680.194
	44.17

	
	June’18
	585.205
	640.766
	995.128
	359.629
	635.499
	-5.267

	
	July’18
	604.712
	612.348
	767.095
	160.722
	606.373
	-5.975

	
	Aug’18
	604.712
	586.549
	1,152.89
	561.626
	591.265
	4.716

	
	Sept’18
	585.205
	606.175
	976.932
	365.889
	611.043
	4.868

	
	Oct’18
	604.712
	676.465
	1,293.38
	600.136
	693.24
	16.77

	
	Nov’18
	585.205
	547.993
	965.032
	350.615
	614.417
	66.424

	
	Dec’18
	604.712
	568.413
	686.294
	114.336
	571.958
	3.545

	
	Jan’19
	604.712
	612.473
	752.559
	142.416
	610.143
	-2.33

	NESCO
	Apr’18
	504.658
	418.945
	528.936
	105.079
	423.857
	4.912

	
	May’18
	521.48
	480.187
	576.819
	102.344
	474.475
	-5.712

	
	June’18
	504.658
	488.448
	598.361
	113.554
	484.807
	-3.641

	
	July’18
	521.48
	481.593
	581.864
	95.907
	485.957
	4.364

	
	Aug’18
	521.48
	494.386
	644.557
	138.545
	506.012
	11.626

	
	Sept’18
	504.658
	467.35
	575.488
	99.903
	475.585
	8.235

	
	Oct’18
	521.48
	494.564
	594.427
	108.007
	486.42
	-8.144

	
	Nov’18
	504.658
	403.449
	536.939
	101.478
	435.461
	32.012

	
	Dec’18
	521.48
	412.703
	528.254
	91.205
	437.049
	24.346

	
	Jan’19
	521.48
	458.171
	549.538
	97.082
	452.456
	-5.715

	SOUTHCO
	Apr’18
	300.822
	298.76
	298.778
	0
	298.778
	0.018

	
	May’18
	310.849
	321.453
	323.114
	0
	323.114
	1.661

	
	June’18
	300.822
	316.746
	315.514
	0.57
	314.944
	-1.802

	
	July’18
	310.849
	316.309
	313.076
	0.574
	312.502
	-3.807

	
	Aug’18
	310.849
	322.184
	322.519
	0
	322.519
	0.235

	
	Sept’18
	300.822
	302.037
	309.512
	0
	309.512
	7.475

	
	Oct’18
	310.849
	295.91
	298.996
	0
	298.996
	3.086

	
	Nov’18
	300.822
	248.651
	292.634
	0
	292.634
	43.983

	
	Dec’18
	310.849
	255.345
	276.639
	0
	276.639
	21.294

	
	Jan’19
	310.849
	276.311
	292.500
	0.390
	292.110
	15.799


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
Members may please discuss.

Energy Generation / Import up to the month of January’19
Figures in MU  
	Month
	Thermal

(TTPS+IbTPS)
	OHPC 
& MKD
	CGP Support
	IPP Inj.
	RE
	ISGS
	Total

	April’18
	535.100
	421.700
	362.530
	198.950
	9.690
	872.260
	2400.230

	May’18
	567.940
	573.520
	313.169
	199.230
	14.390
	1066.640
	2734.889

	June’18
	485.813
	481.601
	219.983
	203.230
	11.897
	1084.870
	2487.394

	July’18
	440.179
	421.582
	213.953
	193.928
	10.102
	1292.141
	2571.885

	Aug’18
	473.390
	689.310
	163.300
	202.940
	13.680
	1621.990
	3164.610

	Sept’18
	454.183
	1037.515
	203.086
	136.688
	13.196
	1012.434
	2857.102

	Oct’18
	483.538
	927.724
	227.618
	191.329
	13.269
	1303.948
	3147.426

	Nov’18
	500.555
	406.963
	242.821
	255.937
	12.645
	1196.275
	2615.196

	Dec’18
	554.605
	322.626
	266.526
	179.021
	16.591
	852.921
	2192.290

	Jan’19
	514.055
	334.421
	334.652
	280.205
	12.646
	826.993
	2302.972

	Total
	5009.358
	5616.962
	2547.638
	2041.458
	128.106
	11130.47
	26473.99


E.  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of January’19 are as detailed:
	Month
	Total Generation
	Odisha Drawl
	AP Drawl

	
	MU
	Avg (MW)
	MU
	Avg (MW)
	MU
	Avg (MW)

	Apr’18
	37.162
	51.610
	18.613
	25.851
	16.943
	25.532

	May’18
	48.888
	65.700
	22.424
	30.140
	24.492
	32.919

	June’18
	43.185
	59.980
	19.692
	27.350
	21.635
	30.048

	July’18
	45.146
	60.680
	20.894
	28.083
	22.148
	29.769

	Aug’18
	51.319
	68.977
	23.507
	31.595
	25.708
	34.554

	Sept’18
	45.449
	63.123
	20.039
	27.032
	23.324
	32.394

	Oct’18
	50.184
	69.700
	22.268
	30.927
	25.721
	35.726

	Nov’18
	49.688
	69.011
	21.964
	30.506
	25.621
	 35.585

	Dec’18
	52.772
	70.930
	24.878
	33.438
	25.653
	34.479

	Jan’19
	59.629
	80.146
	28.179
	37.875
	29.257
	39.323

	Total
	483.422
	
	222.458
	
	240.502
	


Drawl of State share power from Machhakund is decreasing for the current Financial Year. Southco may add more feeders to Podagada S/s. In the 128th PSOC meeting Southco stated that the contractor is not turning up for the work. 
SOUTHCO may deliberate.
F. Under Frequency Relay operation in OPTCL System during the month of Jan’19.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of January’19.
G. Status of Open Access applications up to the month of January’2019
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’18
	26
	79
	0
	31
	136
	26
	76
	0
	31
	133
	3

	2
	May’18
	59
	90
	0
	26
	175
	59
	89
	0
	26
	174
	1

	3
	June’18
	14
	57
	0
	30
	101
	14
	57
	0
	30
	101
	0

	4
	July’18
	18
	145
	0
	26
	189
	18
	145
	0
	26
	189
	0

	5
	Aug’18
	26
	90
	0
	37
	153
	26
	90
	0
	37
	153
	0

	6
	Sept’18
	25
	97
	0
	32
	154
	25
	97
	0
	32
	154
	0

	7
	Oct’18
	45
	60
	0
	28
	133
	45
	60
	0
	28
	133
	0

	8
	Nov’18
	39
	95
	0
	35
	169
	39
	95
	0
	35
	169
	0

	9
	Dec’18
	36
	68
	0
	28
	132
	36
	67
	0
	27
	130
	2

	10
	Jan’19
	63
	102
	0
	28
	193
	44
	102
	0
	28
	174
	19

	
	Total
	351
	883
	0
	301
	1535
	332
	878
	0
	300
	1510
	25


PART C – Issues discussed in the 154th  OCC meeting of ERPC held on 21.02.2019
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
149th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	30.11.18
	162.5 Cr.


	38.09Cr. Requisition for 11.00 Cr placed.
	90% equipment installed and commissioned. Stn Tfr and some measuring instruments are under tendering process.



	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.22 Cr
	Request for 10% grant already submitted. Agreement  signed
	Tender floated

	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov18
Chiplima

Dec 2018
	22.35 Cr.
	2.235 Cr
	Placed work order for Balimele

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 
	27-07-18
	
	31.94 Cr
Ested. Cost. Approved amount 30.26 Cr. Grant amount 27.23 Cr.
	27.23 Cr.
	Agreement signed and sent to NLDC for signature. Tender floated.

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost. 2.93 Cr recommended by Appraisal committee.
	
	Approved by Appraisal committee. Forwarded to CERC for concurrence.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	12.03.2018  Date of submission 
	
	41.1 Cr

Estt cost
	
	Compliance to TSEG observation submitted. Audit observation has been sent to NLDC. 


OCC suggested that OPTCL & OHPC may update the target date of completion. O&M may write to ERPC to expedite the clearance of pending amount from PSDF.
      CGM (O&M) / OHPC/ SLDC may please update the status.
C.2: Implementation of Automatic Generation Control (AGC) in India (at Inter-State level) 

 
CERC in its order dated 13.10.2015 in Petition No. 11/SM/2015 reiterated the need for mandating Primary Reserves as well as enabling Secondary Reserves, through Automatic Generation Control (AGC) as follows: 

“(a) All generating stations that are regional entities must plan to operationalise AGC along with reliable telemetry and communication by 1st April, 2017. This would entail a one-time expense for the generators to install requisite software and firmware, which could be compensated for Communication infrastructure must be planned by the CTU and developed in parallel, in a cost effective manner. 
(b) On the other hand, National/Regional/State Load Dispatch Centres (NLDC/RLDCs/SLDCs) would need technical upgrades as well as operational procedures to be able to send automated signals to these generators. NLDC /RLDCs and SLDCs should plan to be ready with requisite software and procedures by the same date. (c) The Central Commission advises the State Commissions to issue orders for intra-state generators in line with this timeline as AGC is essential for reliable operation of India’s large inter-connected grid.” 

The issue was discussed in 8th NPC Meeting held on 30th November 2018, it was decided that each RPC would submit the status of implementation of AGC to NPC.  

Members may discuss.  

C.3: Power Assistance at Manique GSS from DVC and at Kendposi GSS from OPTCL –JUSNL 

JUSNL vide letter dated 8th February 2019 informed that they are planning shutdown of 132 KV D/C RCP-ADP line for erection of 05 nos. Multi Circuit Tower in place of existing transmission tower. Erection of Multi Circuit Tower is inevitable for new 132 KV RCP-Jadugoda transmission line due to limitation of vacant corridor. 

Due to proposed shutdown, 220/132 KV Chandil GSS will be overloaded. lt will be pertinent to mention here that SER is availing power from Kendposi, RKSN, CKP and Goilkera GSS which require reliable power for smooth functioning of Railway. 

Considering all the above facts and for reliability of the system it is requested to shift the load  of Manique GSS on DVC system and Kendposi should be fed through OPTCL Joda Power for 31 days. 

Members may discuss.

C.4: Automatic Under Frequency Load Shedding (AUFLS) Scheme and Mapping of Feeders 

(A) Review of AUFLS Settings 

 In 8th NPC held on 30th November 2018, it was agreed for the AUFLS scheme with 4 stages and raising the frequency by 0.2 Hz viz. 49.4, 49.2, 49.0 & 48.8 Hz. It was also decided that, NRPC may appoint a Consultant from their own resources as proposed by MS (NRPC) for studying the AUFLS scheme for Indian grid and submit the study report to NPC Secretariat within a time of six months. 

 
The revised load relief for AUFLS computed by NPC Secretariat would be discussed along with the report of Consultant appointed by NRPC (if available), in the next meeting of NPC which would be held in the month of May, 2019. 

Members may note. 

  
(B) Mapping of Feeders 

 
In 8th NPC held on 30th November 2018, it was decided that each RPC would submit the details / progress of feeder mapping to NPC secretariat on a regular basis (quarterly). 

Members may submit the latest status.

C.5: Coal requirement for thermal power plants –MoP 

MoP vide letter dated 7th February 2019 informed that, it has been decided that in view of expected increased power demand in the next few months up to monsoons, all power plants be advised to be watchful, and do maintain plant availability and adequate coal stocks as per norms, in this period.  

 
All the thermal plants are advised to take effective steps for immediate implementation of the decision. The action taken report may also be forwarded to the Ministry at the earliest.  

Thermal plants may comply and submit the report.

C.6: RGMO/FGMO and PSS Tuning of Generators in Eastern Region 

In line with 148th OCC decision, a separate meeting on Restricted Governor /Free Governor Mode Operation and PSS Tuning of generators with the power station authorities in the Eastern Region was held on 31st January 2019.  All the station representatives stated that the gap in understanding the provisions of the grid code had been addressed through the deliberations in the meeting. Minutes of the meeting are awaited.   

Members may note.

C.7: Information regarding details of existing transmission system (220 kV and above AC & DC voltage level) in Eastern Region as on 31.12.2018 

CEA vide letter dated 29/01/2019 intimated that MoP, GoI has desired information regarding details of state wise growth of transmission system (both interstate and intra state system) over the years to create database of existing transmission system. 

Accordingly, it is requested that the information in respect of existing transmission system (both interstate and intra state system) as well as State Power Map and single line Diagram of transmission network including Powergrid (ISTS) and other Transmission Service Provider (TSPs) (as on 31.12.2018) may please be made available in the specified format attached at Annexure –B14. I & II to ERPC for onward transmission to CEA / MoP by 28.02.2019. 

Members may furnish
C.8: Adequate measures to safeguard system(s) during planned shutdown – Proposal of POSOCO 

It has been noted with concern that whenever the transmission elements including bus bars are taken under shutdown on account of Annual maintenance work / System Augmentation, inadvertent switching / testing activities / Mal – operations are causing unwanted tripping of other bus leading to multiple element tripping and in some cases complete outage of substations which is a real threat to system security /reliability. It is also observed that during planned shutdown, works related to bus bar stability, Protection testing, bay maintenance and other miscellaneous activities are carried out without any advanced intimation to NLDC / RLDC, which is causing difficulties in assessment of the risk involved for such shutdown. 

 
It may be mentioned that the manual of “Transmission Planning Criterion ” of CEA suggests that even“ A stuck breaker condition shall not cause disruption of more than four feeders for the 220 kV systems and two feeders for the 400 kV and 765 kV Systems”. 

 
All concerned are requested to take necessary precautions before availing shutdown and furnish the details of nature of work to be carried out during shutdown so as to ensure adequate measures & preparatory actions to safeguard systems during shutdown period. 

Members may discuss.
C.9: Updation of Restoration procedure of Eastern Region 

In compliance with clause 5.8 (a) and (b) of the present IEGC, The Restoration Procedure has to be developed and updated annually by RLDC in consultation with NLDC, all users, STU, SLDC,CTU, RPC Secretariat of the region. 

Draft copy of “Black Start and Restoration Procedure” was mailed on 11th Jan 2019 for review and feedback from stake holder.  

Only DVC has provided the comments on the draft procedure. Based on comments and updates procedure was finalized on 31st Jan 2019 and same was also sent to all the entity of ER. 

As per 153rd OCC decision, a workshop on Restoration procedure of Eastern Region had been conducted on 15th February 2019.  

1. Ensuing healthiness of normally switched off Tie lines between states/utilities for fast restoration during blackout: ERLDC 

 
As per approved black start and restoration procedure of Eastern Region the following 132 kV lines which are normally kept off may be required to be used during start-up procedure: 

a) Joda-Kendposi 132 kV S/C (GRIDCO/JUSNL)
b) Sahupuri-Karmnasa 132 kV D/C (UPPCL /BSPTCL) 
c) Kharagpur-Kharagpur 132 kV Bus Extension (DVC/WBSETCL) 
d) Kolaghat-Kolaghat 132 kV Bus Extension (DVC/WBSETCL) 
e) Patratu-Patratu 132 kV S/C (DVC/JUSNL) 
f) Golekera-Rourkela 132 kV S/C (JUSNL/GRIDCO) 
The lines, therefore, should be tested once in a month for its healthiness. The communication between the concerned stations should be kept healthy. 

Concerned may update the present status. 

2. Updated Black Start and Restoration procedure of State 

 
As per clause IEGC 5.8(b)  

“Detailed plans and procedures for restoration after partial/total blackout of each User’s/STU/CTU system within a Region will be finalized by the concerned User’s/STU/CTU in coordination with the RLDC. The procedure will be reviewed, confirmed and/or revised once every subsequent year.” 

In fulfillment of same constituents are requested to share their updated restoration procedure. 

SLDCs may update.  

C.10: Ratification of projected Demand and generation for POC transmission charges and loss calculations for Q1 (2019-20)--ERLDC 

The projected Demand and Generation of ER constituents to be considered in the base case for POC transmission charge and loss calculations for Q1 (April 19-June 19) are attached at Annexure-B17 for ratification by the constituents. 

GRIDCO may go through and confirm.

C.11: Implementation of Automatic Demand Management Scheme

The latest status along with proposed logic as follows: 
	Sl. No
	State /Utility
	Logic for ADMS operation
	Implementation status/target
	Proposed logic (if different from under implementation logic

	1
	Odisha
	1. System Frequency < 49.9 Hz 
2. Odisha over-drawl > 150 MW
3. DISCOM over-drawl > (40 MW) 
	10 Months

Sent for PSDF approval
	Logic 2 and 3 is AND or OR, in case it is AND then ADMS may not operate when DISCOMs are in schedule but GRIDCO is over drawing due to less generation at State embedded generators.


In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 123rd PSOc meeting SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval

In the 124th PSOC meeting SLDC stated that the revised estimate has been approved in the BoD.

In the 129th PSOC meeting SLDC stated that CERC approval is awaited for tendering.

In the 129th PSOC meeting it was suggested by members that SLDC may write to ERPC in this regard

SLDC may deliberate the status

C.12: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 129th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by March’19. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by March’19.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	220 kV S.C line and Keonjhar S/S (220/33 kV) , 2x20 MVA charged on 31.12.2018.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	March’2019 


CGM (Cont) / CGM (O&M) may update

C.13: Bypassing arrangement of LILO of 400kV Lines at Angul 
LILO of Meramundali-Bolangir/Jeypore 400 kV S/C line and LILO of one Ckt of Talcher-Meramundali 400 kV D/C line has been done at Angul 765/400kV Sub-station. The bypass arrangements for these circuits were under implementation at Angul by Powergrid.  

In 150th OCC, Powergrid informed that bypass arrangement would be completed by January 2019.   

Members may note
C.14: Update on status of telemetry  

 
CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed  NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action.  

Major issues are given below: 

 
i. Regarding frequent intermittent of real time SCADA data from Talcher STPS Stage 1 & 2, NTPC agreed to provide additional ports by March 2019.  ii. Alternate path for Malda–Farakka OPGW link 

In 153rd OCC, Powergrid was advised to implement alternate OPGW link through 400 kV Kishenganj- Darbhanga-Muzaffarpur lines.  

OCC advised Powergrid to coordinate with Kalpatru Power Transmission Ltd. and DMTCL for implementation of the scheme.  

With regard to the State network, this was deliberated in the last meetings that data communication from Narsingpur S/s is not in place. Also date communication from NALCO is not stable. Telecom stated that provision for laying optical fibre in Bhanjanagar-Meramundali line has been kept in PSDF scheme. However, if wave trap foundation will be done at Narsingpur S/S, the data communication can be established. 

In the 129th PSOC meeting it was decided that NALCO shall write to OPTCL for preparation of estimate for laying of Optical fibre. Construction wing of OPTCL agreed for construction of wave trap foundation at Narsingpur S/S.
Const./Telecom / NALCO may update the status

C.15: Replacement of Non-functioning/Defective Meter--ERLDC 

  Erroneous data of Energy meter 

Following meters at different substation of PGCIL and BSPTCL is recording erroneous reading since last few weeks. The problem was informed to the respective substation through e mail and telephonically. However the problem of erroneous data of meters is still persisting. 

	Sl. No.
	Substation
	Name of Feeder
	Meter  S.No
	Date of start of problem Issues

	4
	BOLANGIR
	220 KV SIDE BOLANGIR 400/220 KV 500 MVA ICT-I
	ER-1573-A
	03.12.18 Wrong Connection of CT/PT

	5
	BOLANGIR
	220 KV SIDE BOLANGIR 400/220 KV 500 MVA ICT-I
	NP-7919-A
	03.12.18 Wrong Connection of CT/PT

	9
	BARIPADA
	400 KV SIDE 500 MVA 400/220 BARIPADA ICT-3
	ER-1564-A
	26.12.18 Wrong connection of CT/PT 



OCC advised all the concerned constituents to take the necessary action to resolve the issues at other locations.  

 O&M may please update the status.
C.16: Mock Black start exercises in Eastern Region – ERLDC 

The tentative schedule of black-start exercises for F.Y 2018-19 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2018
	Done on 28.06.2018& 27.09.18
	Last week of January 2019
	March’2019

	3
	Rengali
	2nd week of June 2018
	Done on 18.08.2018
	Last week of November 2018
	Done on 12.02.19

	4
	U. Indravati
	3rd week of June 2018
	Done on 28th Dec’18
	2nd week of February 2019
	February’2019

	6
	Balimela
	3rd week of October  2018
	Done on 21st Dec’18
	1st week of March 2019
	March’19

	9
	Burla
	Last week of June 2018
	Done on 07.06.2018
	Last week of February 2019
	March’19


SLDC / OHPC may update. 

 C.17: Submission of Thermal Loading of Transmission line and associated terminal equipment by ISTS licensee  

In line with the MoM of 4th NRCE Meeting dt.03-11-14 and “Operational Guidelines for determination Of TTC, ATC and TRM for the Short-Term Horizon (0-3 Months)” published by NRCE dt.20-02-15, thermal limit for transmission line has to be used for calculation of ATC/TTC. However, the thermal loading of transmission line depend on the Maximum Conductor Temperature, End equipment thermal rating. This has to be submitted by the Owner of the equipment. Further, the equipment owner also has to confirm that relay setting has been aligned so that the line can be operated up to its thermal limit. In the absence of complete details, ERLDC is utilising the data from the CEA Planning Criteria  for thermal rating as given below : 

	Conductor Type 


	Ampacity per 

conductor(A)* 
	Thermal loading 

limit of line (MVA) 

	765 kV Quad ACSR_Bersimis
	732
	3880

	765 kV HexaACSR_Zebra
	560
	4452

	400 kV Twin ACSR_Moose
	631
	874

	400 kV Quad ACSR_Moose 
	631
	1749

	400 kV Quad ACSR_Bersimis 
	732
	2029

	400 kV Triple Snowbird
	630
	1309

	400 kV Twin ACSR_Lapwing
	773
	1071

	220 kV Single AAAC_Zebra
	557
	212

	220 kV Single ACSR_Zebra 
	560
	213

	220 kV Twin ACSR_Moose 
	631
	481

	132 kV Single ACSR_Zebra 
	560
	128

	132 kV Single ACSR_Panther 
	366
	84


*Ambient and Maximum conductor temperature are taken as 45°C and 75°C respectively. Apart from above specifically mentioned in CEA transmission planning criteria following loading limit is considered for HTLS line while calculating ATC/TTC 

	Conductor Type 


	Ampacity per 

conductor(A)* 


	Thermal loading 

limit of line (MVA) 



	400 kV Twin HTLS
	1262 
	1750

	220 kV Single HTLS 
	1020 
	390

	132 kV Single HTLS
	732
	168


In view of this, it is desired that all ISTS Licensee and STU (for 400 kV and important 220 kV lines) may kindly submit the following details to ERLDC for utilization in ATC/TTC calculation: 
a) Transmission line wise Ampacity and Thermal loading along with Maximum Conductor Temperature and conductor type.
b) End Equipment Rating and 
c) Confirmation whether the relay setting has been adopted in line with the thermal rating of the line 

d) Any constraint during thermal loading of line  

In 152nd OCC, ERLDC informed they received the details only from DVC. 

OCC advised all the other ISTS licensees and STUs to submit the relevant data to ERLDC and ERPC. 
In the 128th PSOC meeting it was suggested that Corporate Planning wing may intimate the required data to ERPC/ERLDC.

In the 129th PSOC meeting Sr. G.M (CP) stated that thermal loading data has been submitted by them. O&M shall submit the terminal equipment data

C.G.M (O&M) may deliberate

C.18: Delay in furnishing information to ERLDC/ERPC regarding of Commissioning of new Transmission Elements/ Generating Units within State--ERLDC 

The above matter was deliberated in various OCC meetings and data submission format was also circulated. All states and transmission licensees agreed to submit the list of transmissions elements (ISTS & within state) synchronized for the first timeduring last month and new elements to be commissioned during next month, within 7th day of the current month to ERLDC through mail.  

For the Month of January-2019, states and transmission licensees did not submit their List of Transmission element /generators synchronised in the previous Month and List of Transmission element and generators expected to be synchronised during next Month. 

Non-submission of new charged elements list of Jan '19 and tentative charging list of Feb '19 

It has been observed that some major 220kV intra-state lines have been charged without any data integration & prior information to ERLDC. The list of the lines is as follows: 

220 KV Meramundali (GR)Bhanjanagar(GR) lILO at Narsingpur 

 
West Bengal, Bihar& Odisha may please explain.
C.19: Review of Cyber Security Works/Activities- CEA 

CEA vide letter informed that Secretary (Power) is going to review the cyber security related works /activities being carried out in Power Sector. In this regard, it is requested to provide the State wise status on following action points pertaining to cyber security at the earliest: 

1. Appointment of organization-wise Chief Information Security Officers and its status

2. Identification of organization-wise Critical Infrastructure and its status 

3. Preparation of organization-wise Crisis Management Plan and its status 

4. Status of Cyber Security Mock Drill activity in coordination with CERT-In 

5. Status of Training / Workshops on Cyber Security organized / participated by power sector entities 

6. Status of action taken on CERT-In / NCIIPC advisories 

In 148th OCC, all the constituents were advised to send the latest status to mserpc-power@nic.in within a week.   

The details had been received from DVC, WBSETCL, Bihar and OPTCL only.  

C.20: Submission of static data for preparation of a report on coal fired stations in the country--ERLDC 

One internal committee has been formed by POSOCO to prepare a report on coal fired stations in the country, which will be submitted to the FOLD &FOR, at a later stage. Similar reports have already been prepared by POSOCO for hydro, gas and RES plants, which has been widely appreciated in different forums like FOLD & FOR.  

To prepare this report, some static data (commercial, technical, environmental & general) in proper format for all coal fired stations (ISGS, IPP and State Generators) of capacity >= 200 MW need to be submitted to ERLDC so that the compilation and subsequent analysis of data of thermal generators on an all India basis could be made within stipulated time period. 

The format for data submission was intimated to all generators and state SLDCs via email. Till date only GMR, Adhunik, MPL and Sagardighi have submitted their static data. 

ISGS (NTPC), IPP and State Generators of Eastern Region are requested to kindly accord high priority for submitting the static data to ERLDC in erldcso@posoco.in for preparation of the report within stipulated period. 

Nodal coordinators for this Process from ERLDC are: 

1. Shri Biswajit Mondal, Sr. Engineer, Mob No: 9903329271 2. Shri Chandan Mallick, Sr. Engineer, Mob No: 9007059660 

In 152nd OCC, ERLDC updated the following generating stations have not submitted static data for preparation of report on coal firing stations: 

1.    IB thermal stage -1 

2.    TTPS (Odisha) 

3.    Talcher STPP

4.    Santaldih TPP

5.    Budge-Budge TPP 

6.    Tenughat TPP 

OCC advised above thermal generators to submit the relevant information to ERLDC at the earliest.
All Thermal Generators may comply.

C.21: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC 

As a National Grid operator, POSOCO is continuously working for ensuring reliability and security of the Grid. With penetration of more and more renewable energy source the task is becoming complicated day by day.  An accurate dynamic modeling of the National Grid needs modeling of conventional as well as renewable / distributed generation sources. World Bank has engaged Digsilent as consultant for assisting POSOCO for building dynamic model of the Grid. A guideline for dynamic data collection has been developed in consultation with Digsilent Pacific team.    All the utilities are requested to collect data from the grid scale renewable power plants as well as from conventional power plants under their jurisdiction and submit the same to ERLDC/ERPC as early as possible. 

In the 129th PSOC meeting CGM (PP), GRIDCO stated that M/S MGM Solar has been selected for the pilot project

GRIDCO may update the status.
C.22: Operation Eastern Regional grid from ERLDC back up control Centre at, NLDC, New Delhi as a part of Disaster Management--ERLDC 

 
As informed in 153rd OCC ERPC, ERLDC has successfully operated its backup control center at NLDC, New Delhi from 11:00Hrs to 14:00Hrs on 8th February 2019. All control room activity such as issuance of real time switching code, monitoring of Eastern Region GRID, real time scheduling & reporting were done from backup control center NLDC New Delhi. Entire SCADA system, Open Access & scheduling system have shifted to backup control center of ERLDC. During this process, all the utilities have obtained real time switching code from back up control center and use scheduling server hosted at backup control NLDC, New Delhi for submission of their requisition. 

 
Entire process of operation of ERLDC backup control center was successful only because of full co-operation of utilities of Eastern Region. 

Members may please note. 

 C.23: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA. 

In 142nd OCC, ERLDC informed that, in line with Enquiry Committee Recommendation, cyber security audit is being conducted on regular basis for SCADA system installed at ERLDC and SLDC as well but cyber security audit for telecom infrastructure installed in Eastern Region is not being carried out.  

OCC advised all the constituents to conduct the cyber security audit on telecom infrastructure installed in Eastern Region. It is further advised that compliance / mitigation of the points observed during the audit should also be completed for improvement of the telecom infrastructure in ER. 

A workshop on cyber security was conducted by CEA at ERPC, Kolkata on 09-05-2018.  

 
As suggested by CEA, a format would be circulated among ER constituents for furnishing the information of their respective systems for discussion in OCC Meeting. The format is enclosed at Annexure-E2. 

OCC advised all the constituents to submit the information to ERPC as per Annexure-E2.  

 C.24: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

 
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.  

As per the information received from the constituents the following generators certified with IS 18001:  • All NTPC stations in Eastern Region  • Teesta, NHPC • All OHPC generating units  • All CESC generating units  • All units of WBPDCL • DGPC units 

In the 129th PSOC meeting O&M stated that 2nd stage internal audit has been done. Report is yet to be received. Process has been initiated for deposit of application money for external audit. On compliance of the observations Certificate may be issued.    

CGM (O&M may deliberate
C.25: Providing relevant data by Power Utilities /Stations in National Power Portal. 

CEA vide letter dated 26th June 2018 informed that National Power Portal (NPP) (URL: npp.gov.in), has been launched by Hon'ble Minister of Power on 14th November, 2017. NPP is modified and more user-friendly data portal than the existing Information Management System (IMS) in CEA. Reports prepared from NPP are of vital importance for Power Sector data analytics in order to frame policies, regulations, future road-map for Power Sector etc. at Central as well as at State level. Accordingly, all power utilities have been issued user ID and password, either organisation-wise or station-wise, based on their request , for providing their data on NPP. 

 
NPP has replaced IMS since 1st June, 2018. A Circular (which is available in Circular Section of CEA Website, i.e. cea.nic.in) has been issued by CEA to all power utilities/stations  on  14.06.2018  for  providing  their  data  online  in  NPP  only.  

In this regard, letters/mails have been issued to Utilities to provide their data online through NPP. A letter dated 20.06.2018 was also issued to all SLDC, requesting them to direct the power utilities I stations under their purview for providing data on NPP.  

 
Any issue/problem faced by utilities may kindly be communicated to itcea@nic.in, npp.support@gov.in, ceopm-cea@gov.in and if required, IT Division, CEA may be contacted on 011-26732368 or 011-26732303 

CEA requested to pursue the power utilities I stations under their purview for providing data on NPP. Further, a workshop/presentation may be arranged if required in each region in which IT Division, CEA will provide a brief demonstration regarding data entering process and report generation into NPP. 

C.26: Commissioning of new transmission elements in Eastern Region
IB_St2_OPGC unit # 4 First time synchronization on 23-01-2019 at 18:01Hrs.
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of January’18:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	16.411
	2.831

	2
	WESCO
	0
	-2.330
	0.380

	3
	NESCO
	0
	-5.715
	1.247

	4
	SOUTHCO
	0
	15.799
	5.717

	
	Total
	0
	24.165
	


It is noticed that SOUTHCO & CESU were over drawn during the month while WESCO & NESCO were under drawn. SOUTHCO has deviated 5.717% followed by CESU 2.831% from the scheduled energy while WESCO and NESCO have deviated 0.380 % & 1.247 % respectively. DISCOMs may forecast their drawal in realistic approach to minimise deviation.

SLDC/ Discoms may please deliberate.
D.2: Communication issues 
The status of data communication from CGPs as deliberated in the 124rd PSOC meeting meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	2
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. 
In the 123rd PSOC meeting it was deliberated that RT&C have sought some information from Telecom wing which will be intimated. NALCO stated that due to problem in their internal communication system, data communication to SLDC is being interrupted.
In the 124th PSOC meeting Telecom stated that communication system for Paradeep area industries will be completed by September’2018. Telecom was advised to give a reply to the information sought by RT&C. 

In the 125th PSOC meeting Telecom stated that the information sought by RT&C will be forwarded soon.
In the 126th PSOC meeting it was decided that SLDC shall convene a meeting with Telecom, GCC & RT&C and discuss the issue for filing case before the OERC.

A meeting was convened between SLDC, Telecom, GCC, RT&C, NINL & IRE Ltd on dt.15.01.2019 at SLDC conference hall to discuss the communication issue. Representative of IRE, SLDC, GCC and Telecom were attended the meeting. IRE deliberated that presently CB, CT & CVT are not installed at their end. Tendering for procurement of CB, CT & CVT have already been done, which will be expected by end of April’2019. Due to space constraint at IRE Switch yard, installation of the equipment may not be possible, unless the Switchyard is modified. For modification they may need the help of OPTCL. It was suggested by SLDC that IRE may approach Sr. G.M (O&M), Zone-1, OPTCL in this regard. Simultaneously, they also to write Sr. G.M (Telecom), OPTCL for preparing estimate for extending data communication from their end.

NINL was not present in the meeting.  

In the 129th PSOC meeting it was decided that DGM (O&M), Berhampur and DGM(Cons.), Berhampur shall visit IRE S/W yard and submit a status report to Sr. G.M (O&M), Berhampur. RT&C may file a case before the OERC for non-compliance of extending data communication facility by M/s NINL

RT&C may deliberate. Members may discuss 
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 119th PSOC meeting IT stated that Parameters of 16 Nos meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
In the 123rd PSOC meeting IT stated that out of 840 Nos interface meters connected with AMI, 750 Nos are reporting at present. The newly replaced meters are not reporting. 2 Nos. of meters has sent to M/s SECURE meters for study.

In the 127th PSOC meeting IT stated that TCS is demanding Rs. 6.5 lacs for developing the required software. The proposal is placed before the management for approval

In the 128th PSOC meeting IT stated that the memorandum has been placed before the PSC

In the 129th PSOC meeting IT stated that PSC has already approved the proposal. TCS will develop the software.

IT may update the status
D.4: OPGC Agenda:


OPGC proposed to carry out the following activities in 220KV IB – Budhipadar Circuits. 

1. IB-Budhipadar ckt-2, R-Phase, CVT oil leakage to be arrested.

2. Implementation of Carrier Protection Scheme to be implemented in all 4 ckts of 220 KV IB-Budhipadar lines.

3. Implementation of  Single Phase Auto Recloser scheme to be implemented in all 4 ckts of 220 KV IB-Budhipadar lines.

OPGC may deliberate.
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Expected to be completed by March’19.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	February’2019

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	February’2019

	4
	220/33 kV, 2x20 MVA Baliguda S/S
	July’19

	5
	220/33 kV, 2x20 MVA Kalimela S/S
	July’19

	6
	220/33 kV, 2x20 MVA Kasipur S/S
	February’2019

	7
	220/132 /33 kV, 2x100 MVA Aska S/S
	March’19

	8
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’19

	9
	220/132/33 kV Jayapatana S/S(320 MVA)
	July’19

	10
	220/132 kV Pratapsasan S/S(320 MVA)
	Dec’19

	11
	220/132 kV Kesinga S/S (320 MVA)
	March’19

	12
	132/33 kV Betanati S/S
	March’19

	13
	132/33 kV R.Udyagiri S/S
	March’19

	14
	132/33 kV Chikiti S/S
	(Bus test charged on 11.09.18)


The Discoms are requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement.
CGM (Construction) / DISCOMs may please deliberate the status.
E.2: Major Events in the month of January’19
1.   On 16.01.2019 at 14:56 Hrs 132 KV Sunabeda-Patangi line idle charged from Sunabeda end.
2.  On 26.01.2019 at 18:32 Hrs 220 kV Theruvali-Indravati ckt LILO at Kasipur main bus and Kasipur bus charged.
Members may note

E.3: Important Grid Incidences during the month of January’19.
(a) On 01.01.2019 at 04:33 Hrs-   220 kV Lapanga-Budhipadar ckt-II tripped at both end followed by tripping of 220 kV Budhipadar –Vedanta ckt-I&II at Budhipadar end. 

(b) On 07.01.2019 at 15:40 Hrs- Katapali-Bolangir (PG) ckt tripped at Katapali end with DP relay operated due to snapping of R-Ph jumper at location No. 4 and falling on Y-Ph conductor. All 220 kV and 132 kV incomer/feeders tripped at Kantapali end resulting total blackout of Katapali S/S.

O&M may deliberate
E.4: Outage of major transmission Elements during the month of January’19. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration

Dt/time
	Reason

	1
	220 kV Katapali-  Balangir (PG) ckt.
	07.01.19
15:40
	08.01.2019/ 14:14
	R-ph Jumper snapped at Loc No-4 and fallen on Y-ph 

	2
	400 kV Lapanga-Vedanta ckt-II(at Vedanta end) 
	16.01.19 / 20:00

	18.01.19 / 16:50
	Malfunction of Tele-protection equipment at Vedanta end resulting DTT relay operation.

	3
	220 kV Tarkera-RSP ckt II tripped
	20.01.19
/ 10:13
	21.01.19
/ 10:54
	Bursting  of R-ph LA at Terkera Grid

	4
	220 kV Mendhashal-Bidanasi Fdr
	23.01.19
/ 2:10
	23.01.19
/ 17:54
	Puncture of B-Ph string insulator at location No.18.

	5
	220 kV Theruvali-Indravati  ckt-II
	27.01.19

/ 05:43
	29.01.19
/ 15:22
	Insulator failure at tower location no- 183


O&M may discuss
E.5:  Review of Outage Program of State Generators / Transmission elements for the month of March’19:
Tentative Outage programme for State Generators for the month of March’2019 
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 4
# 5

# 6
	14.03.18 to continue
25.10.18 to continue
25.10.16 to continue

16.10.15 to continue
	T&G coupling cover water leakage
Annual Maintenance

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to continue
	Under R,M & U

	3
	Balimela
	# 1
# 2
# 3
	05.08.16 to continue
20.11.17 to continue
04.02.19 to 03.03.19
	Under R,M & U

Programming for R&M
Annual Maintenance

	4
	Rengali
	# 2
	12.12.18 to continue
	Replacement of Runner disc.

	5
	Upper Kolab
	# 1
# 4
	18.02.19 to 16.03.19
01.02.19 to continue
	Annual Maintenance
Capital maintenance work

	6
	Upper Indravati
	# 3
	01.03.19 to 31.03.19
	Annual Maintenance


OHPC may deliberate
E.6: Generation Program for the month of March’19.
Generation schedule for the month of March’19 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.02.19
	Reservoir Level as on 01.02.18
	MDDL
	High Flood    Reservoir Level

	
	Mar’19
(1st fortnight)
	Mar’19
 (2nd fortnight)
	
	
	
	

	HPS-I, Burla
	35
	35
	622.58 ft.
	623.91 ft.
	590 ft.
	630 ft.

	HPS-II, Chiplima
	25
	25
	-
	-
	-
	-

	Balimela
	300
	300
	1503.20 ft.
	1467.30 ft.
	1440 ft.
	1516 ft.

	Rengali
	40
	40
	117.20 mtr.
	122.25 mtr.
	109.72mtr 
	123.5 mtr.

	U.Kolab
	100
	100
	854.22 mts.
	853.02 mtr.
	844 mtr 
	858 mtr.

	U. Indravati
	250
	250
	638.00 mtr.
	635.20 mtr.
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2739.55 ft.
	2745.90 ft.
	2685 ft.
	2750 ft.

	TOTAL
	780
	780
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

SLDC / OHPC may deliberate

E.7: Anticipated power generation and demand for the month of March’2019.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1150
	1300

	2
	WESCO
	1100
	1250

	3
	NESCO
	850
	900

	4
	SOUTHCO
	350
	400

	6
	Total Discom
	3450
	3850

	
	System Loss & others 
	150
	200

	
	Total Demand
	3600
	4050

	Availability
	
	

	1
	Hydro
	780  
	1200

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	500
	500

	4
	ISGS share (including OA& purchase)
	1220
	1250

	5
	CGP support (OA)
	350
	350

	6
	Total availability
	3600
	4050

	7
	Surplus / Deficit
	0
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (131st) PSOC meeting.
PAGE  

