                                                                                                                  
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image1.png]PTC




Agenda

for

131st Power System Operational Co-ordination Meeting

Date: 29.03.2019
Venue: Power Training Center, Chandaka, Bhubaneswar 
Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 131st PSOC Meeting to be held on 29.03.2019 at OPTCL Power Training Center, Chandaka, Bhubaneswar
A. Confirmation of the minutes of the 130th PSOC Meeting held on 25.02.2019
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2019/670 (47) dated 07.03.2019 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there are no comments, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   :  Grid Performance for the month of February’2019
C.1: Status of projects funded under PSDF scheme 
C.2: Mapping of Feeders of Automatic Under Frequency Load Shedding (AUFLS) Scheme 
C.3: Coal requirement for thermal power plants –MoP
C.4: Removal of Vedanta Towers (5 nos) for direct connectivity on permanent basis of 400kV Sundargarh-Raigarh ckt#4 and 400kV Sundargarh-Raigarh ckt#2--Powergrid
C.5: Implementation of Automatic Generation Control (AGC) in India (at Inter-State level)
C.6: Power Assistance at Manique GSS from DVC and at Kendposi GSS from OPTCL –JUSNL
C.7: Information regarding details of existing transmission system (220 kV and above AC & DC voltage level) in Eastern Region as on 31.12.2018 

C.8: Review of the PSS Tuning of Generators in Eastern Region  

C.9: Bypassing arrangement of LILO of 400kV Lines at Angul

C.10: Updated Black Start and Restoration procedure of State—ERLDC As per clause IEGC 5.8(b)

C.11: Periodical Audit and Vulnerability Assessment & Penetration Testing (VPAT) of ICT Infrastructure--CEA 

C.12: Details of Capacitor bank installed in Distribution/Sub transmission network --ERLDC 

C.13: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC 

C.14: Implementation of Automatic Demand Management Scheme
C.15: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s
C.16: Update on status of telemetry  

C.17: Mock Black start exercises in Eastern Region 

C.18: Submission of Thermal Loading of Transmission line and associated terminal equipment by ISTS licensee  

C.19: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Communication issues. 
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.4: DISCOM Agenda.
E.1: Commissioning status of New Transmission elements. 

E.2: Major Events in the month of February’19
E.3: Important grid incidences during the month of February’19.

E.4: Outage of major transmission Elements during the month February’19. (above 10 hrs).
E.5: Review of Outage Program of State Generators for the month of April’2019
E.6: Generation Program for the month of April’2019.

E.7: Anticipated power generation and demand for the month of April’2019.
F.1: Date and Venue of the next (132nd) PSOC meeting
PART B: GRID PERFORMANCE
B. Review of Grid Performance for the month of February’19.

A. Frequency:

Hourly frequency variation for the month of February’19.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	Dec’18
	0.00
	0.02
	11.78
	76.66
	11.54
	49.98

	Jan’19
	0.00
	0.06
	10.24
	69.48
	20.23
	49.98

	Feb’19
	0.00
	0.00
	5.91
	67.23
	26.87
	49.99


Maximum & Minimum frequency during the month of Jan’19 & Feb’19.
	Month
	Freq (Hz)
	Date
	Time

	Jan’19
	Maximum –50.17
	26.01.19
	13:00 Hrs

	
	Minimum – 49.70
	04.01.19
	07:30 Hrs

	Feb’19
	Maximum –50.16
	11.02.19
	03:15 Hrs

	
	Minimum – 49.75
	21.02.19
	00:45 Hrs


Grid Demand up to the month of February’19
	 Month
	Max. Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	Apr’18
	92.65
	23.04.18
	2400
	3334
	4430
	22.04.18
	21:00
	2348
	01.04.18
	24:00

	May’18
	98.61
	24.05.18
	2735
	3798
	4692
	07.05.18
	21.00
	2113
	14.05.18
	12.00

	June18
	98.45
	01.06.18
	2497
	3455
	4729
	01.06.18
	02:00
	2173
	29.06.18
	14:00

	July’18
	94.27
	29.07.18
	2572
	3457
	4498
	28.07.18
	22:00
	2010
	16.07.18
	13:00

	Aug’18
	114.57
	24.08.18
	3165
	4254
	5428
	23.08.18
	21:00
	3313
	28.08.18
	14:00

	Sept’18
	108.58
	30.09.18
	2857
	3968
	4973
	30.09.18
	21:00
	2881
	21.09.18
	05:00

	Oct’18
	116.85
	05.10.18
	3147
	4230
	5270
	02.10.18
	19:00
	3033
	12.10.18
	07:00

	Nov’18
	92.71
	06.11.18
	2615
	3632
	4522
	08.11.18
	19:00
	2959
	26.11.18
	03:00

	Dec’18
	81.98
	01.12.18
	2188
	2941
	4038
	01.12.18
	19:00
	1698
	18.12.18
	03:00

	Jan’19
	83.50
	26.01.19
	2303
	3095
	4199
	29.01.19
	20:00
	2246
	02.01.19
	03:00

	Feb’19
	83.61
	14.02.19
	2113
	3144
	4223
	14.02.18
	20:00
	2142
	16.02.19
	5:00

	Feb’18
	83.37
	21.02.18
	2194
	3265
	4211
	12.02.18
	20:00
	2241
	16.02.18
	15:00


B. Voltage Profile of 220 kV Buses in OPTCL system for the month of: February’19
	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Atri
	231.28
	28
	23:45
	211.82
	26
	18:15

	2
	Balasore
	231.63
	25
	4:00
	226.43
	21
	18:30

	3
	Barkote
	232.78
	25
	1:45
	226.43
	21
	18:30

	4
	Bhadrak
	234.40
	28
	1:45
	217.42
	22
	20:00

	5
	Bhanjanagar
	234.11
	5
	2:45
	220.19
	26
	18:15

	6
	Bidanasi
	236.59
	1
	2:45
	215.35
	26
	18:15

	7
	Bolangir
	232.61
	26
	13:45
	227.12
	14
	9:15

	8
	Budhipadar
	232.61
	26
	13:45
	227.12
	14
	9:15

	9
	Chandaka
	233.18
	27
	23:45
	212.40
	26
	18:15

	10
	Cuttack
	232.15
	28
	00:00
	210.09
	26
	18:15

	11
	Duburi(O)
	234.46
	4
	2:30
	222.39
	23
	18:45

	12
	Duburi (N)
	231.45
	1
	2:45
	220.71
	23
	19:30

	13
	Jayanagar
	233.30
	5
	7:00
	228.22
	21
	19:00

	14
	Joda
	235.32
	16
	3:45
	216.79
	25
	18:15

	15
	Katapalli
	228.28
	16
	1:00
	218.69
	26
	18:30

	16
	Lapanga
	231.68
	16
	1:00
	217.19
	8
	13:00

	17
	Laxmipur
	233.88
	5
	7:00
	226.20
	21
	18:45

	18
	Mendhasal
	233.82
	27
	23:45
	213.79
	26
	18:15

	19
	Meramundali
	227.76
	1
	14:00
	220.60
	23
	18:45

	20
	Narendrapur
	231.45
	5
	2:45
	205.01
	26
	18:15

	21
	Nayagarh
	232.78
	27
	23:45
	215.11
	26
	18:15

	22
	Paradeep
	234.57
	27
	2:15
	208.71
	23
	19:30

	23
	Tarkera
	230.53
	25
	2:00
	224.29
	14
	9:00

	24
	Theruvali
	231.68
	5
	7:00
	220.02
	26
	18:15

	25
	Samangara
	231.05
	4
	2:30
	211.65
	26
	18:15


The maximum Voltage of 236.59 kV occurred at Bidanasi 220 kV bus, while Narendrapur 220 kV bus has experienced the minimum Voltage of 205.01 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Mendhasal, Meramundali  and New Duburi bus during the month of February’2019 are indicated. 
[image: image2.emf]210

212

214

216

218

220

222

224

226

228

230

232

234

236

238

240

242

244

246

248

250

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE  PROFILE OF BIDANASI 220 kV BUS

For February 2019


[image: image3.emf]210

215

220

225

230

235

240

245

250

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF JAYANAGAR 220 kV BUS

FOR FEBRUARY 2019


[image: image4.emf]200

205

210

215

220

225

230

235

240

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NARENDRAPUR 220 kV BUS

FOR FEBRUARY 2019


[image: image5.emf]200

205

210

215

220

225

230

235

240

245

250

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MENDHASAL 220 kV BUS

For February 2019


[image: image6.emf]380

385

390

395

400

405

410

415

420

425

430

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MENDHASAL 400 kV BUS

FOR  FEBRUARY' 2019


[image: image7.emf]390

395

400

405

410

415

420

425

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MERAMUNDALI 400 kV BUS

For February 2019


[image: image8.emf]390

395

400

405

410

415

420

425

430

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NEW DUBURI 400 kV BUS

For February 2019


Members may discuss.
C. Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of Feb-2019 [image: image9.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  FEBRUARY'2019

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

46.12 18 20:15 2.76 7 02:30

46.16 18 20:15 2.72 7 02:30

89.68 7 10:45 30.64 2 08:15

89.92 7 10:45 30.64 2 08:15

87.12 11 18:15 8.84 7 08:15

1x100

23.12 14 14:30 3.52 25 12:15

1x160

7.36 28 10:45 2.28 18 13:15

1x100 48.08 25 04:45 1.12 4 03:30

1x160 70.36 2 17:00 5.92 23 15:45

1x160 68.32 22 20:15 5.96 23 15:45

1x160 72.60 14 07:15 15.80 11 15:45

1x160 64.12 14 07:15 13.64 11 15:45

1x160 29.92 9 19:00 1.64 5 02:45

1x100 31.60 12 18:15 1.64 5 02:45

1x100 44.88 12 18:15 2.64 5 02:45

129.96 3 18:45 5.16 16 00:45

137.44 14 06:45 5.44 15 00:45

96.68 23 08:30 36.24 16 01:00

93.40 19 16:45 36.12 16 01:00

1x100 53.56 21 18:15 8.48 27 23:45

1x160 93.44 21 18:30 12.72 16 13:45

1x100 67.64 8 08:45 5.60 12 10:45

1x160 82.96 15 18:15 14.00 27 23:45

1x160

55.64

14 18:15 3.72 3 16:00

1x100

45.36

28 13:00 7.32 3 16:00

1x160 83.80 9 20:00 10.88 15 03:00

1x100 54.40 6 14:30 6.44 3 14:15

1x100 51.64 6 14:30 6.80 3 14:15

1x160 137.16 8 09:15 20.08 26 12:15

1x160 81.16 6 20:15 4.20 8 09:15

62.12 3 08:15 6.40 6 16:00

65.00 3 07:45 2.40 6 08:00

63.56 2 19:00 3.28 3 08:00

1x100 29.20 3 10:30 2.08 4 19:15

1x100 29.16 3 10:30 1.88 4 19:15

1x160 13.80 12 15:30 2.68 1 06:00

80.60 20 10:00 7.32 15 23:30

76.72 19 16:45 6.32 15 23:45

44.76 26 18:00 2.00 2 13:30

43.96 26 18:00 2.12 2 13:30

41.56 26 18:15 1.52 2 13:30

21.00 15 06:00 6.00 28 12:00

34.80 15 05:45 6.60 27 12:00

114.08 5 17:15 36.48 1 00:45

108.96 26 19:30 2.24 5 10:00

1x100 65.72 5 17:15 20.68 1 00:45

1x160 108.08 5 18:45 4.16 27 02:00

1x100 65.88 5 18:45 2.52 27 02:00

1x50

4x100  65.96 15 07:15 8.44 25 01:30

71.16 8 08:30 9.16 25 01:30

69.72 8 08:30 8.52 25 01:30

69.24 8 08:30 4.36 2 14:45

2x100 44.20 22 21:15 14.60 7 13:00

42.04 22 21:15 14.40 7 12:45

1x160 68.60 22 19:00 13.84 8 15:00

1x160  80.99 6 14:30 0.00 18 11:30

1x160 80.99 6 14:30 0.00 18 11:30

2x160 76.36 22 11:45 15.52 21 10:00

82.16 21 12:30 9.40 22 10:15

Drawal details

Maximum Minimum

ATRI                                                     

{Banki, Khurda, Chandpur & Argul}

2x160

BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

3x160 



BARGARH 220/132 kV

BHADRAK 220/132 KV

{Bargarh, Ghensh}

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}



BIDANASI 220/132 KV

{Bidanasi, Khurda }



BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

2x160

BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), 

MCL, Sundergarh,Brajarajnagar, 

Rajgangpur}

2x160 



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }



CUTTACK

DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, 

Jajpur Road, Kalarangi, Jajpur Town}



JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

3x100 

"*" - Alternate P/S from 

Kuchei.

KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & 

Katapali area load.}

Supported by Burla & 

Chipilima power.

LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

2x160

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100

Mendhasal { Part area load of Khurda S/S} 2x100

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, 

Digapahandi, Mohana.}

2x160



PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



SAMANGARA                                          

{ Puri, Nimapara & Konark}

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 



THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

Rayagada & 

Paralakhemundi can be fed 

from Machhkund system.

TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 


D. DISCOM Drawal up to the month of February’19
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	Apr’18
	745.479
	734.495
	770.403
	19.655
	750.748
	16.253

	
	May’18
	770.329
	819.87
	850.674
	20.004
	830.67
	10.8

	
	June’18
	745.48
	836.254
	848.445
	14.721
	833.724
	-2.53

	
	July’18
	770.329
	805.001
	823.135
	16.707
	806.428
	1.427

	
	Aug’18
	770.329
	825.849
	833.67
	17.428
	816.242
	-9.607

	
	Sept’18
	745.48
	741.752
	784.029
	5.113
	778.916
	37.164

	
	Oct’18
	770.329
	728.178
	783.342
	9.693
	773.649
	45.471

	
	Nov’18
	745.48
	608.066
	665.861
	14.026
	651.835
	43.769

	
	Dec’18
	770.329
	582.852
	600.916
	14.372
	586.544
	3.692

	
	Jan’19
	770.329
	579.570
	614.936
	18.955
	595.981
	16.411

	
	Feb’19
	695.781
	576.292
	595.547
	12.531
	583.016
	6.724

	WESCO
	Apr’18
	585.205
	636.576
	689.137
	57.318
	631.819
	-4.757

	
	May’18
	604.712
	636.024
	1042.2
	362.004
	680.194
	44.17

	
	June’18
	585.205
	640.766
	995.128
	359.629
	635.499
	-5.267

	
	July’18
	604.712
	612.348
	767.095
	160.722
	606.373
	-5.975

	
	Aug’18
	604.712
	586.549
	1,152.89
	561.626
	591.265
	4.716

	
	Sept’18
	585.205
	606.175
	976.932
	365.889
	611.043
	4.868

	
	Oct’18
	604.712
	676.465
	1,293.38
	600.136
	693.24
	16.77

	
	Nov’18
	585.205
	547.993
	965.032
	350.615
	614.417
	66.424

	
	Dec’18
	604.712
	568.413
	686.294
	114.336
	571.958
	3.545

	
	Jan’19
	604.712
	612.473
	752.559
	142.416
	610.143
	-2.33

	
	Feb’19
	546.192
	581.849
	637.069
	92.692
	544.377
	-37.472

	NESCO
	Apr’18
	504.658
	418.945
	528.936
	105.079
	423.857
	4.912

	
	May’18
	521.48
	480.187
	576.819
	102.344
	474.475
	-5.712

	
	June’18
	504.658
	488.448
	598.361
	113.554
	484.807
	-3.641

	
	July’18
	521.48
	481.593
	581.864
	95.907
	485.957
	4.364

	
	Aug’18
	521.48
	494.386
	644.557
	138.545
	506.012
	11.626

	
	Sept’18
	504.658
	467.35
	575.488
	99.903
	475.585
	8.235

	
	Oct’18
	521.48
	494.564
	594.427
	108.007
	486.42
	-8.144

	
	Nov’18
	504.658
	403.449
	536.939
	101.478
	435.461
	32.012

	
	Dec’18
	521.48
	412.703
	528.254
	91.205
	437.049
	24.346

	
	Jan’19
	521.48
	458.171
	549.538
	97.082
	452.456
	-5.715

	
	Feb’19
	471.014
	428.836
	511.223
	92.599
	418.624
	-10.212

	SOUTHCO
	Apr’18
	300.822
	298.76
	298.778
	0
	298.778
	0.018

	
	May’18
	310.849
	321.453
	323.114
	0
	323.114
	1.661

	
	June’18
	300.822
	316.746
	315.514
	0.57
	314.944
	-1.802

	
	July’18
	310.849
	316.309
	313.076
	0.574
	312.502
	-3.807

	
	Aug’18
	310.849
	322.184
	322.519
	0
	322.519
	0.235

	
	Sept’18
	300.822
	302.037
	309.512
	0
	309.512
	7.475

	
	Oct’18
	310.849
	295.91
	298.996
	0
	298.996
	3.086

	
	Nov’18
	300.822
	248.651
	292.634
	0
	292.634
	43.983

	
	Dec’18
	310.849
	255.345
	276.639
	0
	276.639
	21.294

	
	Jan’19
	310.849
	276.311
	292.500
	0.390
	292.11
	15.799

	
	Feb’19
	280.767
	264.509
	276.747
	0.205
	276.542
	12.033


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
Members may please discuss.

Energy Generation / Import up to the month of February’19
Figures in MU  
	Month
	Thermal

(TTPS+IbTPS)
	OHPC 
& MKD
	CGP Support
	IPP Inj.
	RE
	ISGS
	Total

	April’18
	535.100
	421.700
	362.530
	198.950
	9.690
	872.260
	2400.230

	May’18
	567.940
	573.520
	313.169
	199.230
	14.390
	1066.640
	2734.889

	June’18
	485.813
	481.601
	219.983
	203.230
	11.897
	1084.870
	2487.394

	July’18
	440.179
	421.582
	213.953
	193.928
	10.102
	1292.141
	2571.885

	Aug’18
	473.390
	689.310
	163.300
	202.940
	13.680
	1621.990
	3164.610

	Sept’18
	454.183
	1037.515
	203.086
	136.688
	13.196
	1012.434
	2857.102

	Oct’18
	483.538
	927.724
	227.618
	191.329
	13.269
	1303.948
	3147.426

	Nov’18
	500.555
	406.963
	242.821
	255.937
	12.645
	1196.275
	2615.196

	Dec’18
	554.605
	322.626
	266.526
	179.021
	16.591
	852.921
	2192.290

	Jan’19
	514.055
	334.421
	334.652
	280.205
	12.646
	826.993
	2302.972

	Feb’19
	485.768
	356.056
	226.254
	314.636
	11.201
	719.249
	2112.786

	Total
	5495.126
	5973.018
	2773.892
	2356.094
	139.307
	11849.721
	28586.780


E.  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of February’19 are as detailed:
	Month
	Total Generation
	Odisha Drawl
	AP Drawl

	
	MU
	Avg (MW)
	MU
	Avg (MW)
	MU
	Avg (MW)

	Apr’18
	37.162
	51.610
	18.613
	25.851
	16.943
	25.532

	May’18
	48.888
	65.700
	22.424
	30.140
	24.492
	32.919

	June’18
	43.185
	59.980
	19.692
	27.350
	21.635
	30.048

	July’18
	45.146
	60.680
	20.894
	28.083
	22.148
	29.769

	Aug’18
	51.319
	68.977
	23.507
	31.595
	25.708
	34.554

	Sept’18
	45.449
	63.123
	20.039
	27.032
	23.324
	32.394

	Oct’18
	50.184
	69.700
	22.268
	30.927
	25.721
	35.726

	Nov’18
	49.688
	69.011
	21.964
	30.506
	25.621
	 35.585

	Dec’18
	52.772
	70.930
	24.878
	33.438
	25.653
	34.479

	Jan’19
	59.629
	80.146
	28.179
	37.875
	29.257
	39.323

	Feb’19
	56.272
	83.738
	26.209
	39.001
	28.068
	41.768

	Total
	539.694
	61.609
	248.667
	28.387
	268.570
	30.659


Drawl of State share power from Machhakund is decreasing for the current Financial Year. Southco may add more feeders to Podagada S/s. In the 128th PSOC meeting Southco stated that the contractor is not turning up for the work. 
SOUTHCO may deliberate.
F. Under Frequency Relay operation in OPTCL System during the month of Feb’19.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of February’19.
G. Status of Open Access applications up to the month of February’2019
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’18
	26
	79
	0
	31
	136
	26
	76
	0
	31
	133
	3

	2
	May’18
	59
	90
	0
	26
	175
	59
	89
	0
	26
	174
	1

	3
	June’18
	14
	57
	0
	30
	101
	14
	57
	0
	30
	101
	0

	4
	July’18
	18
	145
	0
	26
	189
	18
	145
	0
	26
	189
	0

	5
	Aug’18
	26
	90
	0
	37
	153
	26
	90
	0
	37
	153
	0

	6
	Sept’18
	25
	97
	0
	32
	154
	25
	97
	0
	32
	154
	0

	7
	Oct’18
	45
	60
	0
	28
	133
	45
	60
	0
	28
	133
	0

	8
	Nov’18
	39
	95
	0
	35
	169
	39
	95
	0
	35
	169
	0

	9
	Dec’18
	36
	68
	0
	28
	132
	36
	67
	0
	27
	130
	2

	10
	Jan’19
	63
	102
	0
	28
	193
	44
	102
	0
	28
	174
	19

	11
	Feb’19
	29
	58
	0
	35
	122
	26
	58
	0
	35
	119
	3

	
	Total
	380
	941
	0
	336
	1657
	358
	936
	0
	335
	1629
	28


PART C – Issues discussed in the 155th  OCC meeting of ERPC held on 25.03.2019
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
149th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	31.03.19
	162.5 Cr.
Total expenditure may not exceed Rs. 68 Crs.


	38.09Cr. Requisition for 11.00 Cr placed.
	90% equipment installed and commissioned. Stn Tfr and some measuring instruments are under tendering process.



	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.22 Cr
	Request for 10% grant already submitted. Agreement  signed
	Tender floated. Bank mandate to be opened.

	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov18
Chiplima

Dec 2018
	22.35 Cr.
	2.235 Cr
	Placed work order for Balimele

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 
	27-07-18
	
	31.94 Cr
Ested. Cost. Approved amount 30.26 Cr. Grant amount 27.23 Cr.
	27.23 Cr. 10% funding will be asked.
	Agreement signed and sent to NLDC for signature. Tender floated.

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost. 2.93 Cr recommended by Appraisal committee.
	
	Approved by Appraisal committee. Forwarded to CERC for concurrence.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	12.03.2018  Date of submission 
	
	41.1 Cr

Estt cost
	
	Compliance to TSEG observation submitted. Audit observation has been sent to NLDC. 


      CGM (O&M) / OHPC/ SLDC may please update the status.
C.2: Mapping of Feeders of Automatic Under Frequency Load Shedding (AUFLS) Scheme 

In 8th NPC held on 30th November 2018, it was decided that each RPC would submit the details / progress of feeder mapping to NPC secretariat on a regular basis (quarterly). 

 In 154th OCC, DVC informed that mapping of the UFR feeders had already been implemented in DVC system.  

In 40th TCC, Bihar and Jharkhand have confirmed that mapping of the UFR feeders has been implemented. 

West Bengal informed that out of 18 S/s only 6 S/s data are available at SLDC. For the remaining 12 S/s the RTUs are old and needed replacement. WBSETCL added that they have already placed a proposal for PSDF funding.  

OPTCL informed that out of 58 feeders only 14 feeders data are available at SLDC. For mapping of the remaining feeders, the RTUs needed to be replaced as they were old. OPTCL added that replacement of old RTUs is in advance stage and it would be implemented within a year.  
CGM (O&M) / Sr. G.M (Telecom) may deliberate

C.3: Coal requirement for thermal power plants –MoP 

MoP vide letter dated 7th February 2019 informed that, it has been decided that in view of expected increased power demand in the next few months up to monsoons, all power plants be advised to be watchful, and do maintain plant availability and adequate coal stocks as per norms, in this period.  

All the thermal plants are advised to take effective steps for immediate implementation of the decision. The action taken report may also be forwarded to the Ministry at the earliest.  

In 154th OCC, all the thermal generators were advised to assess the requirement of coal in the coming few months and take the necessary action to build up adequate stock to ensure uninterrupted supply of power.  

In 40th TCC, all the thermal generators were advised to inform ERPC Secretariat any hurdle being faced by them in building up the coal stock. If required, a separate meeting would be convened by ERPC Secretariat with the thermal generators, coal companies and the Railways. 

Thermal plants may comply and submit the report. 

C.4: Removal of Vedanta Towers(5 nos) for direct connectivity on permanent basis of 400kV Sundargarh-Raigarh ckt#4 and 400kV Sundargarh-Raigarh ckt#2--Powergrid 

Initially 02 nos LILO was made in 400kV Rourkela-Raigarh ckt-2 and Ckt-4 to evacuate power generation of Sterlite Energy Ltd (Now Vedanta Ltd),Jharsuguda. However, as per directives from ERLDC/ERPC LILO of 400kV Rourkela-Raigarh ckt-2(Now Sundargarh-Raigarh ckt-3) was opened in 2014 and LILO of 400kV Rourkela-Raigarh ckt-4(Now Sundargarh-Raigarh ckt-4) was opened in October 2017. 

As a temporary measure to facilitate immediate disconnection of LILO and making the line direct PG clamps were used in Vedanta Towers. In this process 05nos of Vedanta Towers are there in the 400kv Sundargarh-Raigarh ckt-2 and 4. 03nos between Loc 298-299of 400kV Sundargarh-Raigarh ckt-4 and 02nos of Towers between Loc 834-833 of 400kV Sundargarh-Raigarh Ckt3.The sketch showing the Vedanta Towers in both the circuits is enclosed for ready reference. 

The matter for removal of Towers and making direct connectivity with Raigarh on permanent basis has been discussed several times with M/s Vedanta. But till date no action has been taken by M/s Vedanta for making the line direct after removal of Towers. Maintenance of the said Towers and corridor are not being done. Any outage of these lines due to issues in these towers and span shall not be attributed to POWERGRID.M/s Vedanta may be asked to restored the line as it was before making the Line LILO.  

Vedanta may deliberate

C.5: Implementation of Automatic Generation Control (AGC) in India (at Inter State level) 

CERC in its order dated 13.10.2015 in Petition No. 11/SM/2015 reiterated the need for mandating Primary Reserves as well as enabling Secondary Reserves, through Automatic Generation Control (AGC) as follows: 

(a) All generating stations that are regional entities must plan to operationalise AGC along with reliable telemetry and communication by 1st April, 2017. This would entail a one-time expense for the generators to install requisite software and firmware, which could be compensated for Communication infrastructure must be planned by the CTU and developed in parallel, in a cost effective manner. 
(b) On the other hand, National/Regional/State Load Dispatch Centres (NLDC/RLDCs/SLDCs) would need technical upgrades as well as operational procedures to be able to send automated signals to these generators. NLDC /RLDCs and SLDCs should plan to be ready with requisite software and procedures by the same date. (c) The Central Commission advises the State Commissions to issue orders for intra-state generators in line with this timeline as AGC is essential for reliable operation of India’s large inter-connected grid.” 

The issue was discussed in 8th NPC Meeting held on 30th November 2018, it was decided that each RPC would submit the status of implementation of AGC to NPC.  

In 154th OCC, it was informed that ISGS generators at Barh and Teesta V are in the process of implementation of the AGC as a pilot project. 
It was informed by Member Secretary, ERPC that, during the deliberation in the 8th NPC meeting on 30.11.2019, it emerged that states in the other regions had already taken initiative for implementation of AGC. ERPC was advised to sensitize this issue in the ERPC forum. 

OCC advised Odisha, West Bengal and DVC to identify one generator in their system for implementation of AGC as a pilot project and place the detailed implementation plan in coming TCC Meeting. 
In 40th TCC, NTPC informed that AGC at Barh STPS will be implemented by May, 2019. 

SLDC Odisha informed that they have written a letter in this regard to OPGC also pointed that regulatory changes need to be framed by SERC before implementation of AGC in the state. 

OPGC suggested to implement the AGC in new units to be commissioned shortly. 

DVC confirmed that unit#8 of Mejia TPS has been identified for AGC implementation as a pilot project. 

WBPDCL informed that they will submit the details in OCC meeting. 

The followings were decided in the TCC Meeting: 

1. Status of implementation of AGC shall be regularly monitored in OCC meetings. 

 2. An workshop shall be organised in ERPC wherein NLDC and NTPC will be invited to interact with the ER constituents regarding the experience they have gained in implementing the AGC in other regions. 
 
Members may discuss.  

C.6: Power Assistance at Manique GSS from DVC and at Kendposi GSS from OPTCL –JUSNL 

JUSNL vide letter dated 8th February 2019 informed that they are planning shutdown of 132 KV D/C RCP-ADP line for erection of 05 nos. Multi Circuit Tower in place of existing transmission tower. Erection of Multi Circuit Tower is inevitable for new 132 KY RCP-Jadugoda transmission line due to limitation of vacant corridor. 

 In 154th OCC, JUSNL explained that they needed around 35 MW power from Manique (DVC) and 40 MW power from Joda (OPTCL) S/s during the shutdown of 132kV Ramchandrapur-Adityapur D/C line for 31 days.  

DVC informed that, due to network constraints in DVC system, DVC would not be in a position to give power from Manique (DVC).  

OPTCL informed that the ATRs at Joda are quite old and they are planning to augment the ATRs. Power could be extended to JUSNL only after completion of augmentation of ATR.   

Underlining the need to facilitate the shut-down to JUSNL and at the same time, to ensure system integrity, OCC advised Member Secretary, ERPC to convene a special meeting at ERPC Secretariat to discuss the issue with JUSNL, DVC, OPTCL, ERPC and ERLDC to arrive at an acceptable solution.  

Accordingly, a separate meeting was held on 1st March 2019. After detailed deliberation, the following were decided: 
1. OPTCL shall take shutdown of one 100MVA 220/132kV ATR at Joda from 2nd March 2019 to start the augmentation work 
2. After completion of augmentation of 220/132kV ATR at Joda, JUSNL shall avail the shutdown of 132kV Ramchandrapur-Adityapur D/C line tentatively from 6th April 2019. 
3. OPTCL shall provide additional 40 MW power from Joda (OPTCL) to fed Kendiposi loads during the shutdown period of 132kV Ramchandrapur-Adityapur D/C line 
4. DVC shall provide power support of 35 MW during off peak and 25 MW during peak hours at Manique subjected to availability of unit #3 of Bokaro during the shutdown period of 132kV Ramchandrapur-Adityapur D/C line

OPTCL added that during shutdown of one 100MVA, 220/132kV ATR at Joda from 2nd March 2019, they can only give 20 MW power to Kendiposi during off peak hours and they cannot give any power during peak hours due to significant load growth in Joda area. 
Jharkhand agreed and requested to keep the 220kV Joda-Kendiposi line as idle charged condition so that they can draw railway power in case of any emergency. 
Odisha agreed but requested Jharkhand to avoid power drawal during peak hours.  Jharkhand assured that they would draw power only during emergency after taking consent from OPTCL. 

It was opined that most of the JUSNL loads would be met by 220kV Chandil S/s during shutdown of 132kV Ramchandrapur-Adityapur D/C line. Jharkhand was advised to maintain the reliability of the 220kV Chandil S/s and ensure healthiness of the protection system at Chandil S/s.


Members may discuss.

C.7: Information regarding details of existing transmission system (220 kV and above AC & DC voltage level) in Eastern Region as on 31.12.2018 

 
CEA vide letter dated 29/01/2019 intimated that MoP, GoI has desired information regarding details of state wise growth of transmission system (both interstate and intra state system) over the years to create database of existing transmission system. 

 
Accordingly, it is requested that the information in respect of existing transmission system (both interstate and intra state system) as well as State Power Map and single line Diagram of transmission network including Powergrid (ISTS) and other Transmission Service Provider (TSPs) (as on 31.12.2018) may please be made available in the specified format attached at 
Annexure –B14. I & II to ERPC for onward transmission to CEA / MoP by 28.02.2019. 

Members may furnish
 C.8: Review of the PSS Tuning of Generators in Eastern Region  

PSS tuning meeting was conducted by ERPC on 31st January 2019 where generators from Eastern Region have participated. The MoM of the meeting has been released by ERPC and is available on the website. During the PSS meeting following decision have been taken: 

1. Generators who had already done the PSS tuning shall submit the details of the Excitation System, PSS tuning and its report. The generators shall submit the Generator terminal voltage, Field voltage, Real power, Reactive Power, Generator Speed, and PSS output in excel/.csv format for better analysis of the result.
2. Generators for which PSS tuning was not carried out shall take up the PSS Tuning with OEM immediately.  
3.  Generators for which PSS was not in service shall take up the issue with OEM immediately to bring the PSS into service. 4. For any future tuning, it was recommended to all generators to collect the response along with data in .csv/excel format. 5. All the generators where the PSS tuning was done and PSS not in service shall submit their action plan for PSS Tuning in line with IEGC and CEA standards before the next OCC meeting to ERPC/ERLDC. 

In view of the same five categories have been made for comprehensive checkup and plan for PSS tuning for Eastern region Generating plants, which are given at Annexure-B14.  

Members may update. 
C.9: Bypassing arrangement of LILO of 400kV Lines at Angul 
LILO of Meramundali-Bolangir/Jeypore 400 kV S/C line and LILO of one Ckt of TalcherMeramundali 400 kV D/C line has been done at Angul 765/400kV Sub-station. The bypass arrangement for these circuits were under implementation at Angul by Powergrid.  In 154th OCC, Powergrid informed that bypass arrangement would be completed by March 2019.   

O&M may deliberate.
C.10: Updated Black Start and Restoration procedure of State—ERLDC As per clause IEGC 5.8(b)  

“Detailed plans and procedures for restoration after partial/total blackout of each User’s/STU/CTU system within a Region, will be finalized by the concerned User’s/STU/CTU in coordination with the RLDC. The procedure will be reviewed, confirmed and/or revised once every subsequent year.” 

In 154th OCC all the SLDCs to were advised to submit the updated restoration procedure of their respective state. 

However SLDCs are yet to submit the Black Start and restoration procedure for respective states.  

 
SLDCs may update.
C.11: Periodical Audit and Vulnerability Assessment & Penetration Testing (VPAT) of ICT Infrastructure--CEA 

 
Central Electricity Authority vide letter dated 31st January 2019 informed that a vulnerability has been reported in website of an organization under Power Sector. Any vulnerability present in ICT infrastructure, website, web application etc. may invite attackers to carry out malicious activities. In this case, attackers could exploit the targeted organization.  
To avoid the possibility of Cyber Security related issue by plugging and fixing the vulnerability, it is essential to conduct regular & meaningful audit and Vulnerability Assessment and Penetration testing (VPAT) of all ICT infrastructure in addition to adopting the best practices and guidelines by all Power Sector Organizations.  
In this regard, all Power Sector organizations are requested to ensure periodical audit and Vulnerability Assessment and Penetration testing (VPAT) of all ICT infrastructure by competent auditors and testers. Further, Sectoral CERTs are requested to take immediate action and coordinate with organizations under their purview for the same.  
In 154th OCC, all the constituents were advised to conduct the Audit, Vulnerability Assessment and Penetration Testing (VPAT) of all ICT infrastructure, website, web application etc. and submit a report to CISO, MoP with a copy to ERPC Secretariat. 
CGM (O&M) / IT may deliberate

C.12: Details of Capacitor bank installed in Distribution/Sub transmission network --ERLDC 

Details of capacitor installed in Eastern Region as a whole was last collected in year 2011. The last updated list is given in Annexure-B18. In the meantime, many utilities might have installed additional capacitor bank for better voltage regulation some has also applied for fund form PSDF for installation of capacitor banks.  

Utilities are requested to provide the updated capacitor bank list for record purpose. 

DISCOMs may submit the data.  

C.13: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC 

As a National Grid operator, POSOCO is continuously working for ensuring reliability and security of the Grid. With penetration of more and more renewable energy source the task is becoming complicated day by day.  An accurate dynamic modeling of the National Grid needs modeling of conventional as well as renewable / distributed generation sources. World Bank has engaged Digsilent as consultant for assisting POSOCO for building dynamic model of the Grid. A guideline for dynamic data collection has been developed in consultation with Digsilent Pacific team.    All the utilities are requested to collect data from the grid scale renewable power plants as well as from conventional power plants under their jurisdiction and submit the same to ERLDC/ERPC as early as possible. 

In the 129th PSOC meeting CGM (PP), GRIDCO stated that M/S MGM Solar has been selected for the pilot project

In the 130th PSOC meeting GRIDCO stated that CESU MRT is not co-operating for accessing the energy meter by M/s Chemtrol. CESU representative assured to take up the matter with their MRT wing

GRIDCO may update the status.
C.14: Implementation of Automatic Demand Management Scheme

The latest status along with proposed logic as follows: 
	Sl. No
	State /Utility
	Logic for ADMS operation
	Implementation status/target
	Proposed logic (if different from under implementation logic

	1
	Odisha
	1. System Frequency < 49.9 Hz 
2. Odisha over-drawl > 150 MW
3. DISCOM over-drawl > (40 MW) 
	10 Months

Sent for PSDF approval
	Logic 2 and 3 is AND or OR, in case it is AND then ADMS may not operate when DISCOMs are in schedule but GRIDCO is over drawing due to less generation at State embedded generators.


In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 123rd PSOc meeting SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval

In the 124th PSOC meeting SLDC stated that the revised estimate has been approved in the BoD.

In the 129th PSOC meeting SLDC stated that CERC approval is awaited for tendering.

In the 129th PSOC meeting it was suggested by members that SLDC may write to ERPC in this regard

SLDC may deliberate the status

C.15: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 130th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by March’19. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by July’19.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	220 kV S.C line and Keonjhar S/S (220/33 kV) , 2x20 MVA charged on 31.12.2018. 2nd ckt; March’2019

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019. Order placed.

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	July’2019 


In the 130th PSOC meeting Telecom stated that OPGW and telecom equipment for Keonjhar (PG)-Keonjhar line is not available. CGM (Cont) was requested to process the file and write a letter to Telecom. NESCO stated that two nos of feeders will be completed by end of March’2019 for drawing load from Keonjhar S/S.
CGM (Cont) / CGM (O&M) may update

C.16: Update on status of telemetry  

CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed  NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action.  

x x x
With regard to the State network, this was deliberated in the last meetings that data communication from Narsingpur S/s is not in place. Also date communication from NALCO is not stable. Telecom stated that provision for laying optical fibre in Bhanjanagar-Meramundali line has been kept in PSDF scheme. However, if wave trap foundation will be done at Narsingpur S/S, the data communication can be established. 

In the 129th PSOC meeting it was decided that NALCO shall write to OPTCL for preparation of estimate for laying of Optical fibre. Construction wing of OPTCL agreed for construction of wave trap foundation at Narsingpur S/S.
In the 130th PSOC meeting Sr. G.M (Telecom) stated that NALCO has submitted a request letter in this regard. Wave trap foundation at Narsingpur is yet to be done.
Const./Telecom / NALCO may update the status

C.17: Mock Black start exercises in Eastern Region – ERLDC 

The tentative schedule of black-start exercises for F.Y 2018-19 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2018
	Done on 28.06.2018& 27.09.18
	Last week of January 2019
	March’2019

	3
	Rengali
	2nd week of June 2018
	Done on 18.08.2018
	Last week of November 2018
	Done on 12.02.19

	4
	U. Indravati
	3rd week of June 2018
	Done on 28th Dec’18
	2nd week of February 2019
	

	6
	Balimela
	3rd week of October  2018
	Done on 21st Dec’18
	1st week of March 2019
	Done on 11.03.19

	9
	Burla
	Last week of June 2018
	Done on 07.06.2018
	Last week of February 2019
	Done on 07.03.19


SLDC / OHPC may update. 

 C.18: Submission of Thermal Loading of Transmission line and associated terminal equipment by ISTS licensee  

In line with the MoM of 4th NRCE Meeting dt.03-11-14 and “Operational Guidelines for determination Of TTC, ATC and TRM for the Short-Term Horizon (0-3 Months)” published by NRCE dt.20-02-15, thermal limit for transmission line has to be used for calculation of ATC/TTC. However, the thermal loading of transmission line depend on the Maximum Conductor Temperature, End equipment thermal rating. This has to be submitted by the Owner of the equipment. Further, the equipment owner also has to confirm that relay setting has been aligned so that the line can be operated up to its thermal limit. In the absence of complete details, ERLDC is utilising the data from the CEA Planning Criteria for thermal rating
OCC advised all the other ISTS licensees and STUs to submit the relevant data to ERLDC and ERPC. 
In the 129th PSOC meeting Sr. G.M (CP) stated that thermal loading data has been submitted by them. O&M shall submit the terminal equipment data

In the 130th PSOC meeting O&M was requested to expedite for furnishing the data.

C.G.M (O&M) may deliberate

 C.19: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

 
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.  

As per the information received from the constituents the following generators certified with IS 18001:  • All NTPC stations in Eastern Region  • Teesta, NHPC • All OHPC generating units  • All CESC generating units  • All units of WBPDCL • DGPC units 

In the 129th PSOC meeting O&M stated that 2nd stage internal audit has been done. Report is yet to be received. Process has been initiated for deposit of application money for external audit. On compliance of the observations Certificate may be issued.    

In the 130th PSOC meeting O&M stated that the external audit will be conducted on 7th & 8th March’2019.

CGM (O&M may deliberate
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of February’18:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	6.724
	1.166

	2
	WESCO
	0
	-37.472
	6.440

	3
	NESCO
	0
	-10.212
	2.381

	4
	SOUTHCO
	0
	12.033
	4.549

	
	Total
	0
	- 28.927
	


It is noticed that SOUTHCO & CESU were over drawn during the month while WESCO & NESCO were under drawn. SOUTHCO has deviated 5.717% followed by CESU 2.831% from the scheduled energy while WESCO and NESCO have deviated 0.380 % & 1.247 % respectively. DISCOMs may forecast their drawal in realistic approach to minimise deviation.

SLDC/ Discoms may please deliberate.
D.2: Communication issues 
The status of data communication from CGPs as deliberated in the 124rd PSOC meeting meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	2
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. 
In the 123rd PSOC meeting it was deliberated that RT&C have sought some information from Telecom wing which will be intimated. NALCO stated that due to problem in their internal communication system, data communication to SLDC is being interrupted.
In the 124th PSOC meeting Telecom stated that communication system for Paradeep area industries will be completed by September’2018. Telecom was advised to give a reply to the information sought by RT&C. 

In the 125th PSOC meeting Telecom stated that the information sought by RT&C will be forwarded soon.
In the 126th PSOC meeting it was decided that SLDC shall convene a meeting with Telecom, GCC & RT&C and discuss the issue for filing case before the OERC.

A meeting was convened between SLDC, Telecom, GCC, RT&C, NINL & IRE Ltd on dt.15.01.2019 at SLDC conference hall to discuss the communication issue. Representative of IRE, SLDC, GCC and Telecom were attended the meeting. IRE deliberated that presently CB, CT & CVT are not installed at their end. Tendering for procurement of CB, CT & CVT have already been done, which will be expected by end of April’2019. Due to space constraint at IRE Switch yard, installation of the equipment may not be possible, unless the Switchyard is modified. For modification they may need the help of OPTCL. It was suggested by SLDC that IRE may approach Sr. G.M (O&M), Zone-1, OPTCL in this regard. Simultaneously, they also to write Sr. G.M (Telecom), OPTCL for preparing estimate for extending data communication from their end.

NINL was not present in the meeting.  

In the 129th PSOC meeting it was decided that DGM (O&M), Berhampur and DGM(Cons.), Berhampur shall visit IRE S/W yard and submit a status report to Sr. G.M (O&M), Berhampur. RT&C may file a case before the OERC for non-compliance of extending data communication facility by M/s NINL.
In the 130th PSOC meeting it was decided that RT&C shall file a case before the OERC against the defaulting CGP / Industries and Telecom will provide the required information to them. RT&C vide their letter No. 104(4) dated 01.03.2019 asked Telecom wing to prepare the draft Petition along with the required information to them.  
RT&C may deliberate. Members may discuss 
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 119th PSOC meeting IT stated that Parameters of 16 Nos meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
In the 123rd PSOC meeting IT stated that out of 840 Nos interface meters connected with AMI, 750 Nos are reporting at present. The newly replaced meters are not reporting. 2 Nos. of meters has sent to M/s SECURE meters for study.

In the 127th PSOC meeting IT stated that TCS is demanding Rs. 6.5 lacs for developing the required software. The proposal is placed before the management for approval

In the 128th PSOC meeting IT stated that the memorandum has been placed before the PSC

In the 130th PSOC meeting IT stated that approved letter was yet to be received by them.

IT may update the status
D.4: DISCOM Agenda
SOUTHCO

1. Gridco & OPTCL has billed the power drawn by M/s Vinto energy Solar connected at Tentulikhunti S/S through 132 kV ckts to Southco. Since there is no such agreement with Southco & M/S Vinto Energy Solar, the bills from December’18 to February’2019 may be withdrawn from Southco bill.
2. OPTCL has charged Nerendrapur-TATA 220 kV DC line and the energy drawn by M/S TATA has been incorporated in SOUTHCO drawl. The transmission /Energy bill also raised by OPTCL /GRIDCO. The bills may be withdrawn.

NESCO    

1. 132/33 kV Dhenkikote S/S drawl need to be incorporated in the RVDU.
2. Revision of schedule in case of adverse weather condition.
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Expected to be completed by March’19.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	March’2019

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	Charged on 28.02.2019

	4
	220/33 kV, 2x20 MVA Baliguda S/S
	July’19

	5
	220/33 kV, 2x20 MVA Kalimela S/S
	July’19

	6
	220/33 kV, 2x20 MVA Kasipur S/S
	March’2019. Line charged.

	7
	220/132 /33 kV, 2x100 MVA Aska S/S
	March’19

	8
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’19

	9
	220/132/33 kV Jayapatana S/S(320 MVA)
	July’19

	10
	220/132 kV Pratapsasan S/S(320 MVA)
	Dec’19

	11
	220/132 kV Kesinga S/S (320 MVA)
	July’19

	12
	132/33 kV Betanati S/S
	March’19

	13
	132/33 kV R.Udyagiri S/S
	March’19

	14
	132/33 kV Chikiti S/S
	S/S charged on 25.02.2019


The Discoms are requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement.
CGM (Construction) / DISCOMs may please deliberate the status.
E.2: Major Events in the month of February’19
1. 20.02.2019:  At 15:50Hrs 132 KV Olavar-Chandbali ckt I & II charged. 132/33 KV GIS Grid S/S, Chandbali also charged along with 40MVA Power Transformer.

2. 25.02.2019: At 11:38 Hrs,132 KV Digapahandi - Chikiti ckt - I & II charged. One 40      MVA (132/33 KV) Power Transfomer also charged at Grid S/S, Chikiti.                                                                                                                                           
3. 27.02.2019: At 15:25 Hrs, 220/33 KV, 20 MVA Transformer at Narasinghpur Grid S/S charged.
4. 27.02.2019:  At 17:18 Hrs, 220 kV Narendrapur-TATA ckt-1 charged. Ckt-2 charged at 17:28 Hrs.                                                                                             
5. 28.02.2019:  At 12:38 Hrs , 315 MVA ( 400/220 KV) ICT -03 at Grid S/S, Mendhasal charged.

Members may note

E.3: Important Grid Incidences during the month of February’19.
1) At 06:38 Hrs dt. 21.02.2019 :-Due to bursting of R –ph bus CT of  Balimela-Jayanagar Ckt-I  at Balimela(PH) Switch yard, all running units (#4,#5,#6,#7 & #8) and all 220 kV feeders emanating from Balimela PH tripped with heavy jerk.
2) At 12:30 Hrs dt. 24.02.2019 :-Due to bursting of Y –ph Bus CT of  Balimela-Jayanagar Ckt-III  at Balimela(PH) Switch yard, only running generating unit #5 and all 220 kV feeders emanating from Balimele PH tripped.
3) At 13:29 Hrs. dt. 21.02.2019 :-132 kV Chandaka-Bhubaneswar ckt-II tripped at Chandaka end on two phase fault. Simultaneously, 132 kV Chandaka-Bhubaneswar ckt-I tripped at Bhubaneswar end only. The feeder did not trip at Chandaka end although D/P relay operated. Subsequently 132 kV Chandaka-Mendhasal ckt tripped at Chandaka end. Due to persistence of fault ( resulting due to non-tripping of the line from Chandaka end), 220 kV Chandaka-Mendhasal ckt-II at Mendhasal end  & 220 kV Chandaka-Chandaka-B at Chandaka-B end . And 220 kV side of Auto Trf-1, 2 & 3  and 132 kV side  of Auto Trf  No-1,2,3 & 4 tripped  respectively. Above incident led to  blackout at  Grid S/S Chandaka. 
4) At 17:25 Hrs dt. 26.02.2019 :- 400KV Meramundali - Mendhasal feeder (Main breaker) tripped at Meramundali end on getting DT signal from Mendhasal end. But associated tie breaker(Dia-402) at Meramundali S/S didn’t trip due to mechanical problem in R-ph limb. Hence LBB of tie breaker (Dia-402) operated which led to tripping of 400 KV Meramundali – New Duburi ckt –II. As 400 KV Meramundali – Mendahsal feeder didn’t trip from Mendhasal end, further led to operation of LBB of Mendhasal feeder main beaker at Meramundali end. All lines and ICT connected with 400 KV Bus – I of Meramundali tripped.
O&M may deliberate
E.4: Outage of major transmission Elements during the month of February’19. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration

Dt/time
	Reason

	1
	132 kV Aska-Chatrapur
	18.02.19
18:36
	25.02.2019/ 18:08
	Bursting of R phase CT 

	2
	132 kV Aska-Bhanjanagar-II
	23.02.19 /09:47
	23.02.19/ 21:05
	132KV PT failure.

	3
	132 kV Aska-Bhanjanagar-II
	24.02.19 / 08:28
	25.02.19 / 18:08
	132KV PT failure.

	4
	132 kV TTPS- Chainpal ckt-II
	26.02.19
/ 08:10
	26.02.19
/ 18:31
	Busting of Y ph and B phase  CT.

	5
	132 kV Joda-Kenduposi fdr
	27.02.19
/ 01:38
	27.02.19
/ 15:55
	Tree fallen over conductor between Loc-214 & 215.

	6
	220 kV Joda-RC Pur line 
	25.02.19/00:54
	25.02.19 /17:32
	Tree fallen over conductor between Location No 169 and 170.


O&M may discuss
E.5:  Review of Outage Program of State Generators / Transmission elements for the month of April’19:
Tentative Outage programme for State Generators for the month of April’2019 
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 4
# 5

# 6
	14.03.18 to continue
25.10.18 to continue
25.10.16 to continue

16.10.15 to continue
	T&G coupling cover water leakage
Annual Maintenance

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to continue
	Under R,M & U

	3
	Balimela
	# 1
# 2
	05.08.16 to continue
20.11.17 to continue
	Under R,M & U

Programming for R&M

	4
	Rengali
	# 2
	12.12.18 to continue
	Replacement of Runner disc.

	5
	Upper Kolab
	# 4
	01.02.19 to continue
	Capital maintenance work



OHPC may deliberate
E.6: Generation Program for the month of April’19.
Generation schedule for the month of April’19 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.03.19
	Reservoir Level as on 01.03.18
	MDDL
	High Flood    Reservoir Level

	
	Apr’19
(1st fortnight)
	Apr’19
 (2nd fortnight)
	
	
	
	

	HPS-I, Burla
	35
	35
	620.00 ft.
	620.97 ft.
	590 ft.
	630 ft.

	HPS-II, Chiplima
	25
	25
	-
	-
	-
	-

	Balimela
	360
	360
	1498.00 ft.
	1458.70 ft.
	1440 ft.
	1516 ft.

	Rengali
	50
	50
	116.34 mtr.
	121.64 mtr.
	109.72mtr 
	123.5 mtr.

	U.Kolab
	140
	140
	853.03 mts.
	852.00 mtr.
	844 mtr 
	858 mtr.

	U. Indravati
	360
	360
	636.66 mtr.
	634.06 mtr.
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2735.40 ft.
	2744.20 ft.
	2685 ft.
	2750 ft.

	TOTAL
	1000
	1000
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

SLDC / OHPC may deliberate

E.7: Anticipated power generation and demand for the month of April’2019.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1200
	1400

	2
	WESCO
	1200
	1400

	3
	NESCO
	850
	950

	4
	SOUTHCO
	350
	400

	5
	Total Discom
	3600
	4150

	
	System Loss & others 
	150
	200

	
	Total Demand
	3750
	4350

	Availability
	
	

	1
	Hydro
	1000  
	1200

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	600
	600

	4
	ISGS share (including OA& purchase)
	1050
	1450

	5
	CGP support (OA)
	350
	350

	6
	Total availability
	3750
	4350

	7
	Surplus / Deficit
	0
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (132nd) PSOC meeting.
PAGE  

