                                                                                                                  
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image1.png]PTC




Agenda

for

133rd Power System Operational Co-ordination Meeting

Date: 29.05.2019
Venue: Power Training Center, Chandaka, Bhubaneswar 
Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 133rd PSOC Meeting to be held on 29.05.2019 at OPTCL Power Training Center, Chandaka, Bhubaneswar
A. Confirmation of the minutes of the 132nd PSOC Meeting held on 19.04.2019
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2019/1322 (48) dated 15.05.2019 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there are no comments, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   :  Grid Performance for the month of April’2019
C.1: Status of projects funded under PSDF scheme 
C.2: Erroneous Energy data of 220kV Balangir-Katapalli line at Bolangir ---SLDC, Odisha
C.3: Guidelines for rationalized use of high performance conductors—CEA
C.4: Review of the PSS Tuning of Generators in Eastern Region  
C.5: Ratification of Demand and Generation for calculation of POC of Q-2 2019-20--ERLDC
C.6: Implementation of Automatic Demand Management Scheme.

C.7: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s 
C.8: Bypassing arrangement of LILO of 400kV Lines at Angul 
C.9: Update on status of telemetry  
C.10: Transfer capability determination by the states  
C.11: Mock Black start exercises in Eastern Region 
C.12: Submission of Thermal Loading of Transmission line and associated terminal equipment by ISTS licensee .

C.13: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC C.14: Implementation of Automatic Generation Control (AGC) in India (at Inter-State level)
C.15: Maintenance and support (AMC) renewal of PSSE software.
C.16: Updated Black Start and Restoration procedure of State—ERLDC
C.17: Shutdown proposal of transmission lines and generating units. 
C.18: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

C.19: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

C.20: Commissioning of new transmission elements in Eastern Region 
D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Communication issues.
D.3: Data communication from newly commissioned RE sources connected at 132 kV- SLDC.

D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.5: Colony consumption of POWERFRID S/Ss
D.6: Collection of modelling data for new Transmission elements / Generators  for system study.
E.1: Commissioning status of New Transmission elements. 

E.2: Major Events in the month of March’19
E.3: Important grid incidences during the month of April’19.

E.4: Outage of major transmission Elements during the month April’19. (above 10 hrs).
E.5: Review of Outage Program of State Generators for the month of June’2019
E.6: Generation Program for the month of June’2019.

E.7: Anticipated power generation and demand for the month of June’2019.
F.1: Date and Venue of the next (134th ) PSOC meeting
PART B: GRID PERFORMANCE
B. Review of Grid Performance for the month of April’19.

A. Frequency:

Hourly frequency variation for the month of April’19.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	Feb’19
	0.00
	0.00
	5.91
	67.23
	26.87
	49.99

	Mar’19
	0.00
	0.02
	8.31
	70.28
	21.39
	49.99

	Apr’19
	0.00
	0.02
	6.49
	68.13
	25.37
	49.99


Maximum & Minimum frequency during the month of Feb’19 & Mar’19.
	Month
	Freq (Hz)
	Date
	Time

	Mar’19
	Maximum –50.21
	01.03.19
	04:30 Hrs

	
	Minimum – 49.71
	11.03.19
	14:15 Hrs

	Apr’19
	Maximum –50.25
	07.04.19
	01:00 Hrs

	
	Minimum – 49.72
	03.04.19
	14:45 Hrs


Grid Demand for the month of April’19
	 Month
	Max. Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	Apr’19
	113.14
	05.04.19
	2786
	3869
	5151
	04.04.19
	20:00
	2689
	20.04.19
	05:00

	Apr’18
	92.65
	23.04.18
	2400
	3334
	4430
	22.04.18
	21:00
	2348
	01.04.18
	24:00


B. Voltage Profile of 220 kV Buses in OPTCL system for the month of: April’19
	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Atri
	230.93
	21
	20:00
	211.59
	16
	15:00

	2
	Balasore
	231.63
	21
	18:00
	210.38
	28
	22:30

	3
	Barkote
	229.89
	23
	01:00
	223.95
	4
	15:30

	4
	Bargarh
	227.24
	9
	18:45
	209.75
	15
	11:30

	5
	Bhadrak
	230.24
	21
	19:00
	209.40
	2
	13:00

	6
	Bhanjanagar
	231.22
	21
	20:00
	217.08
	16
	12:00

	7
	Bidanasi
	234.69
	22
	04:30
	211.59
	29
	14:15

	8
	Bolangir
	226.89
	9
	18:45
	208.94
	7
	16:30

	9
	Budhipadar
	230.01
	19
	06:00
	224.29
	9
	10:00

	10
	Chandaka
	230.30
	21
	19:45
	207.72
	16
	15:00

	11
	Cuttack
	230.99
	21
	19:15
	206.40
	27
	12:15

	12
	Duburi(O)
	230.18
	21
	20:00
	217.42
	27
	15:30

	13
	Duburi (N)
	228.91
	21
	20:00
	216.15
	26
	16:30

	14
	Jayanagar
	235.67
	6
	09:45
	224.35
	4
	12:45

	15
	Joda
	234.51
	21
	16:30
	216.96
	4
	19:15

	16
	Katapalli
	225.68
	19
	06:00
	213.38
	4
	16:15

	17
	Lapanga
	229.43
	19
	06:00
	222.62
	4
	16:15

	18
	Laxmipur
	232.95
	6
	09:45
	222.50
	4
	 12:45

	19
	Mendhasal
	233.18
	21
	20:00
	211.71
	16
	15:00

	20
	Meramundali
	226.37
	23
	03:45
	219.79
	4
	19:15

	21
	Narendrapur
	228.16
	21
	20:15
	206.57
	16
	12:00

	22
	Nayagarh
	231.40
	21
	19:45
	212.57
	29
	14:15

	23
	Paradeep
	230.30
	21
	20:00
	202.70
	27
	14:45

	24
	Tarkera
	230.01
	23
	01:00
	212.81
	8
	18:45

	25
	Theruvali
	227.93
	6
	9:45
	213.56
	7
	17:00

	26
	Samangara
	230.59
	21
	20:00
	210.44
	16
	15:00


The maximum Voltage of 235.67 kV occurred at Jayanagar 220 kV bus, while Paradeep 220 kV bus has experienced the minimum Voltage of 202.70 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Mendhasal, Meramundali  and New Duburi bus during the month of April’2019 are indicated. 
[image: image2.emf]210

215

220

225

230

235

240

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF JAYANAGAR  220 kV BUS

FOR  APRIL 2019


[image: image3.emf]200

205

210

215

220

225

230

235

240

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NARENDRAPUR 220 kV BUS

FOR APRIL 2019


[image: image4.emf]375

380

385

390

395

400

405

410

415

420

425

430

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MENDHASAL  400 kV BUS

FOR APRIL 2019


[image: image5.emf]390

395

400

405

410

415

420

425

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MERAMUNDALI 400 kV BUS

FOR APRIL 2019


[image: image6.emf]390

395

400

405

410

415

420

425

430

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NEW DUBURI 400 kV BUS

FOR APRIL 2019


Members may discuss.
C. Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of April – 2019. [image: image7.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  APRIL'2019

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

47.08 18 22:00 6.28 28 07:15

47.08 18 22:00 6.20 28 07:15

84.40 26 22:15 25.60 8 21:00

84.40 25 22:45 25.60 8 21:00

85.88 25 21:45 26.04 8 20:00

1x100

14.80 18 16:30 4.64 6 16:30

1x160

17.44 13 12:15 4.60 2 18:15

1x100

Under idle charge condition

1x160 72.60 27 22:30 5.92 6 22:45

1x160 72.56 27 22:30 5.92 6 22:45

1x160 81.84 26 12:00 17.76 23 15:15

1x160 72.04 26 12:00 15.52 23 15:15

1x100 29.08 3 14:15 4.92 6 23:45

1x100 28.72 3 14:15 5.56 6 23:45

1x160 41.36 3 14:15 7.40 6 23:45

134.48 4 10:45 13.80 19 23:15

137.72 26 19:30 14.56 19 23:15

117.12 9 14:30 3.28 8 10:15

124.36 8 16:30 10.72 19 12:00

1x100 71.44 16 15:00 4.56 8 13:15

1x160 123.00 16 15:00 9.16 21 19:15

1x100 85.96 27 07:15 5.56 8 13:30

1x160 105.04 30 15:00 10.88 31 21:15

1x160

72.60

1 22:15 4.36 11 18:45

1x100

44.12

1 22:15 3.73 3 07:15

1x160 116.68 27 12:15 35.20 11 15:45

1x100 74.20 27 12:15 22.04 11 15:45

1x100 67.96 27 11:00 10.04 23 18:30

1x160 84.92 29 21:15 22.60 25 17:00

1x160 85.28 29 21:15 22.72 25 17:00

61.80 12 10:00 17.48 21 15:30

64.40 12 11:15 16.56 21 15:15

56.00 7 20:15 17.20 21 15:15

1x100 93.32 15 05:15 7.16 3 12:30

1x100 93.88 15 05:15 7.04 3 12:30

1x160

72.12 13 19:30 3.32 6 15:00

124.24 9 16:30 24.76 4 13:45

47.04 29 14:15 5.12 12 02:15

46.20 29 14:15 5.12 12 02:15

44.92 29 14:15 4.60 12 02:00

108.60 6 19:15 49.84 1 00:30

108.32 6 19:15 29.96 26 11:15

1x100 62.40 6 19:30 28.52 1 00:30

1x160 140.32 6 21:00 7.68 6 23:45

1x100 85.68 6 21:00 4.48 6 23:45

4x100  69.44 13 20:15 3.40 8 17:45

78.88 9 15:00 3.92 8 17:45

72.44 9 15:00 3.44 8 17:45

71.88 9 15:00 3.96 8 17:45

2x100 50.28 3 21:45 2.76 5 10:45

47.72 3 21:45 5.80 19 10:30

1x160 77.92 3 21:45 8.08 19 10:30

1x160  119.36 26 06:45 0.00 22 08:45

1x160 119.36 26 06:45 0.00 22 08:45

2x160 59.60 19 21:45 26.00 11 19:00

97.20 19 09:15 9.20 21 20:15

SAMANGARA                                          

{ Puri, Nimapara & Konark}

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 



THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

Rayagada & 

Paralakhemundi can be fed 

from Machhkund system.

TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 



Mendhasal { Part area load of Khurda S/S} 2x100

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, 

Digapahandi, Mohana.}

2x160



PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & 

Katapali area load.}

Supported by Burla & 

Chipilima power.

LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

2x160

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100

CUTTACK

DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, 

Jajpur Road, Kalarangi, Jajpur Town}



JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

3x100 

"*" - Alternate P/S from 

Kuchei.

BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

2x160

BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), 

MCL, Sundergarh,Brajarajnagar, 

Rajgangpur}

2x160 



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }



BARGARH 220/132 kV

BHADRAK 220/132 KV

{Bargarh, Ghensh}

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}



BIDANASI 220/132 KV

{Bidanasi, Khurda }



Drawal details

Maximum Minimum

ATRI                                                     

{Banki, Khurda, Chandpur & Argul}

2x160

BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

3x160 


D. DISCOM Drawal for the month of April’19
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	Apr’19
	798
	760.542
	857.404
	18.345
	839.059
	78.517

	WESCO
	Apr’19
	635
	649.188
	856.374
	149.999
	706.375
	57.187

	NESCO
	Apr’19
	517
	478.905
	600.692
	99.608
	501.084
	22.179

	SOUTHCO
	Apr’19
	331
	303.576
	334.361
	0
	334.361
	30.785


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
Members may please discuss.

E. Energy Generation / Import for the month of April’19
Figures in MU  
	Month
	Thermal

(TTPS+IbTPS)
	OHPC 
& MKD
	CGP Support
	IPP Inj.
	RE
	ISGS
	Total

	April’19
	588.681
	538.473
	308.480
	263.019
	29.852
	1057.035
	2785.54

	Total
	588.681
	538.473
	308.480
	263.019
	29.852
	1057.035
	2785.54


F.  Drawal of Machhakund Power
The drawal of Machhakund power for the month of April’19 are as detailed:
	Month
	Total Generation
	Odisha Drawl
	AP Drawl

	
	MU
	Avg (MW)
	MU
	Avg (MW)
	MU
	Avg (MW)

	Apr’19
	53.168
	73.844
	24.896
	34.577
	26.401
	36.668

	Total
	53.168
	
	24.896
	
	26.401
	


Drawl of State share power from Machhakund has decreased during the month. Southco may add more feeders to Podagada S/s. 
SOUTHCO may deliberate.
G. Under Frequency Relay operation in OPTCL System during the month of April’19.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of April’19.
H. Status of Open Access applications up to the month of April’2019
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’19
	48
	100
	0
	24
	172
	48
	100
	0
	24
	172
	o

	
	Total
	
	
	
	
	
	
	
	
	
	
	


PART C – Issues discussed in the 157th  OCC meeting of ERPC held on 20.05.2019

C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	31.03.19
	162.5 Cr.
Total expenditure may not exceed Rs. 68 Crs.
	38.09Cr. Received Rs. 8.00 Cr on 28.03.19 
	90% equipment installed and commissioned. Order placed for Stn Tfr and tender for measuring instruments under evaluation.

	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.22 Cr

	2.56 Cr received as 10 % DPR. Claimed for 20 %.
	Order placed.



	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov18
Chiplima

Dec 2018
	22.35 Cr.
	2.235 Cr
	Placed work order for Balimela. PO for other units amounting Rs. 2 Crs placed. Tendering for Rs 7 Cr under finilazation.

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 
	27-07-18
	
	31.94 Cr
Ested. Cost. Approved amount 30.26 Cr. Grant amount 27.23 Cr.
	Rs.2.72 Cr received as 10% of DPR. Retendering under process.
	Agreement signed and sent to NLDC for signature. Tender is under evaluation. Bank mandate submitted.

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost. 2.93 Cr recommended by Appraisal committee.
	
	Approved by Appraisal committee. Forwarded to CERC for concurrence.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	12.03.2018  Date of submission 
	
	41.1 Cr

Estt cost
	10% of DPR to be asked.
	Project approved.  Tender to be floated. 


      CGM (O&M) / OHPC/ SLDC may update the status

C.2: Erroneous Energy data of 220kV Balangir-Katapalli line at Bolangir ---SLDC, Odisha 

The agenda received from SLDC, Odisha is enclosed at Annexure-B10. 

In 156th OCC, GRIDCO informed that they had incurred huge commercial loss in DSM charges because of the erroneous SEM reading at Bolangir and requested for modification of DSM accounts for the affected period.  

OCC noted that the issue has been raised after a lapse of more than two years. OCC advised GRIDCO to establish the fact that the meter reading of SEM of Bolangir is erroneous and the other end readings are o.k. OCC advised to submit the relevant documents to ERPC Secretariat for scrutiny. After receiving the documents from GRIDCO, ERPC Secretariat would study the case and place the details in next OCC and Commercial Meeting.   
SLDC shall furnish the details to ERPC and ERLDC for study and taking a decision.

SLDC may deliberate

C.3: Guidelines for rationalized use of high performance conductors—CEA 

CEA vide letter dated 9th April 2109 informed that use of high performance conductors is on rise to address issues of growing congestion in the existing network and to utilize ROW more effectively.  

CEA has released a document titled “Guidelines for rationalized use of high performance conductors” to create awareness on use of the conductors. Softcopy of the document is available at: http://cea.nic.in/reports/others/ps/psetd/guidelines_conductors.pdf 

O&M may note.  
C.4: Review of the PSS Tuning of Generators in Eastern Region  

On 31st January 2019, PSS Tuning Meeting was held at ERPC. All generating utilities were advised to complete the PSS tuning of their plant at earliest for improvement of damping in the grid during transients. In addition, the tuning reports have also to be submitted to ERLDC/ERPC for their validation. 
In the 131st PSOC meeting OPGC stated that they have already furnished the data to ERPC. GMR and Vedanta were requested to furnish the data soon to ERPC.
In the 132nd PSOC meeting Vedanta stated that they have already furnished the data. GMR was not present to deliberate.
GMR may deliberate

C.5: Ratification of Demand and Generation for calculation of POC of Q-2 2019-20--ERLDC 

The projected Demand and Generation of ER constituents to be considered in the base case for POC transmission charge and loss calculations for Q2 (July 19-Sep 19)  was circulated to all the concerned via email dated 8th May  August 2019 for comments and verification.

GRIDCO deliberated to consider the State’s demand excluding Vedanta import through Open Access.

GRIDCO may deliberate   

C.6: Implementation of Automatic Demand Management Scheme

The latest status along with proposed logic as follows: 
	Sl. No
	State /Utility
	Logic for ADMS operation
	Implementation status/target
	Proposed logic (if different from under implementation logic

	1
	Odisha
	1. System Frequency < 49.9 Hz 
2. Odisha over-drawl > 150 MW
3. DISCOM over-drawl > (40 MW) 
	10 Months

Sent for PSDF approval
	Logic 2 and 3 is AND or OR, in case it is AND then ADMS may not operate when DISCOMs are in schedule but GRIDCO is over drawing due to less generation at State embedded generators.


In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 123rd PSOc meeting SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval

In the 124th PSOC meeting SLDC stated that the revised estimate has been approved in the BoD.

In the 129th PSOC meeting SLDC stated that CERC approval is awaited for tendering.

CERC has approved the revised estimate. SLDC shall process for tendering.
In the 132nd PSOC meeting it was decided that a committee will be constituted with representatives from SLDC, Telecom, IT and DISCOMs to finalize the implementation of the scheme.

SLDC may deliberate
C.7: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 132nd PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by March’19. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by July’19.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	220 kV S.C line and Keonjhar S/S (220/33 kV) , 2x20 MVA charged on 31.12.2018. 2nd ckt; April’’2019

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019. Order placed.

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	July’2019 


In the 132nd PSOC meeting NESCO stated that they have already taken action for downstream takeoff arrangements from Keonjhar S/S. Telecom stated that for charging of Keonjhar-Keonjhar (PG) 2nd ckt, CARD has already been received and ABB engineers has reached the spot. Expected by April’ 2019.

CGM (Cont) / CGM (Telecom) may deliberate

C.8: Bypassing arrangement of LILO of 400kV Lines at Angul 

LILO of Meramundali-Bolangir/Jeypore 400 kV S/C line and LILO of one Ckt of Talcher-Meramundali 400 kV D/C line has been done at Angul 765/400kV Sub-station. The bypass arrangement for these circuits is under implementation at Angul by Powergrid.  

In 157th OCC, Powergrid informed that bypass arrangement would be completed by June 2019.   

OPTCL may please inform the commissioning schedule of the 2nd circuit of 400kV Meramundali-Mendhasal line. 

Powergrid and OPTCL may update.

C.9: Update on status of telemetry  

CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed  NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up 

the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action.  

Major issues are given below: 

xxxxxxxxx.

In the 132nd PSOC meeting CGM (Telecom) stated that survey work for Meramundali-Bhanjanagar line is under process. OPGW will be reached at site after completion of survey and preparation of drum schedule. DGM (Telecom) stated that the vender list and rate will be provided to NALCO for placement of order by them.

Telecom / NALCO may deliberate the status

C.10: Transfer capability determination by the states  

In order to ensure, safe and secure operation of the grid, the states should carry out the power system study for operational planning and power transfer capability through their respective transmission links with the rest of the grid. 

It was decided in the NPC meeting that to begin with, power system study for assessment of operational limits / power transfer capability for each state will be done by the concerned RLDC in association with concerned SLDC. Monthly TTC /ATC will be uploaded by the SLDCs at their respective websites and also communicated to concerned RLDC & NLDC subsequently.

SLDC deliberated that Odisha have furnished the data up to September’2019

SLDC may deliberate

C.11: Mock Black start exercises in Eastern Region – ERLDC 

	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2019
	
	Last week of January 2020
	

	3
	Rengali
	2nd week of June 2019
	
	Last week of November 2020
	

	4
	U.Indravati
	3rd week of June 2019
	
	2nd week of February 2020
	

	6
	Balimela
	3rd week of October  2019
	
	1st week of March 2020
	

	9
	Burla
	Last week of June 2019
	
	Last week of February 2020
	


Format for Reporting of Mock Black Start Activity: 

Mock drill on Black start is a continuous activity ongoing in the power system. In addition to black start mock drill, it is essential to monitor each black start to check the performance. ERLDC is in receipt of reports from various black start stations performing these activities from their respective SLDC however, many a times essential information pertaining to performance monitoring of the activities are missing. In view of this it is proposed that, for any mock drill on black start, SLDC must share the following details to access the performance and  the same need to be intimated one week before to ERLDC along with black start process. This will help in finding out any challenges and sharing of experiences with other utilities. 

1. Name and Contact of Personnel available at SLDC: 
2. Name and Contact of Personnel available at Generating Plant: 
3. Name and Contact of Personnel available at Load Substation: 
4. Single Line diagram of the mock drill: 
5. Details of Steps taken for Mock Drill 

Table 1: Performance monitoring of Mock Drill 
	Activity
	Time (Minutes)

	Time taken to start DG set after black out of Island 


	

	Time taken to charge dead bus at Black start station 
	

	Time taken to charge dead bus at Remote end by line charging
	

	Time taken to connect first load post a black out in the island
	

	Duration of stable island operation after successful black start and building up the of the island till synchronization with grid
	

	Time taken to synchronize the island with Grid
	


6. Issues Observed: 
7. Remedial Action Taken if Any for the challenges: 
8. Any other details:  

SLDC / OHPC may note
C.12: Submission of Thermal Loading of Transmission line and associated terminal equipment by ISTS licensee  

In line with the MoM of 4th NRCE Meeting dt.03-11-14 and “Operational Guidelines for determination of TTC, ATC and TRM for the Short-Term Horizon (0-3 Months)” published by NRCE dt.20-02-15, thermal limit for transmission line has to be used for calculation of ATC/TTC. However, the thermal loading of transmission line depend on the Maximum Conductor Temperature, End equipment thermal rating. This has to be submitted by the Owner of the equipment. Further, the equipment owner also has to confirm that relay setting has been aligned so that the line can be operated up to its thermal limit. In the absence of complete details, ERLDC is utilising the data from the CEA Planning Criteria for thermal rating.

OCC advised all the other ISTS licensees and STUs to submit the relevant data to ERLDC and ERPC. 
In the 129th PSOC meeting Sr. G.M (CP) stated that thermal loading data has been submitted by them. O&M shall submit the terminal equipment data

In the 131st PSOC meeting O&M was requested to expedite for furnishing the data.

In the 132nd PSOC meeting O&M stated that they will submit the data y 15th May 2019
O&M may update

C.13: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC 

As a National Grid operator, POSOCO is continuously working for ensuring reliability and security of the Grid. With penetration of more and more renewable energy source the task is becoming complicated day by day.  An accurate dynamic modeling of the National Grid needs modeling of conventional as well as renewable / distributed generation sources. World Bank has engaged Digsilent as consultant for assisting POSOCO for building dynamic model of the Grid. A guideline for dynamic data collection has been developed in consultation with Digsilent Pacific team.   All the utilities are requested to collect data from the grid scale renewable power plants as well as from conventional power plants under their jurisdiction and submit the same to ERLDC/ERPC as early as possible. 

In the 132nd PSOC meeting, all generators as well as RE sources were requested to furnish data to SLDC for onward transmission to ERPC.
SLDC requested ERPC to forward the format for preparing the data. The format will be circulated to all RE & conventional generators in the State 
SLDC may deliberate

C.14: Implementation of Automatic Generation Control (AGC) in India (at Inter-State level) 

The issue was discussed in 8th NPC Meeting held on 30th November 2018, it was decided that each RPC would submit the status of implementation of AGC to NPC.  

In 40th TCC, NTPC informed that AGC at Barh STPS will be implemented by May, 2019. 

DVC confirmed that unit#8 of Mejia TPS has been identified for AGC implementation as a pilot project. 

The followings were decided in the TCC Meeting: 

1. Status of implementation of AGC shall be regularly monitored in OCC meetings. 

2. A workshop shall be organized in ERPC wherein NLDC and NTPC will be invited to interact with the ER constituents regarding the experience they have gained in implementing the AGC in other regions. 

In 155th OCC, NTPC informed that implementation of AGC at Unit#4 & 5 of Barh STPS are in progress and was expected to complete by May 2019.  

Odisha informed that unit#3 of OPGC had been selected for implementation of AGC.  

WBPDCL informed that unit#5 of Bakreswar had been selected for implementation of AGC.  

In 156th OCC, OCC decided to organize the workshop at ERPC in May 2019 wherein NLDC, NTPC and Siemens will be invited to interact with the ER constituents.  

The workshop on AGC would be held on 31st May 2019 at ERPC, Kolkata.  

OHPC / OPGC / GMR/ Vedanta may note.  

C.15: Maintenance and support (AMC) renewal of PSSE software.  

Siemens vide letter dated 20th March 2019 informed that the AMC for PSSE software has ended on 30th November 2018.  

Siemens requested ERPC Secretariat to renew the maintenance and support period for all the existing supplied licenses of states for next five years.  

In 156th OCC, All the SLDCs in the meeting agreed for renewal of the AMC of PSSE software for next five years and requested to take up the AMC contract jointly for all the states with the Siemens as it was done during the procurement of software.   

OCC advised ERLDC to take up the issue with NLDC and CTU.  

SLDC / O&M / GRIDCO may discuss
C.16: Updated Black Start and Restoration procedure of State—ERLDC As per clause IEGC 5.8(b)  

“Detailed plans and procedures for restoration after partial/total blackout of each User’s/STU/CTU system within a Region, will be finalized by the concerned User’s/STU/CTU in coordination with the RLDC. The procedure will be reviewed, confirmed and/or revised once every subsequent year.” 

In 154th OCC all the SLDCs to were advised to submit the updated restoration procedure of their respective state. 


SLDC has developed a draft Black start Restoration procedure and circulated to OHPC /&O&M for comments. Since no comments have been received till date, the draft procedure is finalized and will be submitted to ERLDC / ERPC.

O&M/OHPC may deliberate 
C.17: Shutdown proposal of transmission lines and generating units 

In 151st OCC, it was observed that constituents had not submitting the shutdown requisition within stipulated time as a result ERLDC had been facing difficulty in properly analyzing the shutdown. 

OCC decided the following procedure for submission of transmission elements outage requisition:  

1. Shutdown of Intra Regional Lines- Transmission licensee/SLDCs/Transmission Asset owners shall apply shutdown of their respective Intra Regional Lines for the next month to ERLDC strictly by 8th of every Month. Based on this, ERLDC shall prepare the list which would be placed in OCC Agenda. Any shutdown requisition received after 8th of the month would not be normally considered for discussion in the OCC meeting unless it is considered to be an emergency requirement.   
2. Shutdown of Inter Regional Lines - Transmission licensee/ SLDCs/Transmission Asset owners shall send their shutdown requisition of Inter Regional Lines for the next month directly to NLDC strictly by 5th of every month with a copy to respective RLDCs.
O&M may circulate the above guide lines to all field units to follow while submitting shutdown proposal. 
O&M may discuss

C.18: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

The activity of the preparation of Crisis Management Plan for countering the cyber-attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA. 

In 142nd OCC, ERLDC informed that, in line with Enquiry Committee Recommendation, cyber security audit is being conducted on regular basis for SCADA system installed at ERLDC and SLDC as well but cyber security audit for telecom infrastructure installed in Eastern Region is not being carried out.  

OCC advised all the constituents to conduct the cyber security audit on telecom infrastructure installed in Eastern Region. It is further advised that compliance / mitigation of the points observed during the audit should also be completed for improvement of the telecom infrastructure in ER. 

As suggested by CEA, a format has been circulated among ER constituents for furnishing the information of the respective systems for discussion in OCC Meeting. The format is enclosed at Annexure-E1. 

OCC advised all the constituents to submit the information to ERPC as per Annexure-E1.
Sr. G.M (IT) may deliberate

C.19: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

 
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.  

As per the information received from the constituents the following generators certified with IS 18001:  • All NTPC stations in Eastern Region • Teesta, NHPC • All OHPC generating units  • All CESC generating units  • All units of WBPDCL • DGPC units 

In the 129th PSOC meeting O&M stated that 2nd stage internal audit has been done. Report is yet to be received. Process has been initiated for deposit of application money for external audit. On compliance of the observations Certificate may be issued.    

In the 131st PSOC meeting O&M stated that Audit has been completed but the report is yet to be received.
In the 132nd PSOC meeting O&M stated that external audit stage-I completed. On completion Stage-II external audit certificate may be received.

CGM (O&M) may deliberate
C.20: Commissioning of new transmission elements in Eastern Region 

The details of new units/transmission elements commissioned in the month of April-2019 based on the inputs received from beneficiaries 

Monthly commissioning List of Transmission element and generators: April 2019 

	Sl No
	Element Name
	Owner
	Charging Date
	Charging Time
	Remarks

	1
	800 MW Darlipali unit 1 (G.T. 1)
	NTPC
	04-04-2019
	09:02
	

	2
	765 KV Jharsuguda- Raipur I
	OGPTL
	04-04-2019
	21:12
	

	3
	765 KV Jharsuguda- Raipur I
	OGPTL
	05-04-2019
	23:32
	

	4
	LILO  132 KV Udala-Baripada SC line at Betanoti S/S 
	OPTCL
	19-04-2019
	14:02
	 (3.104 Kms) in existing line


PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of April’19:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	78.517
	10.323

	2
	WESCO
	0
	57.187
	8.809

	3
	NESCO
	0
	22.179
	4.631

	4
	SOUTHCO
	0
	30.785
	10.140

	
	Total
	0
	188.668
	


It is noticed that all the DISCOMs were over drawn during the month CESU has deviated 10.323% followed by SOUTHCO 10.140% from the scheduled energy while WESCO and NESCO have deviated 8.809 % & 4.631 % respectively. DISCOMs may forecast their drawal in realistic approach to minimise deviation.

SLDC/ Discoms may please deliberate.
D.2: Communication issues 
The status of data communication from CGPs as deliberated in the 124rd PSOC meeting meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	2
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. 
In the 123rd PSOC meeting it was deliberated that RT&C have sought some information from Telecom wing which will be intimated. NALCO stated that due to problem in their internal communication system, data communication to SLDC is being interrupted.
In the 124th PSOC meeting Telecom stated that communication system for Paradeep area industries will be completed by September’2018. Telecom was advised to give a reply to the information sought by RT&C. 

In the 125th PSOC meeting Telecom stated that the information sought by RT&C will be forwarded soon.
In the 126th PSOC meeting it was decided that SLDC shall convene a meeting with Telecom, GCC & RT&C and discuss the issue for filing case before the OERC.

A meeting was convened between SLDC, Telecom, GCC, RT&C, NINL & IRE Ltd on dt.15.01.2019 at SLDC conference hall to discuss the communication issue. Representative of IRE, SLDC, GCC and Telecom were attended the meeting. IRE deliberated that presently CB, CT & CVT are not installed at their end. Tendering for procurement of CB, CT & CVT have already been done, which will be expected by end of April’2019. Due to space constraint at IRE Switch yard, installation of the equipment may not be possible, unless the Switchyard is modified. For modification they may need the help of OPTCL. It was suggested by SLDC that IRE may approach Sr. G.M (O&M), Zone-1, OPTCL in this regard. Simultaneously, they also to write Sr. G.M (Telecom), OPTCL for preparing estimate for extending data communication from their end.

NINL was not present in the meeting.  

In the 130th PSOC meeting it was decided that RT&C shall file a case before the OERC against the defaulting CGP / Industries and Telecom will provide the required information to them. RT&C vide their letter No. 104(4) dated 01.03.2019 asked Telecom wing to prepare the draft Petition along with the required information to them.  
In the 131st PSOC meeting it was decided that T&C and Telecom shall discuss and prepare the Petition to file before the OERC.

In the 132nd PSOC meeting RT&C stated that the draft Petition has been prepared.

RT&C and Telecom may update the status
D.3: Data communication from newly commissioned RE sources connected at 132 kV- SLDC
There are as many 8 Nos. of Solar projects with installed capacity of 272.5 MW have connected with OPTCL network through 132 kV lines. The real time data of these plants are yet to be received at SLDC control room. Since the generation quantum is quite substantial (to the tune of 0.6 MU during a day), this has an impact on real time generation monitoring. 

In the 132nd PSOC meeting it was decided that SLDC shall convene a meeting with the defaulting Solar units and Telecom to discuss the issue. 

SLDC/Telecom may deliberate. 
D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos. of meters integrated, around data from 750 nos. of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos. of meters integrated, data from 717 nos. of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos. of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 119th PSOC meeting IT stated that Parameters of 16 Nos. meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
In the 123rd PSOC meeting IT stated that out of 840 Nos. interface meters connected with AMI, 750 Nos. are reporting at present. The newly replaced meters are not reporting. 2 Nos. of meters has sent to M/s SECURE meters for study.

In the 127th PSOC meeting IT stated that TCS is demanding Rs. 6.5 lacs for developing the required software. The proposal is placed before the management for approval

In the 128th PSOC meeting IT stated that the memorandum has been placed before the PSC

In the 130th PSOC meeting IT stated that approved letter was yet to be received by them.

In the 131st meeting IT stated that TCS has already developed the driver for Paralakhemundi and Balasore S/S meters. Data fetching is under testing stage.

In the 132nd PSOC meeting IT stated that EMD has already been shared. Report is expected by end of April19.

IT / SLDC may update the status
D.5: Colony consumption of POWERGRID S/Ss

In the 131st PSOC meeting SLDC stated that POWERGRID is consuming power for their colony, which is not reflected in the DISCOM bill. POWERGRID stated that they have applied to DISCOMs to make them consumer. 

It was decided that SLDC shall convene a meeting between GRIDCO, POWERGRID & DISCOMs to discuss the issue.

In the 132nd PSOC meeting CESU stated that POWERGRID has already made consumer of CESU. Other DISCOMs may insist to POWERGRID to become their consumer.  

SLDC/ GRIDCO/POWRGRID/DISCOMs may deliberate
D.6: Collection of modelling data for new Transmission elements as well as Generators  for system study.
SLDC is conducting system study for real time operation and determination of ATC & TTC for the State system. For the said study modelling of all transmission elements as well as generators are required. O&M is requested to furnish the parameters of newly inducted transmission lines / Transformers such as conductor type, line length and resistance, reactance and susceptance etc. and percentage impedance for transformers. Generators are requested to furnish the similar parameters in respect of the generator. 

Members may discuss  
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Expected to be completed by June’19.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	July’2019

	3
	220/33 kV, 2x20 MVA Baliguda S/S
	July’19

	4
	220/33 kV, 2x20 MVA Kalimela S/S
	July’19

	5
	220/33 kV, 2x20 MVA Kasipur S/S
	April’2019. Line charged.

	6
	220/132 /33 kV, 2x100 MVA Aska S/S (132/33 kV side)
	132/33 kV Side charged

	7
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’19

	8
	220/132/33 kV Jayapatana S/S(320 MVA)
	July’19

	9
	220/132 kV Pratapsasan S/S(320 MVA)
	Dec’19

	10
	220/132 kV Kesinga S/S (320 MVA)
	July’19

	11
	132/33 kV Betanati S/S
	Charged on 19.04.2019

	12
	132/33 kV R.Udyagiri S/S
	July’2019


The Discoms are requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement.
CGM (Construction) / DISCOMs may deliberate
E.2: Major Events in the month of April’19
1. On dt. 01.04.2019 at 18:46 Hrs - 40 MVA, 132/33 KV Power Transformer charged at GIS S/S, Unit -8, Bhubaneswar.
2. On dt. 19.04.2019 at 14:02 Hrs - 132/33 KV Grid S/S, Betanoti S/S Charged by  LILO Arrangement (3.104 Kms) in existing 132 KV Udala-Baripada SC line. At 14:21 Hrs dt.19.04.19 - 1x20 MVA 132/33 KV Power Transformer idle charged from 132 KV side. At 14:53 Hrs dt. 19.04.19 - 33 KV side of kV Power Transformer charged along with 33 KV bus. At 15:52 Hrs dt. 19.04.19 - 132 KV Udala - Betanoti feeder charged.
Members may note

E.3: Important Grid Incidences during the month of April’19.
On dt. 03.05.19  around at 08:30 Hrs, Extremely severe cyclonic storm "FANI" hit the coast of Odisha near Puri which caused disturbance in OPTCL System hence leading to load loss of  1800MW along with outages of following transmission elements.

400 KV:-

1. 400KV New Duburi-Pandiabil Line

2. 400KV Mendhasal-Meramundali Line
3. 400KV Mendhasal-Pandiabil ckt -I & II
220 KV:-

1. 220KV Mendhasal-Chandaka DC Line( ckt-I,II)
2. 220KV Mendhasal-Chandaka DC Line( ckt-III,IV )
3. 220KV Atri-Infocity Line
4. 220Kv Atri-Pandiabil Ckt-I & II.
5. 220KV Samangara-Pandiabil Ckt-I & II 
6. 220Kv Meramundali-Bidanasi Line
7. 220Kv New Duburi-Paradeep Ckt-I
8. 220KV Narendrapur-Atri Ckt-I & II
9. 220KV New Duburi-Balasore Line
10. 220Kv Mendhasal-Atri Line
132KV:-
1. 132Kv Nimapara-Samangara -Puri Line
2. 132Kv Paradeep-Kendrapara Ckt-I & II

3. 132Kv Paradeep-IFFCO Ckt-II
4. 132Kv Chandaka-Ranasinghpur Line
5. 132Kv Chandaka-Nimapara Line
6. 132Kv Mendhasal-Khurda Line
7. 132 KV Mendhasal-Chandaka SC line
8. 132Kv Atri-BankiLine
9. 132KV Cuttack-Jagatsinghpur Line
10. 132Kv Atri-Khurda Line
11. 132Kv Khurda-Samuka-Puri Line
12. 132Kv Atri-Argul Ckt-I
13. 132Kv Khurda-Chandpur Line
14. 132Kv Choudwar-TSAL-Aarti Steel Line
15. 132 KV Bidanasi - Choudwar ckt 
16. 132 KV  Phulnakhara LILO Lines 
17. 132 KV  Kesura LILO Lines
O&M may deliberate
E.4: Outage of major transmission Elements during the month of April’19. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration

Dt/time
	Reason

	1
	400 kV Mendhasal-Meramundali Line.
	03.05.19
	07.05.19/
21:48
	Tower damage by FANI 

	2
	400KV Mendhasal-Pandiabil ckt -I 
	03.05.19
	07.05.19/ 22:40
	Tower damage by FANI 

	3
	400 kV Mendhasal-Pandiabil ckt -II
	03.05.19
	07.05.19/ 23:42
	Tower damage by FANI 

	4
	220 kV Mendhasal-Chandaka DC Line( ckt-II)
	03.05.19
	07.05.19/ 21:50
	Tower damage by FANI 

	5
	220 kV Mendhasal-Chandaka DC Line( ckt-III,IV )

	03.05.19
	18.05.19 /13:41&

08.05.19/

14:46
	Tower damage by FANI 

	6
	220kV Atri-Infocity Line

	03.05.19
	06.05.19/ 21:21
	Tower damage by FANI 

	7
	220kV Atri-Pandiabil Ckt-I & II
	03.05.19
	06.05.19 /08:25&

08.05.19/

01:50
	Tower damage by FANI 

	8
	220 kV Samangara-Pandiabil Ckt-I & II 
	03.05.19
	B/D
	Tower damage by FANI 

	9
	220kV Meramundali-Bidanasi Line
	03.05.19
	05.05.19/ 07:40
	Tower damage by FANI 

	10
	220kV Narendrapur-Atri Ckt-I & II
	03.05.19
	B/D
	Tower damage by FANI 

	11
	220kV New Duburi-Balasore Line

	03.05.19
	05.05.19/ 21:47
	Jumper snapped 

	12
	220kV Mendhasal-Atri Line

	03.05.19
	05.05.19/ 07:40
	Tower damage by FANI 

	13
	132kV Nimapara-Samangara -Puri Line

	03.05.19
	14.05.19/ 23:13 & 15.05.19/14:14 (Samangara GSS charged by “T” arrangement) 
	Tower damage by FANI 

	14
	132 kV Paradeep-Kendrapara Ckt-I & II


	03.05.19
	04.05.19/ 14:24 & 04.05.19/

14:22
	Jumper snapped 

	15
	132 kV Paradeep-IFFCO Ckt-II

	03.05.19
	04.05.19/ 13:33
	Insulator damage at Loc-31

	16
	132 kV Chandaka-Ranasinghpur Line
	03.05.19
	05.05.19/ 22:02
	Tower damage by FANI 

	17
	132 kV Chandaka-Nimapara Line

	03.05.19
	14.05.19/ 22:53
	Tower damage by FANI 

	18


	132Kv Mendhasal-Khurda Line

	03.05.19
	04.05.19/ 23:23
	Tower damage by FANI 

	19
	132 kV Mendhasal-Chandaka SC line
	03.05.19
	B/D


	Tower damage by FANI 

	20
	132 kV Bidanasi - Choudwar ckt 
	03.05.19
	B/D
	Tower damage by FANI 

	21
	132 kV Phulnakhara LILO Lines 

	03.05.19
	11.05.19/ 18:47
	Tower damage by FANI 

	22
	132 kV  Kesura LILO Lines

	03.05.19
	13.05.19/ 20:58
	Tower damage by FANI 


O&M may discuss
E.5:  Review of Outage Program of State Generators for the month of June’19:
Tentative Outage programme for State Generators for the month of June’2019 
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 4

# 5

# 6
	14.03.18 to continue
25.10.18 to 20.05.19
25.10.16 to continue

16.10.15 to continue
	T&G coupling cover water leakage
Annual Maintenance

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to 15.06.19
	Under R,M work

	3
	Balimela
	# 1
# 2
	05.08.16 to continue
20.11.17 to continue
	Under R,M work
Under R,M work

	4
	Rengali
	# 2
	12.12.18 to continue
	Replacement of Runner disc.

	5
	Upper Kolab
	# 3

# 4
	28.03.19 to 15.06.19

01.02.19 to continue
	Generator stator inter turn / Earth fault

Capital maintenance work



OHPC may deliberate
E.6: Generation Program for the month of June’19.
Generation schedule for the month of June’19 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.05.19
	Reservoir Level as on 01.05.18
	MDDL
	High Flood    Reservoir Level

	
	June’19
(1st fortnight)
	June’19
 (2nd fortnight)
	
	
	
	

	HPS-I, Burla
	50
	50
	611.43 ft.
	611.10 ft.
	590 ft.
	630 ft.

	HPS-II, Chiplima
	35
	35
	-
	-
	-
	-

	Balimela
	360
	360
	1478.40 ft.
	1453.30 ft.
	1440 ft.
	1516 ft.

	Rengali
	30
	30
	113.96 mtr.
	117.87 mtr.
	109.72mtr 
	123.5 mtr.

	U.Kolab
	100
	100
	849.58 mts.
	849.48 mtr.
	844 mtr 
	858 mtr.

	U. Indravati
	80
	80
	631.40 mtr.
	631.15 mtr.
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2725.15 ft.
	2724.75 ft.
	2685 ft.
	2750 ft.

	TOTAL
	685
	685
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

SLDC / OHPC may deliberate

E.7: Anticipated power generation and demand for the month of June’2019.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1130
	1350

	2
	WESCO
	1100
	1300

	3
	NESCO
	920
	1100

	4
	SOUTHCO
	500
	550

	5
	Total Discom
	3650
	4300

	
	System Loss & others 
	150
	200

	
	Total Demand
	3800
	4500

	Availability
	
	

	1
	Hydro
	685  
	1200

	2
	State Thermal
	1020
	1050

	3
	IPP, small hydro &RE
	600
	600

	4
	ISGS share (including OA& purchase)
	1145
	1300

	5
	CGP support (OA)
	350
	350

	6
	Total availability
	3800
	4500

	7
	Surplus / Deficit
	0
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (134th) PSOC meeting.
PAGE  

