Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 134th PSOC Meeting to be held on 24.06.2019 at OPTCL Power Training Center, Chandaka, Bhubaneswar
A. Confirmation of the minutes of the 133rd PSOC Meeting held on 29.05.2019
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2019/1185/1685 (48) dated 13.06.2019 to all the member
s and also uploaded in the SLDC website. Members may offer their comments. If there are no comments, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   :  Grid Performance for the month of May’2019
C.1: Status of projects funded under PSDF scheme 
C.2: Review of the PSS Tuning of Generators in Eastern Region  
C.3: Implementation of Automatic Demand Management Scheme.

C.4: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s 
C.5: Bypassing arrangement of LILO of 400kV Lines at Angul 
C.6: Update on status of telemetry  
C.7: Mock Black start exercises in Eastern Region 
C.8: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC C.9: Implementation of Automatic Generation Control (AGC) in India (at Inter-State level)
C.10: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

C.11: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Communication issues.
D.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
D.4: Data communication from newly commissioned RE sources connected at 132 kV- SLDC.

D.5: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.6: Colony consumption of POWERGRID S/Ss
D.7: Collection of modelling data for new Transmission elements / Generators  for system study.
D.8: Frequent tripping of 400 kV Lapanga-IB D/C line & IBTPS # 3
E.1: Commissioning status of New Transmission elements. 

E.2: Major Events in the month of May’19
E.3: Important grid incidences during the month of May’19.

E.4: Outage of major transmission Elements during the month May’19. (above 10 hrs).
E.5: Review of Outage Program of State Generators for the month of July’2019
E.6: Generation Program for the month of July’2019.

E.7: Anticipated power generation and demand for the month of July’2019.
F.1: Date and Venue of the next (135th ) PSOC meeting
PART B: GRID PERFORMANCE
B. Review of Grid Performance for the month of May’19.

A. Frequency:

Hourly frequency variation for the month of May’19.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	Mar’19
	0.00
	0.02
	8.31
	70.28
	21.39
	49.99

	Apr’19
	0.00
	0.02
	6.49
	68.13
	25.37
	49.99

	May’19
	0.00
	0.05
	8.81
	73.28
	17.85
	49.99


Maximum & Minimum frequency during the month of Apr’19 & May’19.
	Month
	Freq (Hz)
	Date
	Time

	Apr’19
	Maximum –50.25
	07.04.19
	01:00 Hrs

	
	Minimum – 49.72
	03.04.19
	14:45 Hrs

	May’19
	Maximum –50.21
	01.05.19
	08:00 Hrs

	
	Minimum – 49.69
	09.05.19
	14:15 Hrs


Grid Demand for the month of May’19
	 Month
	Max. Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	Mar’19
	98.41
	27.03.19
	2624
	3526
	4643
	27.03.19
	20:00
	2634
	18.03.19
	4:00

	Apr’19
	113.14
	05.04.19
	2786
	3869
	5151
	04.04.19
	20:00
	2689
	20.04.19
	05:00

	May’19
	102.99
	19.05.19
	2638
	3545
	4635
	18.05.19
	24:00
	1720
	03.05.19
	18:00

	May’18
	98.61
	24.05.18
	2735
	3798
	4692
	07.05.18
	21.00
	2113
	14.05.18
	12.00


B. Voltage Profile of 220 kV Buses in OPTCL system for the month of: May’19
	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Atri
	243.23
	5
	6:30
	209.40
	25
	14:15

	2
	Balasore
	234.34
	25
	17:00
	202.82
	21
	13:45

	3
	Barkote
	229.32
	3
	9:30
	222.97
	21
	15:15

	4
	Bargarh
	227.58
	28
	19:00
	211.77
	23
	10:15

	5
	Bhadrak
	236.01
	25
	17:00
	207.55
	29
	23:30

	6
	Bhanjanagar
	238.96
	5
	6:15
	210.15
	10
	20:30

	7
	Bidanasi
	242.13
	5
	11:30
	212.11
	10
	15:30

	8
	Bolangir
	226.89
	28
	20:30
	210.61
	4
	16:45

	9
	Budhipadar
	230.30
	31
	17:45
	225.85
	2
	15:45

	10
	Chandaka
	236.01
	15
	18:45
	199.53
	10
	19:30

	11
	Cuttack
	243.17
	5
	11:15
	201.32
	25
	14:15

	12
	Duburi(O)
	233.13
	3
	6:30
	212.05
	21
	15:15

	13
	Duburi (N)
	231.68
	3
	6:30
	213.04
	20
	15:15

	14
	Jayanagar
	237.11
	27
	18:15
	226.43
	10
	20:30

	15
	Joda
	231.22
	4
	2:15
	214.65
	9
	23:45

	16
	Katapalli
	226.83
	28
	19:00
	206.86
	23
	10:15

	17
	Lapanga
	229.55
	28
	19:00
	224.18
	22
	16:00

	18
	Laxmipur
	239.48
	27
	18:15
	221.12
	19
	9:30

	19
	Mendhasal
	237.00
	15
	18:45
	196.25
	10
	21:15

	20
	Meramundali
	227.35
	3
	6:00
	217.77
	20
	15:00

	21
	Narendrapur
	244.33
	3
	7:30
	192.54
	18
	15:15

	22
	Nayagarh
	239.30
	5
	6:45
	206.28
	10
	20:30

	23
	Paradeep
	233.88
	4
	6:15
	203.68
	20
	13:00

	24
	Tarkera
	261.30
	25
	14:00
	222.50
	7
	23:30

	25
	Theruvali
	244.39
	27
	18:00
	213.32
	10
	20:30

	26
	Samangara
	-
	-
	-
	-
	-
	-


The maximum Voltage of 244.39 kV occurred at Theruvali 220 kV bus, while Narendrapur 220 kV bus has experienced the minimum Voltage of 192.54 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Mendhasal, Meramundali  and New Duburi bus during the month of May’2019 are indicated. 
[image: image1.emf]210

215

220

225

230

235

240

245

250

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF JAYANAGAR 220 kV Bus 

FOR MAY 2019


[image: image2.emf]170

180

190

200

210

220

230

240

250

260

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NARENDRAPUR 220 kV BUS

FOR MAY 2019


[image: image3.emf]375

380

385

390

395

400

405

410

415

420

425

430

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MENDHASAL 400 kV BUS

FOR MAY 2019


[image: image4.emf]390

395

400

405

410

415

420

425

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MERAMUNDALI 400 kV BUS

FOR MAY 2019


[image: image5.emf]390

395

400

405

410

415

420

425

430

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF  New DUBURI 400 kV BUS

FOR MAY 2019


Members may discuss.
C. Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of May– 2019. [image: image6.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  MAY'2019

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

40.16 23 12:30 4.00 10 18:00

67.92 28 16:30 4.40 10 15:45

118.12 25 10:45 7.52 24 15:45

126.68 24 15:30 27.60 15 16:15

127.12 9 18:45 5.64 15 15:45

1x100

13.76 1 16:15 2.80 4 01:00

1x160

15.20 2 11:30 3.40 5 18:00

1x100

Under idle charge condition

1x160 91.00 10 22:30 7.80 5 09:00

1x160 91.12 10 22:30 7.80 5 09:00

1x160 86.44 27 12:15 17.72 12 16:45

1x160 75.80 27 18:30 15.36 12 16:45

1x100 40.76 22 12:00 2.92 31 21:15

1x100 40.28 22 12:00 4.20 8 07:30

1x160 54.96 13 15:15 5.56 8 07:30

130.52 1 16:45 5.28 28 18:45

136.68 1 16:45 5.60 28 18:45

95.84 31 14:45 27.12 16 19:45

95.56 31 14:45 27.36 16 19:45

1x100 74.52 27 14:15 8.28 31 22:45

1x160 129.12 27 14:15 8.68 30 09:15

1x100 80.68 27 14:15 12.12 31 21:30

1x160 125.52 27 14:15 10.28 31 22:45

1x160

76.88

30 15:15 8.76 12 08:45

1x100

47.24

24 14:45 6.88 11 05:15

1x160 110.96 21 15:15 21.00 15 17:45

1x100 70.48 21 15:15 13.04 15 17:45

1x100 67.12 21 15:15 12.48 15 17:45

1x160 82.20 9 19:30 7.84 11 17:45

1x160 117.24 9 08:45 7.76 11 17:45

62.84 18 10:00 11.76 31 16:30

65.32 18 10:00 10.60 31 16:30

51.80 14 20:00 11.32 31 16:30

1x100 40.00 6 12:45 4.52 21 04:00

1x100 38.76 6 12:45 4.68 5 22:00

1x160 57.68 31 20:45 4.44 19 03:00

73.48 23 15:30 7.56 16 20:00

73.28 23 15:30 17.08 16 20:00

45.16 10 19:30 4.32 20 18:00

44.44 10 19:30 4.16 16 02:30

47.64 24 13:15 3.40 16 02:30

45.16 10 19:30 4.32 20 18:00

37.20 1 06:45 2.40 18 12:00

109.84 2 07:15 7.92 27 18:15

109.76 2 07:30 16.40 5 21:45

1x100 63.20 2 07:15 9.12 5 21:45

1x160 140.16 16 07:12 6.16 25 20:00

1x100 85.60 16 22:30 5.84 11 12:00

1x160 44.84 20 22:00:00 9.16 25.00 20:00

4x100  62.96 31 15:00 7.32 28 15:30

64.28 31 15:00 8.28 28 15:30

63.04 31 15:00 7.56 28 15:30

62.64 31 15:00 8.24 28 15:30

2x100 51.20 3 22:30 9.36 2 12:00

48.56 3 22:30 9.52 2 12:00

1x160 79.72 3 22:30 2.32 18 08:15

1x160  105.20 28 18:45 17.16 2 19:15

1x160 105.20 28 18:45 17.16 2 19:15

Drawal details

Maximum Minimum

ATRI                                                     

{Banki, Khurda, Chandpur & Argul}

2x160

BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

3x160 



BARGARH 220/132 kV

BHADRAK 220/132 KV

{Bargarh, Ghensh}

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}



BIDANASI 220/132 KV

{Bidanasi, Khurda }



BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

2x160

BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), 

MCL, Sundergarh,Brajarajnagar, 

Rajgangpur}

2x160 



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }



CUTTACK

DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, 

Jajpur Road, Kalarangi, Jajpur Town}



JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

3x100 

"*" - Alternate P/S from 

Kuchei.

KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & 

Katapali area load.}

Supported by Burla & 

Chipilima power.

LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

2x160

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100

Mendhasal { Part area load of Khurda S/S} 2x100

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, 

Digapahandi, Mohana.}

2x160



PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 



THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

Rayagada & 

Paralakhemundi can be fed 

from Machhkund system.

TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 


D. DISCOM Drawal for the month of May’19
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	Apr’19
	798.00
	760.542
	857.404
	18.345
	839.059
	78.517

	
	May’19
	770.33
	664.438
	689.035
	16.166
	672.869
	8.431

	WESCO
	Apr’19
	635.00
	649.188
	856.374
	149.999
	706.375
	57.187

	
	May’19
	604.71
	703.036
	841.28
	100.320
	740.960
	37.924

	NESCO
	Apr’19
	517.00
	478.905
	600.692
	99.608
	501.084
	22.179

	
	May’19
	521.48
	508.934
	629.852
	89.858
	539.994
	31.06

	SOUTHCO
	Apr’19
	331.00
	303.576
	334.361
	0
	334.361
	30.785

	
	May’19
	310.85
	320.055
	336.003
	0
	336.003
	15.048


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
Members may please discuss.

E. Energy Generation / Import up to the month of May’19
Figures in MU  
	Month
	Thermal

(TTPS+IbTPS)
	OHPC 
& MKD
	CGP Support
	IPP Inj.
	RE
	ISGS
	Total

	April’19
	588.681
	538.473
	308.480
	263.019
	29.852
	1057.035
	2785.54

	May’19
	608.185
	571.561
	290.845
	203.850
	46.247
	916.949
	2637.636

	Total
	1196.866
	1110.034
	599.325
	466.869
	76.099
	1973.984
	5423.176


F.  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of May’19 are as detailed:
	Month
	Total Generation
	Odisha Drawl
	AP Drawl

	
	MU
	Avg (MW)
	MU
	Avg (MW)
	MU
	Avg (MW)

	Apr’19
	53.168
	73.84
	24.896
	34.58
	26.401
	36.67

	May’19
	60.577
	81.42
	26.811
	36.04
	31.821
	42.77

	Total
	113.745
	
	51.707
	
	58.222
	


Drawl of State share power from Machhakund has decreased during the month. Southco may add more feeders to Podagada S/s. 
SOUTHCO may deliberate.
G. Under Frequency Relay operation in OPTCL System during the month of May’19.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of May’19.
H. Status of Open Access applications up to the month of May’2019
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected
	MU

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	
	

	1
	April’19
	48
	100
	0
	24
	172
	48
	100
	0
	24
	172
	0
	

	2
	May’19
	21
	92
	0
	29
	142
	21
	92
	0
	29
	142
	0
	

	
	Total
	69
	192
	0
	53
	314
	69
	192
	0
	53
	314
	0
	


PART C – Issues to be discussed in the 158th  OCC meeting of ERPC on 27.06.2019

C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	31.03.19
	162.5 Cr.
Total expenditure may not exceed Rs. 68 Crs.
	38.09Cr. Received Rs. 8.00 Cr on 28.03.19 
	90% equipment installed and commissioned. Tender for measuring instruments under evaluation. Stn. Tfr will reach by 15th June’19

	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.22 Cr

	2.56 Cr received as 10 % DPR. Claimed for 20 %.
	Order placed. Expected by July’19



	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov18
Chiplima

Dec 2018
	22.35 Cr.
	2.235 Cr
	Placed work order for Balimela. PO for other units amounting Rs. 2 Crs placed. Order under process.( 7 Cr.)

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 
	27-07-18
	
	31.94 Cr
Ested. Cost. Approved amount 30.26 Cr. Grant amount 27.23 Cr.
	Rs.2.72 Cr received as 10% of DPR. Retendering under process.
	Agreement signed and sent to NLDC for signature. Retendering will be done.

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost. 2.93 Cr recommended by Appraisal committee.
	
	Approved by Appraisal committee. CERC approval awaited.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	12.03.2018  Date of submission 
	
	41.1 Cr

Estt cost
	10% of DPR to be asked.
	Project approved.  Tender to be floated after revision of specification.. 


      CGM (O&M) / OHPC/ SLDC may update the status

C.2: Review of the PSS Tuning of Generators in Eastern Region  

On 31st January 2019, PSS Tuning Meeting was held at ERPC. All generating utilities were advised to complete the PSS tuning of their plant at earliest for improvement of damping in the grid during transients. In addition, the tuning reports have also to be submitted to ERLDC/ERPC for their validation. 
In the 131st PSOC meeting OPGC stated that they have already furnished the data to ERPC. GMR and Vedanta were requested to furnish the data soon to ERPC.
In the 132nd PSOC meeting Vedanta stated that they have already furnished the data. GMR was not present to deliberate.
In the 133rd PSOC meeting,GMR was requested to furnish the data, if not done.

GMR may deliberate

C.3: Implementation of Automatic Demand Management Scheme

The latest status along with proposed logic as follows: 
	Sl. No
	State /Utility
	Logic for ADMS operation
	Implementation status/target
	Proposed logic (if different from under implementation logic

	1
	Odisha
	1. System Frequency < 49.9 Hz 
2. Odisha over-drawl > 150 MW
3. DISCOM over-drawl > (40 MW) 
	10 Months

Sent for PSDF approval
	Logic 2 and 3 is AND or OR, in case it is AND then ADMS may not operate when DISCOMs are in schedule but GRIDCO is over drawing due to less generation at State embedded generators.


In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 123rd PSOC meeting SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval

In the 124th PSOC meeting SLDC stated that the revised estimate has been approved in the BoD.

In the 129th PSOC meeting SLDC stated that CERC approval is awaited for tendering.

CERC has approved the revised estimate. SLDC shall process for tendering.
In the 133rd PSOC meeting a committee was constituted with representatives of DISCOM, Telecom, IT & SLDC as detailed

Members

1. Sri B.D.Panda, AGM, SLDC, Convener

2. Sri Manoj Kumar Das, G.M.(Operation),SLDC

3. Sri Pranab Kumar Nayak, DGM (Telecom)

4. Sri Subrat Kumar Mishra, DGM (IT)

5. Sri P.K.Padhy, GM, CESU

6. Sri. Anil Kumar Patra, Manager, WESCO

7. Sri S.C.Mahalik, G.M, NESCO

8. Sri Sanjeeb Mohanty, A.M, SOUTHCO

SLDC may deliberate
C.4: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 133rd PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by July’19.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	220 kV S.C line and Keonjhar S/S (220/33 kV) , 2x20 MVA charged on 31.12.2018. 2nd ckt; June’’2019

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019. Order placed.

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	July’2019 


In the 132nd PSOC meeting NESCO stated that they have already taken action for downstream takeoff arrangements from Keonjhar S/S. Telecom stated that for charging of Keonjhar-Keonjhar (PG) 2nd ckt, CARD has already been received and ABB engineers has reached the spot. Expected by June’ 2019.

CGM (Cont) / CGM (Telecom) may deliberate

C.5: Bypassing arrangement of LILO of 400kV Lines at Angul 

LILO of Meramundali-Bolangir/Jeypore 400 kV S/C line and LILO of one Ckt of Talcher-Meramundali 400 kV D/C line has been done at Angul 765/400kV Sub-station. The bypass arrangement for these circuits is under implementation at Angul by Powergrid.  

In 157th OCC, Powergrid informed that bypass arrangement would be completed by June 2019.   

OPTCL may please inform the commissioning schedule of the 2nd circuit of 400kV Meramundali-Mendhasal line. 

In the 133rd PSOC meeting O&M stated that 3rd ICT at Mendhasal shall be charged after completing DGA test, after which 400 kV Meramundali-Mendhasal 2nd circuit will be charged.

Powergrid and OPTCL may update.

C.6: Update on status of telemetry  

CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed  NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up 

the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action.  

 Major issues are given below: 

 xxxxxxxxx.

In the 132nd PSOC meeting CGM (Telecom) stated that survey work for Meramundali-Bhanjanagar line is under process. OPGW will be reached at site after completion of survey and preparation of drum schedule. DGM (Telecom) stated that the vender list and rate will be provided to NALCO for placement of order by them.

In the 133rd PSOC meeting DGM (Telecom) stated that the vendor list has been provided to NALCO. NALCO stated that the tower schedule has been prepared. 

Telecom / NALCO may deliberate the status

C.7: Mock Black start exercises in Eastern Region – ERLDC 

 Schedule and tentative date for conducting mock black start exercise in OHPC stations is as tabled. 
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2019
	June’19
	Last week of January 2020
	

	3
	Rengali
	2nd week of June 2019
	2nd week of June 2019
	Last week of November 2020
	

	4
	U.Indravati
	3rd week of June 2019
	4th week of June 2019
	2nd week of February 2020
	

	6
	Balimela
	3rd week of October  2019
	
	1st week of March 2020
	

	9
	Burla
	Last week of June 2019
	4th week of June 2019
	Last week of February 2020
	


SLDC / OHPC may deliberate
C.8: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC 

As a National Grid operator, POSOCO is continuously working for ensuring reliability and security of the Grid. With penetration of more and more renewable energy source the task is becoming complicated day by day.  An accurate dynamic modeling of the National Grid needs modeling of conventional as well as renewable / distributed generation sources. World Bank has engaged Digsilent as consultant for assisting POSOCO for building dynamic model of the Grid. A guideline for dynamic data collection has been developed in consultation with Digsilent Pacific team.   All the utilities are requested to collect data from the grid scale renewable power plants as well as from conventional power plants under their jurisdiction and submit the same to ERLDC/ERPC as early as possible. 

In the 132nd PSOC meeting, all generators as well as RE sources were requested to furnish data to SLDC for onward transmission to ERPC.
SLDC requested ERPC to forward the format for preparing the data. The format will be circulated to all RE & conventional generators in the State 
In the 133rd PSOC meeting, SLDC stated that the format will be circulated after receiving from ERPC.

SLDC may deliberate

C.9: Implementation of Automatic Generation Control (AGC) in India (at Inter-State level) 

The issue was discussed in 8th NPC Meeting held on 30th November 2018, it was decided that each RPC would submit the status of implementation of AGC to NPC.  

In 40th TCC, NTPC informed that AGC at Barh STPS will be implemented by May, 2019. 

DVC confirmed that unit#8 of Mejia TPS has been identified for AGC implementation as a pilot project. 

The followings were decided in the TCC Meeting: 

1. Status of implementation of AGC shall be regularly monitored in OCC meetings. 

2. A workshop shall be organized in ERPC wherein NLDC and NTPC will be invited to interact with the ER constituents regarding the experience they have gained in implementing the AGC in other regions. 

In 155th OCC, NTPC informed that implementation of AGC at Unit#4 & 5 of Barh STPS are in progress and was expected to complete by May 2019.  

Odisha informed that unit#3 of OPGC had been selected for implementation of AGC.  

WBPDCL informed that unit#5 of Bakreswar had been selected for implementation of AGC.  

In 156th OCC, OCC decided to organize the workshop at ERPC in May 2019 wherein NLDC, NTPC and Siemens will be invited to interact with the ER constituents.  

In the 133rd PSOC meeting it was decided that all Generators shall furnish their feedback after attending the workshop.

OHPC / OPGC / GMR/ Vedanta may note.  

C.10: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

The activity of the preparation of Crisis Management Plan for countering the cyber-attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA. 

In 142nd OCC, ERLDC informed that, in line with Enquiry Committee Recommendation, cyber security audit is being conducted on regular basis for SCADA system installed at ERLDC and SLDC as well but cyber security audit for telecom infrastructure installed in Eastern Region is not being carried out.  

OCC advised all the constituents to conduct the cyber security audit on telecom infrastructure installed in Eastern Region. It is further advised that compliance / mitigation of the points observed during the audit should also be completed for improvement of the telecom infrastructure in ER. 

As suggested by CEA, a format has been circulated among ER constituents for furnishing the information of the respective systems for discussion in OCC Meeting. The format is enclosed at Annexure-E1. 

OCC advised all the constituents to submit the information to ERPC as per Annexure-E1.
OPTCL has submitted the required data 

Sr. G.M (IT) may update
C.11: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

 
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.  

As per the information received from the constituents the following generators certified with IS 18001:  • All NTPC stations in Eastern Region • Teesta, NHPC • All OHPC generating units  • All CESC generating units  • All units of WBPDCL • DGPC units 

In the 129th PSOC meeting O&M stated that 2nd stage internal audit has been done. Report is yet to be received. Process has been initiated for deposit of application money for external audit. On compliance of the observations Certificate may be issued.    

In the 131st PSOC meeting O&M stated that Audit has been completed but the report is yet to be received.
In the 132nd PSOC meeting O&M stated that external audit stage-I completed. On completion Stage-II external audit certificate may be received.

CGM (O&M) may deliberate
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of April’19:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	8.431
	1.268

	2
	WESCO
	0
	37.924
	5.394

	3
	NESCO
	0
	31.06
	6.102

	4
	SOUTHCO
	0
	15.048
	4.702

	
	Total
	0
	92.463
	


It is noticed that all the DISCOMs were over drawn during the month NESCO has deviated 6.102% followed by WESCO 5.394% from the scheduled energy while SOUTHCO and CESU have deviated 4.702 % & 1.268 % respectively. DISCOMs may forecast their drawal in realistic approach to minimise deviation.

SLDC/ Discoms may please deliberate.
D.2: Communication issues 
The status of data communication from CGPs as deliberated in the 124rd PSOC meeting meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	2
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. 
xxxxxx
In the 130th PSOC meeting it was decided that RT&C shall file a case before the OERC against the defaulting CGP / Industries and Telecom will provide the required information to them. RT&C vide their letter No. 104(4) dated 01.03.2019 asked Telecom wing to prepare the draft Petition along with the required information to them.  
In the 131st PSOC meeting it was decided that T&C and Telecom shall discuss and prepare the Petition to file before the OERC.

In the 133rd PSOC meeting it was decided that RT&C will provide the draft Petition to Telecom wing within a week for their views.
RT&C and Telecom may update the status
D.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMs & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same. Another meeting was proposed to be convened in the month of August’17 to finalize the mechanism of data communication. In the 113th PSOC meeting, it was decided that GRIDCO will take follow up action with all the RE generators to provide real time generation data to SLDC. ERLDC has reminded again to intimate the status.   

A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos. of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.

In the 123rd PSOC meeting Telecom stated that M/S Secure meters could not complete the Demo, as M/S Chemtrol requires Rs. 3.5 lacs to allow firewall access to them. M/s Chemtrol also interested to take up the work. GRIDCO may allow them for the pilot project. OPTCL may examine for Firewall access to avoid burden to the Solar projects.
In the 125th PSOC meeting GRIDCO have agreed to write a letter to M/s Chemtrol. It was decided that a committee shall be constituted with representatives of GRIDCO, O&M, Telecom & SLDC to take a decision.

GRIDCO may deliberate the status.

D.4: Data communication from newly commissioned RE sources connected at 132 kV- SLDC
There are as many 8 Nos. of Solar projects with installed capacity of 272.5 MW have connected with OPTCL network through 132 kV lines. The real time data of these plants are yet to be received at SLDC control room. Since the generation quantum is quite substantial (to the tune of 0.6 MU during a day), this has an impact on real time generation monitoring. 

In the 132nd PSOC meeting it was decided that SLDC shall convene a meeting with the defaulting Solar units and Telecom to discuss the issue. 

In the 133rd PSOC meeting CGM (Telecom) stated that Vinto Solar data can be integrated only after laying of optical fiber, which has been proposed for PSDF funding

Telecom may deliberate. 
D.5: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos. of meters integrated, around data from 750 nos. of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos. of meters integrated, data from 717 nos. of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos. of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 131st meeting IT stated that TCS has already developed the driver for Paralakhemundi and Balasore S/S meters. Data fetching is under testing stage.
In the 132nd PSOC meeting IT stated that EMD has already been shared. Report is expected by end of April19.

In the 133rd PSOC meeting, DGM (IT) stated that Paralakhemundi and Balasore S/S meter data has been tested. The software fetching data for other S/Ss will be tested
IT / SLDC may update the status
D.6: Colony consumption of POWERGRID S/Ss

In the 131st PSOC meeting SLDC stated that POWERGRID is consuming power for their colony, which is not reflected in the DISCOM bill. POWERGRID stated that they have applied to DISCOMs to make them consumer. 

It was decided that SLDC shall convene a meeting between GRIDCO, POWERGRID & DISCOMs to discuss the issue.

In the 132nd PSOC meeting CESU stated that POWERGRID has already made consumer of CESU. Other DISCOMs may insist to POWERGRID to become their consumer.  

In the 133rd PSOC meeting it was decided that all Discoms shall submit the details of their problems regarding making POWERGRID their consumer, to GRIDCO for raising the issue in the Commercial Committee meeting of ERPC.

DISCOMs/GRIDCO may deliberate
D.7: Collection of modelling data for new Transmission elements as well as Generators  for system study.
SLDC is conducting system study for real time operation and determination of ATC & TTC for the State system. For the said study modelling of all transmission elements as well as generators are required. O&M is requested to furnish the parameters of newly inducted transmission lines / Transformers such as conductor type, line length and resistance, reactance and susceptance etc. and percentage impedance for transformers. Generators are requested to furnish the similar parameters in respect of the generator. 

In the 133rd PSOC meeting, it was decided that SLDC will forward the format by 1st week of June’19 to all Generators and O&M for preparing the data in respect of their units and transmission lines.

SLDC may deliberate 
D.8: Frequent tripping of 400 kV Lapanga-IB D/C line & IBTPS # 3 

It is noticed that 400 kV Lapanga-Ib line is tripping frequently causing tripping of IB Unit #3, which is under testing stage. During the month of June the above line has tripped three times on DP (E/F) relay operation and Phase to phase fault. Further there is no reason for tripping of IB unit-3 0n 19.06.2019 (generating about 500 MW), on tripping of one ckt of the said line.

OPGC / O&M may deliberate   
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Expected to be completed by June’19. (idle charged from Jayanagar)

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	July’2019

	3
	220/33 kV, 2x20 MVA Baliguda S/S
	July’19

	4
	220/33 kV, 2x20 MVA Kalimela S/S
	July’19

	5
	220/33 kV, 2x20 MVA Kasipur S/S
	June’2019. Line charged.

	6
	220/132 /33 kV, 2x100 MVA Aska S/S (132/33 kV side)
	132/33 kV Side charged

	7
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’19

	8
	220/132/33 kV Jayapatana S/S(320 MVA)
	July’19

	9
	220/132 kV Pratapsasan S/S(320 MVA)
	Dec’19

	10
	220/132 kV Kesinga S/S (320 MVA)
	July’19

	11
	132/33 kV R.Udyagiri S/S
	July’2019


The Discoms are requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement.
CGM (Construction) / DISCOMs may deliberate
E.2: Major Events in the month of May’19
1. 10.05.2019: At 16:11 Hrs, 132/33 kv, 40 MVA Tfr charged at Baripada Gris S/s and loaded at 09:42 hrs of 12.05.2019
2. 17.05.2019: At 12:22 Hrs, 220/132 kV, 50 MVA Auto Tfr replaced by 160 MVA Tfr at Paradeep Grid S/S and loaded at 16:45 Hrs of 17.05.2019.

3. 29.05.2019: 220 kV Laxmipur-Damanjodi(NALCO) ckt-II & ckt-I charged at 16:00 hrs and 16:55 Hrs respectively.

4. 30.05.2019: 220 kV Bhanjanagar-Aska (New) ckt-I & II charged at 17:53 hrs and 18:18 Hrs respectively.

Members may note

E.3: Important Grid Incidences during the month of May’19.
1.  On dt. 03.05.19  around at 08:30 Hrs, extremely severe cyclonic storm "FANI" hit the coast of Odisha near Puri which caused disturbance in OPTCL System hence leading to load loss of  1800MW along with outages of following transmission elements. Major transmission lines and Distribution network in the Districts of Puri, Khurda and part of Cuttack have been damaged.

2. At 13.05Hrs of dt. 08.05.2019 :- While charging of 400KV side of ICT-2, after prolonged outage after cyclone “FANI” at Grid S/S, Mendhasal ,  400 kV side B-Ph, LA of the said ICT failed leading to tripping of 315 MVA, ICT-2 along with 400 KV Mendhasal-Meramundali Ckt resulting 400KV system black out at Grid S/S, Mendhasal & Pandiabil.  
O&M may deliberate
E.4: Outage of major transmission Elements during the month of May’19. (above 10 hrs).
Due to cyclonic storm "FANI" all major transmission elements in Puri-Khurda- part of Cuttack command area were tripped and remained un-restored for a prolonged period. 
O&M may discuss
E.5:  Review of Outage Program of State Generators for the month of July’19:
Tentative Outage programme for State Generators for the month of July’2019 
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 4

# 5

# 6
	14.03.18 to continue
25.10.18 to 31.07.19
25.10.16 to continue

16.10.15 to continue
	T&G coupling cover water leakage
Intake gate problem
Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to 15.07.19
	Under R,M work

	3
	Balimela
	# 1
# 2
	05.08.16 to continue
20.11.17 to continue
	Under R,M work
Under R,M work

	4
	Rengali
	# 2
	12.12.18 to continue
	Replacement of Runner disc.

	5
	Upper Kolab
	# 3

# 4
	28.03.19 to 15.07.19

01.02.19 to continue
	Generator stator inter turn / Earth fault

Capital maintenance work

	6
	Upper Indravati
	# 4
	15.06.19 to continue
	Penstock water leakage



OHPC may deliberate
E.6: Generation Program for the month of July’19.
Generation schedule for the month of July’19 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.06.19
	Reservoir Level as on 01.06.18
	MDDL
	High Flood    Reservoir Level

	
	July’19
(1st fortnight)
	July’19
 (2nd fortnight)
	
	
	
	

	HPS-I, Burla
	50
	50
	603.50 ft.
	606.33 ft.
	590 ft.
	630 ft.

	HPS-II, Chiplima
	32
	32
	-
	-
	-
	-

	Balimela
	360
	360
	1466.50 ft.
	1449.60 ft.
	1440 ft.
	1516 ft.

	Rengali
	30
	30
	111.63 mtr.
	113.75 mtr.
	109.72mtr 
	123.5 mtr.

	U.Kolab
	100
	100
	847.57 mts.
	847.69 mtr.
	844 mtr 
	858 mtr.

	U. Indravati
	80
	80
	628.87 mtr.
	628.77 mtr.
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2719.00 ft.
	2712.00 ft.
	2685 ft.
	2750 ft.

	TOTAL
	682
	682
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

SLDC / OHPC may deliberate

E.7: Anticipated power generation and demand for the month of July’2019.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1100
	1250

	2
	WESCO
	1000
	1200

	3
	NESCO
	900
	1050

	4
	SOUTHCO
	450
	500

	5
	Total Discom
	3450
	4000

	
	System Loss & others 
	150
	200

	
	Total Demand
	3600
	4200

	Availability
	
	

	1
	Hydro
	682 
	1200

	2
	State Thermal
	1000
	1050

	3
	IPP, small hydro &RE
	400
	450

	4
	ISGS share (including OA& purchase)
	1145
	1150

	5
	CGP support (OA)
	350
	350

	6
	Total availability
	3577
	4200

	7
	Surplus / Deficit
	23
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (135th) PSOC meeting.
PAGE  

