
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image1.png]PTC




Agenda

for

138th Power System Operational Co-ordination Meeting

Date: 25.10.2019
Venue: Power Training Center, Chandaka, Bhubaneswar 
Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 138th PSOC Meeting to be held on 25.10.2019 at OPTCL Power Training Center, Chandaka, Bhubaneswar
A. Confirmation of the minutes of the 137th PSOC Meeting held on 21.09.2019
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2019/3074 (49) dated 27.09.2019 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there are no comments, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   :  Grid Performance for the month of September’2019
C.1: Status of projects funded under PSDF scheme 
C.2: Finalization Outage Request and processing timeline—ERLDC.

C.3: Implementation of Automatic Demand Management Scheme.

C.4: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s 
C.5: Bypassing arrangement of LILO of 400kV Lines at Angul 
C.6: Update on status of telemetry  
C.7: Mock Black start exercises in Eastern Region 
C.8: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC.

C.9: Implementation of Automatic Generation Control in Eastern Region--ERLDC

C.10: Submission of data in MERIT Order portal--CEA
C.11: Data for preparation Load Generation Balance Report (LGBR) of ER for the year 2020-21

C.12: Monitoring of Next Six-Month New Element Integration in OCC and Its Update on Monthly Basis --ERLDC
C.13: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
D.3: Data communication from newly commissioned RE sources connected at 132 kV- SLDC.

D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.5: Colony consumption of POWERGRID S/Ss
D.6: Dispute in Energy Accounting of DISCOMs
E.1: Commissioning status of New Transmission elements. 

E.2: HT metering at DISCOM interface points.-SLDC.

E.3: Major Events in the month of September’19
E.4: Important grid incidences during the month of September’19.

E.5: Outage of major transmission Elements during the month September’19. (above 10 hrs).
E.6: Prolonged outage of Transmission elements

E.7: Review of Outage Program of State Generators for the month of November’2019
E.8: Generation Program for the month of November’2019.

E.9: Anticipated power generation and demand for the month of November’2019.
F.1: Date and Venue of the next (139th) PSOC meeting.
PART B: GRID PERFORMANCE
B. Review of Grid Performance for the month of September’19.

A. Frequency:

Hourly frequency variation for the month of September’19.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	July’19
	0.00
	0.05
	7.00
	67.57
	25.39
	50.00

	Aug’19
	0.00
	0.10
	7.29
	71.69
	20.92
	49.99

	Sept’19
	0.00
	0.08
	4.56
	74.71
	20.64
	50.00


Maximum & Minimum frequency during the month of August’19 & Sept’19.
	Month
	Freq (Hz)
	Date
	Time

	Aug’19
	Maximum –50.26
	15.08.19
	09:30 Hrs

	
	Minimum – 49.66
	20.08.19
	19:15 Hrs

	Sept’19
	Maximum –50.20
	29.09.19
	13:30 Hrs

	
	Minimum – 49.70
	18.09.19
	18:30 Hrs


B. Grid Demand up to the month of September’19
	 Month
	Max. Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	Mar’19
	98.41
	27.03.19
	2624
	3526
	4643
	27.03.19
	20:00
	2634
	18.03.19
	04:00

	Apr’19
	113.14
	05.04.19
	2786
	3869
	5151
	04.04.19
	20:00
	2689
	20.04.19
	05:00

	May’19
	102.99
	19.05.19
	2638
	3545
	4635
	18.05.19
	24:00
	1720
	03.05.19
	18:00

	June’19
	105.24
	11.06.19
	2653
	3684
	4790
	11.06.19
	23:00
	2556
	13.06.19
	06:00

	July’19
	106.80
	15.07.19
	2744
	3688
	4899
	15.07.19
	21:00
	2640
	02.07.19
	04:00

	Aug’19
	105.41
	21.08.19
	2924
	3930
	4901
	16.08.19
	21:00
	3161
	08.08.19
	05:00

	Sept’19
	107.91
	19.09.19
	2780
	3862
	4969
	18.09.19
	20:00
	2982
	30.09.19
	05:00

	Sept’18
	108.58
	30.09.18
	2857
	3968
	4973
	30.09.18
	21:00
	2881
	21.09.18
	05:00


C. Voltage Profile of 220 kV Buses in OPTCL system for the month of: September’19
	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Atri
	234.74
	7
	3:30
	218.12
	20
	18:30

	2
	Balasore
	231.74
	25
	4:15
	215.90
	20
	20:30

	3
	Barkote
	231.63
	8
	6:00
	225.85
	23
	15:30

	4
	Bargarh
	231.68
	29
	20:15
	214.08
	24
	15:15

	5
	Bhadrak
	232.15
	25
	4:15
	212.75
	15
	13:15

	6
	Bhanjanagar
	236.36
	26
	4:00
	221.23
	14
	18:30

	7
	Bidanasi
	236.53
	7
	3:45
	224.29
	30
	18:15

	8
	Bolangir
	234.86
	23
	19:15
	209.40
	24
	18:00

	9
	Budhipadar
	232.09
	30
	4:00
	227.93
	24
	7:30

	10
	Chandaka
	230.64
	25
	4:00
	212.92
	16
	22:30

	11
	Cuttack
	232.67
	7
	3:30
	214.08
	16
	19:00

	12
	Duburi(O)
	231.68
	25
	4:15
	221.81
	14
	20:45

	13
	Duburi (N)
	225.22
	25
	3:45
	215.40
	14
	20:45

	14
	Jayanagar
	239.94
	26
	5:45
	232.15
	14
	18:30

	15
	Joda
	231.11
	29
	6:00
	218.81
	14
	21:00

	16
	Katapalli
	228.45
	30
	4:00
	219.62
	18
	16:45

	17
	Lapanga
	229.66
	8
	13:45
	224.29
	18
	16:45

	18
	Laxmipur
	239.65
	25
	4:00
	228.39
	14
	18:30

	19
	Mendhasal
	233.47
	7
	3:30
	216.56
	16
	22:30

	20
	Meramundali
	228.62
	7
	6:00
	220.77
	30
	19:15

	21
	Narendrapur
	237.11
	4
	14:15
	213.44
	20
	18:30

	22
	Nayagarh
	235.55
	7
	3:30
	217.02
	10
	14:00

	23
	Paradeep
	232.32
	12
	8:30
	213.79
	1
	21:00

	24
	Tarkera
	230.36
	8
	11:00
	224.58
	12
	20:45

	25
	Theruvali
	236.30
	29
	15:00
	220.71
	14
	18:30

	26
	Rengali
	229.37
	7
	6:00
	224.58
	16
	20:45


The maximum Voltage of 239.94 kV occurred at Jayanagar 220 kV bus., while Bolangir 220 kV bus has experienced the minimum Voltage of 209.40 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Mendhasal, Meramundali and New Duburi bus during the month of Sept’2019 are indicated. 
[image: image2.emf]210

215

220

225

230

235

240

245

250

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF JAYANAGAR 220 kV BUS

FOR SEPTEMBER'2019


[image: image3.emf]170

180

190

200

210

220

230

240

250

260

0:00 0:45 1:30 2:15 3:00 3:45 4:30 5:15 6:00 6:45 7:30 8:15 9:00 9:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NARENDRAPUR 220 kV BUS 

FOR SEPTEMBER 2019


[image: image4.emf]350

355

360

365

370

375

380

385

390

395

400

405

410

415

420

425

430

0:00 0:45 1:30 2:15 3:00 3:454:30 5:15 6:00 6:457:30 8:15 9:00 9:45

10:3011:15 12:00 12:45 13:3014:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:1521:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MENDHASAL 400 kV BUS

FOR SEPTEMBER'2019


[image: image5.emf]390

395

400

405

410

415

420

425

0:00 0:45 1:30 2:15 3:00 3:45 4:30 5:15 6:00 6:45 7:30 8:15 9:00 9:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MERAMUNDALI 400 kV BUS

FOR SEPTEMBER'2019


[image: image6.emf]390

395

400

405

410

415

420

425

430

0:00 0:45 1:30 2:15 3:00 3:45 4:30 5:15 6:00 6:45 7:30 8:15 9:00 9:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NEW DUBURI 400 kV BUS

FOR SEPTEMBER'2019


Members may discuss.
D. Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of Sept– 2019. [image: image7.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  SEPTEMBER'2019

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

51.32 16 5:45 7.84 4 15:45

51.44 16 5:45 7.84 4 15:45

80.20 30 10:30 26.20 5 9:30

77.92 7 21:00 26.32 5 9:30

76.96 30 9:30 27.44 19 9:00

1x100

12.36 22 16:30 2.32 21 6:00

1x160

13.16 24 18:00 2.48 20 1:45

1x100

35.60 8 19:30 7.64 14 9:15

1x160 64.32 8 19:30 9.76 23 4:15

1x160 64.48 8 19:30 14.24 14 9:15

1x160 88.36 11 18:30 8.56 28 14:15

1x160 77.04 11 18:30 7.24 28 14:15

1x100 27.44 9 12:00 5.52 3 17:00

1x100 17.44 9 12:00 5.52 3 17:00

1x160 38.84 9 12:00 8.04 3 17:00

140.40 18 14:00 16.60 19 13:30

132.00 20 18:45 15.12 24 18:00

112.60 18 16:00 24.72 12 6:15

111.92 18 16:00 24.68 12 6:15

1x100 65.88 13 15:00 31.36 28 11:15

1x160 115.60 13 15:00 55.04 28 11:15

1x100 70.72 16 14:45 34.12 28 11:15

1x160 111.76 13 15:00 53.16 28 11:15

1x160

65.36

13 19:00 14.00 10 12:00

1x100

58.08

10 12:00 14.52 1 16:15

1x160 48.16 27 19:00 6.88 6 5:30

1x100 30.32 19 5:00 6.48 1 15:15

1x100 28.96 19 5:00 6.12 1 15:15

1x160 66.40 23 19:00 6.16 9 19:45

1x160 48.52 14 21:15 10.64 11 14:45

53.64 1 19:30 13.12 8 18:00

66.92 8 18:30 25.92 28 14:00

66.92 8 18:30 25.76 28 14:00

1x100 22.12 29 18:00 0.00 1 0:15

1x100 16.44 18 14:00 0.00 1 0:15

1x160 53.16 29 17:45 0.00 1 0:15

49.52 23 21:45 6.40 12 6:00

48.36 27 17:00 6.32 12 6:00

25.36 9 12:00 4.16 19 5:30

24.84 9 12:00 4.16 19 5:30

23.60 9 12:00 3.56 19 5:45

55.80 30 11:00 12.00 7 5:15

47.40 16 11:15 16.80 5 5:00

114.28 25 12:15 6.00 14 17:15

101.76 20 22:30 9.76 14 17:30

1x100 58.52 20 22:45 3.48 25 13:15

1x100 51.44 5 21:00 6.24 19 4:00

1x160 84.56 5 21:00 17.04 27 19:00

1x160 86.16 5 21:00:00 9.40 19.00 4:00

4x100  52.28 23 19:00 17.88 9 19:45

56.00 30 8:30 7.12 24 12:15

54.80 30 8:30 13.44 29 19:30

54.56 30 8:30 13.92 29 19:30

2x100 46.76 22 20:15 10.08 30 10:45

44.52 22 20:15 10.12 30 10:45

1x160 72.48 22 20:15 15.40 30 10:45

1x160  57.34 16 20:00 0.00 3 0:00

1x160 57.34 16 20:00 0.00 3 0:00

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 



THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

Rayagada & 

Paralakhemundi can be fed 

from Machhkund system.

TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 



Mendhasal { Part area load of Khurda S/S} 2x100

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, 

Digapahandi, Mohana.}

2x160



PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & 

Katapali area load.}

Supported by Burla & 

Chipilima power.

LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

2x160

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100

CUTTACK

DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, 

Jajpur Road, Kalarangi, Jajpur Town}



JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

3x100 

"*" - Alternate P/S from 

Kuchei.

BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

2x160

BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), 

MCL, Sundergarh,Brajarajnagar, 

Rajgangpur}

2x160 



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }



BARGARH 220/132 kV

BHADRAK 220/132 KV

{Bargarh, Ghensh}

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}



BIDANASI 220/132 KV

{Bidanasi, Khurda }



Drawal details

Maximum Minimum

ATRI                                                     

{Banki, Khurda, Chandpur & Argul}

2x160

BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

3x160 


E. DISCOM Drawal up to the month of September’19
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	Apr’19
	798
	760.542
	857.404
	18.345
	839.059
	78.517

	
	May’19
	770.33
	664.438
	689.035
	16.166
	672.869
	8.431

	
	June’19
	798
	758.651
	793.853
	17.431
	776.422
	17.771

	
	July’19
	770.33
	778.505
	798.994
	15.847
	783.147
	4.642

	
	Aug’19
	770.33
	745.852
	785.057
	14.196
	770.861
	25.009

	
	Sept’19
	798
	766.486
	755.33
	15.336
	739.994
	-26.492

	WESCO
	Apr’19
	635
	649.188
	856.374
	149.999
	706.375
	57.187

	
	May’19
	604.71
	703.036
	841.28
	100.32
	740.96
	37.924

	
	June’19
	635
	656.64
	789.792
	110.175
	679.617
	22.977

	
	July’19
	604.71
	670.083
	835.876
	143.639
	692.237
	22.154

	
	Aug’19
	604.71
	637.41
	1043.79
	423.111
	620.682
	-16.728

	
	Sept’19
	635
	650.296
	908.15
	281.184
	626.966
	-23.33

	NESCO
	Apr’19
	517
	478.905
	600.692
	99.608
	501.084
	22.179

	
	May’19
	521.48
	508.934
	629.852
	89.858
	539.994
	31.06

	
	June’19
	517
	490.244
	607.403
	105.15
	502.253
	12.009

	
	July’19
	521.48
	532.112
	660.208
	131.831
	528.377
	-3.735

	
	Aug’19
	521.48
	493.554
	627.779
	128.157
	499.622
	6.068

	
	Sept’19
	517
	451.669
	557.042
	99.737
	457.305
	5.636

	SOUTHCO
	Apr’19
	331
	303.576
	334.361
	0
	334.361
	30.785

	
	May’19
	310.85
	320.055
	336.003
	0
	336.003
	15.048

	
	June’19
	331
	318.393
	324.819
	0.116
	324.703
	6.31

	
	July’19
	310.85
	315.891
	305.83
	0.061
	305.769
	-10.122

	
	Aug’19
	310.85
	291.711
	296.609
	0
	296.609
	4.898

	
	Sept’19
	331
	298.482
	290.17
	0.007
	290.163
	-8.319


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
Members may please discuss.

F. Energy Generation / Import up to the month of September’19
Figures in MU  
	Month
	Thermal

(TTPS+IbTPS)
	OHPC 
& MKD
	CGP Support
	IPP Inj.
	RE
	ISGS
	Total

	April’19
	588.681
	538.473
	308.480
	263.019
	29.852
	1057.035
	2785.540

	May’19
	608.185
	571.561
	290.845
	203.850
	46.247
	916.949
	2637.637

	June’19
	581.856
	414.962
	329.321
	212.683
	47.362
	1066.419
	2652.603

	July’19
	566.902
	407.505
	363.839
	198.433
	46.030
	1171.210
	2753.919

	Aug’19
	359.551
	836.840
	345.534
	56.723
	46.535
	1278.578
	2923.761

	Sept’19
	828.709
	808.759
	328.938
	75.013
	44.608
	694.453
	2780.479

	Total
	3533.882
	3578.100
	1966.958
	1009.721
	260.634
	6184.644
	16533.939


G.  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of September’19 are as detailed:
	Month
	Total Generation
	Odisha Drawl
	AP Drawl

	
	MU
	Avg (MW)
	MU
	Avg (MW)
	MU
	Avg (MW)

	Apr’19
	53.168
	73.84
	24.896
	34.58
	26.401
	36.67

	May’19
	60.577
	81.42
	26.811
	36.04
	31.821
	42.77

	June’19
	52.203
	72.50
	22.395
	31.10
	30.840
	42.84

	July’19
	59.779
	80.35
	26.579
	35.73
	31.116
	41.82

	Aug’19
	53.318
	71.66
	24.773
	33.30
	27.139
	36.48

	Sept’19
	52.348
	72.706
	23.869
	33.151
	26.276
	36.494

	Total
	331.393
	
	149.323
	
	173.593
	


In the 136th PSOC meeting Southco stated that Dasmantpur feeder in expected to be charged today i.e on 21.08.2019.

Sr.GM (O&M), Zone –I suggested to explore the following link lines for providing adequate matching load in Machhakund system. 

i.   Connecting Patangi S/S or Proposed Lamtaput S/S with Podagada S/S through 132 kV link.

ii.  Providing Sunabeda S/S area load in Machhakund system

iii.  Modification of Jayanagar S/S to accommodate Jayanagar load 

In the 137th PSOC meeting, SOUTHCO stated that 33 kV Dasmantpur feeder did not stand after charging. Insulators are being changed by the contractor. Sr. GM (Const) stated that 132 kV Patangi-Podagada line is under construction and expected by March’2010. He also suggested to utilize 132 kV NALCO-Sunabeda line to feed Sunabeda area load from Machhakund system by bus splitting. 
GRIDCO / O&M/SLDC/SOUTHCO may deliberate.
H. Under Frequency Relay operation in OPTCL System during the month of September’19.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of September’19.
I. Status of Open Access applications up to the month of September’2019
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected
	MU

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	
	

	1
	April’19
	48
	100
	0
	24
	172
	48
	100
	0
	24
	172
	0
	522.98

	2
	May’19
	21
	  92
	0
	29
	142
	21
	  92
	0
	29
	142
	0
	487.30

	3
	June’19
	49
	106
	0
	32
	187
	49
	106
	0
	32
	187
	0
	641.01

	4
	July’19
	94
	  60
	0
	28
	182
	94
	  60
	0
	28
	182
	0
	726.36

	5
	Aug’19
	114
	132
	0
	38
	284
	110
	132
	0
	38
	284
	4
	904.48

	6
	Sept’19
	66
	122
	0
	58
	246
	66
	122
	0
	58
	246
	1
	576.64

	
	Total
	392
	612
	0
	209
	1213
	392
	612
	0
	209
	1213
	5
	3858.77


PART C – Issues discussed in the 162st OCC meeting of ERPC on 22.10.2019

C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	31.03.20
	162.5 Cr.
Total expenditure may not exceed Rs. 68 Cr.
	38.09Cr. Received Rs. 8.00 Cr on 28.03.19 
	95% equipment installed and commissioned. Tender for measuring instruments under evaluation. 

	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.22 Cr

	2.56 Cr received as 10 % DPR. Claimed for 20 %.
	Order placed. Expected by Nov’19. Inspection under process.

	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov18
Chiplima

Dec 2018
	22.35 Cr.
	2.674 Cr
	Placed work order for Balimela. PO for other units amounting Rs. 12.79 Crs placed. Order under process.

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 
	27-07-18
	
	31.94 Cr
Ested. Cost. Approved amount 30.26 Cr. Grant amount 27.23 Cr.
	Rs.2.72 Cr received as 10% of DPR. Retendering under process.
	Agreement signed and sent to NLDC for signature. Retendering already done.

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost. 2.93 Cr recommended by Appraisal committee.
	
	CERC approval received. Tendering under process.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	12.03.2018  Date of submission 
	
	41.1 Cr

Estt cost
	10% of DPR to be asked.
	Project approved.  Tender to be floated after revision of specification. Agreement sent to NLDC. 


CGM (Const)/CGM (O&M) / OHPC may deliberate

C.2: Finalization Outage Request and processing timeline--ERLDC 

The procedure for timeline regarding submission of outage request till approval of the outage formulated by ERLDC has been circulated and discussed in 156th OCC meeting held at NTPC, Kahalgaon. The same had also been presented in 157th OCC meeting held at ERPC, Kolkata for beneficiary’s comments/suggestion. Till date ERLDC did not receive any objection/suggestion from the utilities. Under this circumstance, the procedure mentioned through a flow chart in Annexure-B15 may be approved and minute unless any modification/suggestion recommended. In 158th OCC, all the constituents were advised to submit their comments on outage procedure within a week. OCC decided to finalize the procedure in next OCC Meeting. 
 In 161st OCC it was informed that comments have been received only from Powergrid.   

OCC advised all the other constituents to submit their comments to ERLDC at the earliest.   

In the 136th PSOC meeting it was decided that SLDC and O&M shall submit feedback to ERPC

SLDC stated that this issue was discussed in the OCC. CGM (O&M) / CGM (Const) may forward their comments, if any to ERPC directly.

SLDC / O&M may deliberate.

C.3: Implementation of Automatic Demand Management Scheme

The latest status along with proposed logic as follows: 
	Sl. No
	State /Utility
	Logic for ADMS operation
	Implementation status/target
	Proposed logic (if different from under implementation logic

	1
	Odisha
	1. System Frequency < 49.9 Hz 
2. Odisha over-drawl > 150 MW
3. DISCOM over-drawl > (40 MW) 
	10 Months

Sent for PSDF approval
	Logic 2 and 3 is AND or OR, in case it is AND then ADMS may not operate when DISCOMs are in schedule but GRIDCO is over drawing due to less generation at State embedded generators.


In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 123rd PSOC meeting SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval.
In the 133rd PSOC meeting a committee was constituted with representatives of DISCOM, Telecom, IT & SLDC.

A meeting of the Committee was held on Dt. 06.07.2019. SLDC made a presentation on the logic and methodology to be adopted for the ADMS. The technical specifications prepared by SLDC were shared among the concern wings of OPTCL for their views. The specification will be finalized on receipt of the same. The DISCOMs were requested to update the list of feeders and group considering the present network configuration. On finalization of the above, the tendering process will be taken up by CPC wing of OPTCL as already approved by CMD, OPTCL.

The role of different wings was discussed in the meeting as tabled.     

[image: image8.emf]Role of different wings of OPTCL for implementation of ADMS  

Task  Responsible Entity in OPTCL  

Preparation of Tender Document   and  finalization of ADMS logic  SLDC   

Finalization of Technical Spec.   Telecom wing, OPTCL  

Floating of Tender  CPC wing, OPTCL  

In terfacing between SCADA and  ADMS Server at SLDC  Telecom wing, OPTCL  

Communication link between SLDC  ADMS Server and Grid S/S  IT /  Telecom wing, OPTCL  

Installation of RTU at Grid S/s  Under the supervision of O&M /  Telecom wing,  OPTCL  

Connection of 33KV t rip Ckt. with  RTU at Grid S/S  Under the supervision of  O & M wing, OPTCL  

Updating and Grouping of 33KV  feeders  Discom  

Day to day monitoring of ADMS  SLDC  

Bidding Guidelines  As per OPTCL procurement guidelines  

 


As decided in the 135th PSOC meeting, SLDC convened a meeting on 06.08.2019 with Telecom, O&M, IT and CPC to discuss their rolls in the ADMS project.

The Technical & Commercial specification have been approved by the committee and forwarded to CPC for processing the Tender. 
In the 137th PSOC meeting, it was suggested by CGM (Telecom) that BoQ & SoQ in different formats need to be matched and technical sanction shall be made by SLDC and forwarded to CPC for necessary action.

SLDC may deliberate
C.4: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 137th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by March’20.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) & 220 kV D/C line
	220 kV S.C line and Keonjhar S/S (220/33 kV), 2x20 MVA charged on 31.12.2018. 2nd ckt; charged on 03.08.2019.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) & 220 kV D/C Line.
	By 2021. Order placed.

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C
	December’2019 


C.GM (Cont) / CGM (Telecom) may update.
C.5: Bypassing arrangement of LILO of 400kV Lines at Angul 

LILO of Meramundali-Bolangir/Jeypore 400 kV S/C line and LILO of one Ckt of Talcher-Meramundali 400 kV D/C line has been done at Angul 765/400kV Sub-station. The bypass arrangement for these circuits is under implementation at Angul by Powergrid.  

In 158th OCC, Powergrid informed that bypass arrangement would be completed by August 2019. OPTCL informed that 2nd circuit of 400 kV Meramundali-Mendhasal line would be commissioned 
by 1st week of August 2019.  

OPTCL informed that 2nd circuit of 400kV Meramundali-Mendhasal line would be commissioned by end of August 2019. 

As per POWERGRID email dated 16th September, the anticipated date for commissioning of the LILO by-pass arrangements at Angul SS is by end of Oct’2019. 

OCC advised POWERGRID to take urgent steps for commissioning of the bypass arrangement. Delay in implementation of the arrangement is causing loss of operational flexibility besides subjecting the grid to the risk of high fault current.

In the 137th PSOC meeting, DGM (Const) stated that 3rd ICT at Mendhasal in under testing. O&M stated that tree clearance has already been completed. After commissioning of the ICT, 400 kV Mendhasal-Meramundali 2nd ckt will be charged.
O&M may update.

C.6: Update on status of telemetry  

CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action. Major issues are given below:

i. Regarding frequent intermittent of real time SCADA data from Talcher STPS Stage 1 & 2, NTPC agreed to provide additional ports by March 2019. 
ii. Alternate path for Malda–Farakka OPGW link In 153rd OCC, Powergrid was advised to implement alternate OPGW link through 400 kV Kishenganj- Darbhanga-Muzaffarpur lines. 
In 159th OCC, ERLDC informed that PMU data available at ERLDC is intermittent due to communication issues and PMU data reporting from PDCs at SLDCs is also intermittent. ERLDC opined that alternate OPGW link is required for reliable communication. OCC advised Powergrid to take the necessary action to resolve the issue. CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed, NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action.  

Issues relating OPTCL Network: 

Narsingpur data: 
In the 132nd PSOC meeting CGM (Telecom) stated that survey work for Meramundali-Bhanjanagar line is under process. OPGW will be reached at site after completion of survey and preparation of drum schedule. 
In the 134th meeting CGM (Telecom) stated that delivery of OPGW has already been started. 

In the 135th PSOC meeting DGM (Telecom) stated that replacement of earth wire by OPGW in 220 kV Bhanjanagar-Meramundali is expected by December’2019

NALCO data: DGM (Telecom) stated that the vender list and rate will be provided to NALCO for placement of order by them.

In the 137th PSOC meeting, NALCO stated that the estimate has already been received from OPTCL (Telecom). Approval from higher authority in under process.

Telecom / NALCO may deliberate the status

C.7: Mock Black start exercises in Eastern Region – ERLDC 

 Schedule and tentative date for conducting mock black start exercise in OHPC stations is as tabled. 

	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2019
	Done on 19th July19
	Last week of January 2020
	

	3
	Rengali
	2nd week of June 2019
	Done on June’19
	Last week of November 2020
	

	4
	U.Indravati
	3rd week of June 2019
	Nov’ 2019
	2nd week of February 2020
	

	6
	Balimela
	3rd week of October  2019
	Done on 17th July19
	1st week of March 2020
	Dec’2019

	9
	Burla
	Last week of June 2019
	Done on 20th July’ 2019
	Last week of February 2020
	Dec’2019


In the 136th PSOC meeting, SLDC stated that while conducting mock Black start exercise for Upper Kolab and Upper Indravati HEPs Muniguda Traction feeder is getting interrupted. In view of the above, feeding of Muniguda Traction S/S from Theruvali S/S through a separate dedicate line may be examined. 

In the 137th PSOC meeting, Sr. G.M (O&M), Zone-1 suggested to put Rayagada area load on Indravati for black start exercise. SLDC may develop the procedure accordingly. 

Since Rayagada area load is not adequate (15 MW) to run the Indravati unit, it is proposed to connect Kesinga area load for Indravati HEP Black start exercise. Muniguda traction shall be interrupted during the mock drill. Vinto Solar generation and Kesinga traction shall be shifted through bus splitting.   

SLDC / O&M/ OHPC may deliberate
C.8: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC 

As a National Grid operator, POSOCO is continuously working for ensuring reliability and security of the Grid. With penetration of more and more renewable energy source the task is becoming complicated day by day.  An accurate dynamic modeling of the National Grid needs modeling of conventional as well as renewable / distributed generation sources. World Bank has engaged Digsilent as consultant for assisting POSOCO for building dynamic model of the Grid. A guideline for dynamic data collection has been developed in consultation with Digsilent Pacific team.   All the utilities are requested to collect data from the grid scale renewable power plants as well as from conventional power plants under their jurisdiction and submit the same to ERLDC/ERPC as early as possible. 

In the 157th OCC advised all the SLDCs to submit the details to ERPC and ERLDC.  Format along with an explanation for collection of Wind and Solar Data had been shared by ERLDC with all SLDCs. 

Bihar/ West Bengal and Orissa are having Solar Plant with more than 5 MW capacity. However, details have not yet been received in terms of modeling data.

In the 132nd PSOC meeting, all generators as well as RE sources were requested to furnish data to SLDC for onward transmission to ERPC.
In the 137th PSOC meeting, SLDC stated that the format has been forwarded to all entities and GRIDCO. It was requested that GRIDCO may pursue to all RE generators to submit the data. 
GRIDCO / SLDC may update
C.9: Implementation of Automatic Generation Control in Eastern Region--ERLDC

In compliance to CERC’s direction in order dated 06/12/2017 in petition no 79/RC/2017, AGC was commissioned in NTPC Barh on 01st August 2019 and operationalized since 23rd August, 2019.

Vide order dated 28th August 2019, CERC in Petition No.: 319/RC/2018 directed that all the ISGS stations whose tariff is determined or adopted by CERC shall be AGC-enabled and the ancillary services including secondary control through AGC be implemented as per the following direction:

I. All thermal ISGS stations with installed capacity of 200 MW and above and all hydro stations having capacity exceeding 25 MW excluding the Run-of-River Hydro Projects irrespective of size of the generating station and whose tariff is determined or adopted by CERC are directed to install equipment at the unit control rooms for transferring the required data for AGC as per the requirement to be notified by NLDC. NLDC shall notify the said requirements within one month of this order.

II. All such ISGS stations whose tariff is determined or adopted by CERC shall have communication from the nearest wide band node to the RTU in the unit control room.

xxxxxxxxx
IX. All new thermal ISGS stations with installed capacity of 200 MW and above and hydro stations having capacity exceeding 25 MW excluding the Run-of-River Hydro Projects irrespective of size of the generating station and whose tariff is determined or adopted by CERC shall mandatorily have the capability to provide AGC support.

Member may discuss

C.10: Submission of data in MERIT Order portal--CEA 

CEA vide mail dated 9th July 2019 informed that the MERIT Order portal had been launched on 23rd June, 2017 by Honourable  Minister of Power. One of the most important advantages of “Merit” Portal is Transparent information dissemination pertaining to marginal variable cost and source wise purchase of electricity and indication of supply side reliability, adequacy, and cost of power procurement. 

However, it has been observed that many of the states are not filling the data regularly and sometimes the data filled varies widely from the data available on the respective RLDCs daily reports.  

It is requested that the states may be advised to fill the data regularly and check that correct data is filled on the MERIT Portal. 

In 159th OCC, all the SLDCs were advised to fill the correct data in MERIT portal on regular basis.

SLDC may deliberate

C.11: Data for preparation Load Generation Balance Report (LGBR) of ER for the year 2020-21

As per the IEGC, RPC Secretariat is responsible for finalization of the Annual Load Generation Balance Report (LGBR) for Peak as well as Off-peak scenarios and the annual outage plan for the respective region To facilitate the preparation of LGBR of Eastern Region by ERPC Secretariat within the schedule period, the following data/information for the year 2020-21 in respect of the constituents/utilities of Eastern Region is urgently required:

i)  The unit wise and station wise monthly energy generation proposed from existing units during 2020-21 (thermal/hydro/RES).

ii)  Annual maintenance programme for each of the generating units (thermal and hydro both).

iii)  Generating units under R&M / long outage indicating date of outage and reasons of outage and expected date of return (thermal and hydro both).

iv) Partial and forced outage figures (in %) of generating units for the last 3 years.

v) Month wise peak demand (MW) – restricted and unrestricted peak demand.

vi) Month wise off-peak demand (MW).

vii) Month wise energy requirement (in MU).

viii) Month wise & source wise power (both MU & MW) purchase and/or sale plan.

ix) Schedule of commissioning of new generating units during 2020-21 and unit-wise

monthly generation programme (in MU).

x) Allocation of power from new generating units.

xi) Month wise and annual planned outage of transmission system (Transmission lines 220kV and above / ICTs / Reactors/ other elements.

Information may please also be submitted in the form of soft copy through email (mail ID: mserpcpower@nic.in / erpcjha@yahoo.co.in).

Members may furnish the above data.

C.12: Monitoring of Next Six-Month New Element Integration in OCC and Its Update on Monthly Basis --ERLDC

It has been observed that many elements are getting interconnected into the system and beforehand details are not available with the system operator resulting in difficulty in carrying our operational planning activity. In view of this, as a regular agenda all ISTS and ISGS/IPP to update the OCC regarding any new elements at 220 kV and above which will be integrated in next six month with the grid. For State Grid, SLDC will be submitting the details on behalf of its intrastate Generation and transmission system. The format is given below:

	Transmission

Elements


	Agency/

Owner


	Scheme (ERSS/

TBCB/ Standing

Committee/State


	Schedule

Completion


	Projected

Month for

Completion


	Issue

Being

Faced



	
	
	
	
	
	


In previous several OCC, Transmission licensees and SLDCs are requested to submit RLDC/RPC following details on monthly basis

· List of transmission element /generators of State and ISTS licensees synchronised in the last month.

· List of transmission element /generators expected to be synchronised during next month or in near future

Some SLDCs are submitting the list of intrastate and interstate line on regular basis, however transmission element /generators expected to be synchronised during next month or in near future is not submitted by any SLSC/Transmission licensee to RLDC/RPC.

SLDC may explain, CGM (Const) / CGM (O&M) may deliberate
C.13: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

The activity of the preparation of Crisis Management Plan for countering the cyber-attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA. 

In 142nd OCC, ERLDC informed that, in line with Enquiry Committee Recommendation, cyber security audit is being conducted on regular basis for SCADA system installed at ERLDC and SLDC as well but cyber security audit for telecom infrastructure installed in Eastern Region is not being carried out.  

OCC advised all the constituents to conduct the cyber security audit on telecom infrastructure installed in Eastern Region. It is further advised that compliance / mitigation of the points observed during the audit should also be completed for improvement of the telecom infrastructure in ER. 

As suggested by CEA, a format has been circulated among ER constituents for furnishing the information of the respective systems for discussion in OCC Meeting. The format is enclosed at Annexure-E1. 

OCC advised all the constituents to submit the information to ERPC as per Annexure-E1.
OPTCL has submitted the required data 

In the 136th PSOC meeting, IT wing was requested to submit the quarterly report for the quarter ending September’2019.

In the 137th PSOC meeting, IT stated that after completion of the audit, the quarterly report will be submitted. Further, Telecom may intimate the details of their infrastructures to be incorporated in Cyber Security audit.  

Sr. G.M (IT) /Telecom may update
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of Sept’19:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	-26.492
	3.45

	2
	WESCO
	0
	-23.330
	3.58

	3
	NESCO
	0
	5.636
	1.248

	4
	SOUTHCO
	0
	-8.319
	2.787

	
	Total
	0
	-52.505
	


It is noticed that all the DISCOMs except NESCO were under drawn during the month, while NESCO have over drawn. CESU has deviated 3.45% followed by WESCO 3.58% from the scheduled energy while SOUTHCO & NESCO have deviated 2.787 % & 1.248 % respectively. DISCOMs may forecast their drawal in realistic approach to minimise deviation. Daily drawal profile of all DISCOMs is as follows. 
[image: image9.emf]0

200

400

600

800

1000

1200

1400

1600

1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 29 30

MW

DAY--------->

PEAK & AVERAGE DRAWL OF CESU (Sept/19)

PEAK AVERAGE


[image: image10.emf]0

500

1000

1500

2000

2500

1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 29 30

MW

DAY--------->

PEAK & AVERAGE DRAWL OF WESCO (Sept/19)

PEAK AVERAGE


[image: image11.emf]0

200

400

600

800

1000

1200

1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 29 30

MW

DAY--------->

PEAK & AVERAGE DRAWL OF NESCO (Sept/19)

PEAK AVERAGE


[image: image12.emf]0

100

200

300

400

500

600

1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 29 30

MW

DAY--------->

PEAK & AVERAGE DRAWL OF SOUTHCO (Sept/19)

PEAK AVERAGE


SLDC/ Discoms may please deliberate.
D.2: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.

In the 125th PSOC meeting GRIDCO have agreed to write a letter to M/s Chemtrol. It was decided that a committee shall be constituted with representatives of GRIDCO, O&M, Telecom & SLDC to take a decision.

In the 134th PSOC meeting, GRIDCO stated that M/s Camptrol has successfully completed the pilot project i.e real time data communication for MGM Solar at Tangi. 

A committee has been constituted with representatives of GRIDCO, O&M, Telecom & SLDC. This issue was also discussed in the 16th GCC meeting held on 09.08.2019. GRIDCO assured to make a demo of data communication from MGM Solar at Tangi to SLDC by end of August’19. 
In the 137th PSOC meeting, DGM (Telecom) stated that M/S Chemtrol has made a Demo but GRIDCO was not present to witness. However’ Chemtrol has agreed to show a Demo in last week of Sept’2019 with prior intimation to GRIDCO. 

GRIDCO may deliberate the status.

D.3: Data communication from newly commissioned RE sources connected at 132 kV- SLDC
There are as many 8 Nos. of Solar projects with installed capacity of 272.5 MW have connected with OPTCL network through 132 kV lines. The real time data of these plants are yet to be received at SLDC control room. Since the generation quantum is quite substantial (to the tune of 0.6 MU during a day), this has an impact on real time generation monitoring. 

In the 132nd PSOC meeting it was decided that SLDC shall convene a meeting with the defaulting Solar units and Telecom to discuss the issue. 

In the 133rd PSOC meeting CGM (Telecom) stated that Vinto Solar data can be integrated only after laying of optical fiber, which has been proposed for PSDF funding

In the 134th PSOC meeting, CGM (Tel) stated that release of optical fiber has already processed.

This issue was discussed in the 16th GCC meeting held on 09.08.2019, where Director (Commercial) suggested to prioritize data communication from Solar plants.

In the 137th PSOC meeting CGM (Telecom) stated that laying of optical fiber is expected to be completed by December’2019. DGM (Telecom) suggested that SLDC may write a letter to Vento Power (Solar) at Kesinga to explore the data communication, since all communication equipment are available with them. Data communication can be made through after visit of the service Engineer of the company.

SLDC /Telecom may deliberate the status. 
D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos. of meters integrated, around data from 750 nos. of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos. of meters integrated, data from 717 nos. of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos. of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 133rd PSOC meeting, DGM (IT) stated that Paralakhemundi and Balasore S/S meter data has been tested. The software fetching data for other S/Ss will be tested
In the 136th PSOC meeting, IT stated that the meter data has been checked and presentation done on 2nd August’2019.  The same has been forwarded to SLDC.

In the 137th PSOC meeting IT stated that, the software developed by M/S TCS has been tested for DLMS -2 energy meters. This has to be developed for DLMS-3 type energy meters. TCS has asked for one month time for the same.
IT / SLDC may update the status
D.5: Colony consumption of POWERGRID S/Ss

In the 131st PSOC meeting SLDC stated that POWERGRID is consuming power for their colony, which is not reflected in the DISCOM bill. POWERGRID stated that they have applied to DISCOMs to make them consumer. 

It was decided that SLDC shall convene a meeting between GRIDCO, POWERGRID & DISCOMs to discuss the issue.

In the 133rd PSOC meeting it was decided that all Discoms shall submit the details of their problems regarding making POWERGRID their consumer, to GRIDCO for raising the issue in the Commercial Committee meeting of ERPC.

In the 134th PSOC meeting it was decided that SLDC shall prepare the energy accounting considering consumption of POWERGRID. The DISCOMs may insist POWERGRID stations in their respective control area to become their consumer. SLDC has prepared the energy Accounting of DISCOMs including drawal of POWERGRID.

In the 136th PSOC meeting it was decided that GRIDCO shall write a letter to ERPC to convene a special meeting involving POWERGRID and add DISCOMs of the State to resolve the issue. This item has been listed in the OCC agenda.
In the 137th PSOC meeting it was suggested that the DISCOMs may file Petition before the OERC separately to resolve the issue.

DISCOMS may discuss

D.6: Dispute in Energy Accounting of DISCOMs 

It is noticed that DISCOMs are frequently raising disputes in the monthly Energy Accounting before GRIDCO, which are being forwarded to SLDC subsequently by GRIDCO. SLDC is clarifying the disputes, which is a lengthy and time consuming process. It is requested that the executives of DISCOMs involved in the billing activity of DISCOMs may attend SLDC EASSC personally to resolve their disputes.

DISCOMs may discuss.  

PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the last meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	220 kV Jayanagar-Jeypore(PG) 2nd DC line 
	December’2019

	2
	400 kV Meramundali-Mendhasal 2nd ckt.
	October’2019

	3
	132 kV Kesinga-Junagarh line
	October’2019

	4
	220 kV Pandiabili-Pratapsasan line
	March’20

	5
	132 kV Pratapsasan-Phulnakhara line
	Dec’19

	6
	220/132/33 kV,  Pratapsasan S/S
	Dec’19

	7
	220/33 kV, Deogarh S/S
	March’20

	8
	132/33 kV, Maneswar S/S
	March’20

	9
	132/33 kV, Boriguma S/S
	Feb’20

	10
	220/33 kV, 2x20 MVA Baliguda S/S
	March’20

	11
	220/33 kV, 2x20 MVA Kalimela S/S
	April’20

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	March’20

	13
	220/132 kV Kesinga S/S
	Mar’20

	14
	132/33 kV R.Udyagiri S/S
	Mar’20

	16
	220/33 kV Laxmipur S/S 2nd 20 MVA Tfr
	Oct’19

	18
	132/33 kV, Mancheswar GIS
	Dec’19

	19
	132/33 kV, Satasankha S/S
	Dec’19


All the Discoms are requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. 
CGM (Construction) / DISCOMs may deliberate
E.2: HT metering at DISCOM interface points.-SLDC.

As per the Central Electricity Authority (Installation and Operation of Meters) Amendment Regulations, 2010, the interface meters shall be installed at the High Voltage side of the Inter Connecting Transformer. Accordingly POWERGRID has implemented the amended Regulation. GRIDCO / OPTCL may examine for metering in the High Voltage side of the ICT, which is done in the Low Voltage side at present.

In the 134th PSOC meeting, SLDC stated that Gridco may convene a meeting with DISCOMs and OPTCL to implement CEA Regulation to reduce the loss level of State system and increase revenue of GRIDCO. Further OERC vide order dated 29.03.2019 in case No. 71/2018 in the matter of ARR and Transmission tariff of OPTCL at Para 181 directed OPTCL to take necessary steps for reduction of transmission loss by avoiding over loading as well as other innovative action.  

This issue was also discussed in the 16th GCC meeting, where the DISCOMs highlighted the PPA provision for receiving power at 33 kV Voltage level by them. Director (Commercial) agreed to convene a meeting between DISCOMs, O&M & SLDC to discuss the issue. If required, GRIDCO shall approach the Hon’ble OERC for amendment of the PPA/ Supply Code if required to comply CEA Regulation. 

In the 136th PSOC meeting, GRIDCO has agreed to convene a meeting in the month of September’19 to discuss the issue

In the 137th PSOC meeting it was requested that GRIDCO may convene a meeting to discuss the issue
OPTCL / GRIDCO may deliberate 

E.3: Major Events in the month of September’19
1. On dt. 15.09.19 at 12:50 Hrs - 132/33 kV, Pottangi Grid S/S bus charged. (132 kV Sunabeda- Pottangi SC line has already been idle charged since 14:56 Hrs dt. 16.01.19). At 13:20 Hrs dt. 15.09.19 -20 MVA, 132/33 kV Power Transformer charged at Grid S/S, Pottangi.
Members may note

E.4: Important Grid Incidences during the month of September’19.
No major grid disturbances occurred during the month Sept-19.
E.5: Outage of major transmission Elements during the month of September’19. (above 10 hrs).
	Sl No
	Transmission line / element
	Tripping 

Dt/time
	Restoration

Dt/time
	Reason

	1
	132 kV Balasore - Udala ckt
	02.09.19 /13:56 Hrs
	03.09.19 /17:13 Hrs
	Insulator strings damaged at location no. 97, 98 & 100.

	2
	220 kV Meramundali- Duburi (Old) ckt -II
	03.09.19/ 15:42  Hrs
	04.09.19/ 12:43 Hrs
	Snapping of conductor

	3
	220 kV Tarkera –Rengali ckt - II
	05.09.19 /20:52 Hrs
	06.09.19 / 08:57 Hrs
	Charged after thorough patrolling

	4
	220 kV Theruvali - Bhanjanagar ckt -I
	10.09.19 / 00:26 Hrs
	11.09.19 / 18:20 Hrs
	Y- phase conductor snapped  at loc. 1015 to1016

	5
	132 kV Duburi  (Old)– Mesco fdr
	10.09.19 / 17:27 Hrs
	Under breakdown condition
	Insulator puncture at Loc No - 31

	6
	220 kV Narendrapur- Atri ckt-I
	18.09.19 /13:48 Hrs
	20.09.19 /12:22
	CVT found to be defective at Atri end.

	7
	160 MVA Auto –II at Grid S/S, Paradeep
	18.09.19 / 05:10 Hrs
	21.09.19 / 13:39 Hrs
	220kV cross bus insulator punctured & conductor snapped at PDP switchyard.

	8
	132 kV Rourkela – BK Steel feeder
	19.09.19 / 03:45
	19.09.19 / 17:14 Hrs
	Snapping of Line Conductor due to tree falling.

	9
	220 kV Theruvali -Kolab ckt -III
	21.09.19 / 14:46 Hrs
	24.09.19 /19:26 Hrs
	Insulator failure at loc 705 to 706

	10
	220 kV Bolangir (New) – Bolangir (PG) ckt
	23.09.19 / 18:42 Hrs
	24.09.19 / 19:06 Hrs
	Snapping of R-Ph conductor

	11
	220 kV Bolangir (New) – Bargarh (New) ckt
	24.09.19 / 17:49 Hrs
	25.09.19 / 17:05 Hrs
	Insulator failure at loc No 292 & 293

	12
	132 kV Jajpur Road – Jajpur town fdr
	24.09.19 / 19:03 Hrs
	25.09.19 / 22:38 Hrs
	Y-ph CT burst at  Grid S/S, Jajpur Town

	13
	132 kV Paradeep – PPL ckt -II
	28.09.19 / 15:24 Hrs
	03.10.19 / 17:18 Hrs
	R-ph LA burst at Paradeep switchyard

	14
	220 kV Theruvali –Indravati ckt -I
	30.09.19 / 02:37 Hrs
	03.10.19 / 08:29 Hrs
	Insulator failure at Tower location no-200


O&M may discuss
E.6: Prolonged outage of Transmission elements

	Sl No
	Transmission line / element
	Date of outage
	Reason
	Expected date of restoration

	1
	220 kV Samangara – Pandiavil ckt –I& II
	03.05.19
	Tower collapsed during the severe cyclonic storm FANI.
	


E.7:  Review of Outage Program of State Generators for the month of November’19:
Tentative Outage programe for State Generators for the month of November’2019 
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 5

# 6
# 7
	14.03.18 to continue
25.10.16 to continue

16.10.15 to continue
01.11.19 to 30.11.19
	T&G coupling cover water leakage
Under R,M & U

Under R, M & U
Annual Maintenance

	2
	Chipilima
	# 1
	15.11.19 to 14.12.19
	Annual Maintenance

	3
	Balimela
	# 1
# 2
# 8
	05.08.16 to continue
20.11.17 to continue
05.11.19 to 29.11.19
	Under R,M work
Under R,M work
Annual Maintenance

	4
	Rengali
	# 4
	01.11.19 to 30.11.19
	Annual Maintenance & PSDF work

	5
	Upper Kolab
	# 1
	04.11.19 to 03.12.19
	Annual Maintenance

	6
	U. Indravati
	# 3
	15.11.19 to 13.12.19
	Annual Maintenance



OHPC may deliberate
E.8: Generation Program for the month of November’19.
Generation schedule for the month of November’19 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.10.19
	Reservoir Level as on 01.10.18
	MDDL
	High Flood    Reservoir Level

	
	Nov’19
(1st fortnight)
	Nov’19
 (2nd fortnight)
	
	
	
	

	HPS-I, Burla
	130
	130
	630.00 ft.
	629.56 ft.
	590 ft.
	630 ft.

	HPS-II, Chiplima
	40
	40
	-
	-
	-
	-

	Balimela
	240
	240
	1513.00 ft.
	1515.30 ft.
	1440 ft.
	1516 ft.

	Rengali
	200
	200
	123.98 mtr.
	121.21 mtr.
	109.72 mtr 
	123.5 mtr.

	U.Kolab
	100
	100
	856.34 mts.
	857.11 mtr.
	844 mtr 
	858 mtr.

	U. Indravati
	300
	300
	641.02 mtr.
	641.08 mtr.
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2748.25 ft.
	2748.10 ft.
	2685 ft.
	2750 ft.

	TOTAL
	1040
	1040
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

SLDC / OHPC may deliberate

E.9: Anticipated power generation and demand for the month of November’2019.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1150
	1300

	2
	WESCO
	1050
	1100

	3
	NESCO
	800
	1000

	4
	SOUTHCO
	400
	500

	5
	Total Discom
	3400
	4000

	
	System Loss & others 
	150
	200

	
	Total Demand
	3550
	4100

	Availability
	
	

	1
	Hydro
	1040 
	1200

	2
	State Thermal
	1100
	1100

	3
	IPP, small hydro &RE
	350
	300

	4
	ISGS share (including OA& purchase)
	900
	1150

	5
	CGP support (OA)
	350
	350

	6
	Total availability
	3740
	4100

	7
	Surplus / Deficit
	190
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (139th) PSOC meeting.
PAGE  

