[image: image1.png]STATE LOAD DESPATCH CENTRE
OFFICE OF THE CHIEF LOAD DESPATCHER

ODISHA POWER TRANSMISSION CORPORATION LIMITED
GRIDCO Colony, P.O.- Mancheswar Rly. Colony, Bhubaneswar-17, FAX-0674- 2748509

CIN = U401020R2004SGCO07553

CLY,

No-SGM (PS)-PL-15/2016/ 3 F &S Dated:0%11.2017

From:

The Chief Load Despatcher
SLDC, OPTCL, Bhubaneswar-17.

To:
As per distribution list

Sub: Minutes of 114™ PSOC meeting held on 27.10.2017 at PTC, Chandaka,
Bhubaneswar

Sir,
Please find enclosed herewith the minutes of 114™ Power System Operational Co-

ordination meeting held on 27.10.2017 at PTC, Chandaka, Bhubaneswar.

This is for your information & necessary action.

Yours faithfully;

Encl: As above \J

\Y
Chief Load Despatcher,
SLDC, OPTCL

Copy along with enclosures forwarded to the Executive Assistant to CMD, Gridco / OPTCL
for kind information of CMD.




Distribution list

1. The Director (Commercial), Gridco, Bhubaneswar

2. The Director (Operation), OPTCL, Bhubaneswar

3. The Director (Projects), OPTCL, Bhubaneswar

4. The Director (Operation), OHPC, Bhubaneswar

5. The CGM (O&M), OPTCL, Bhubaneswar.

6. The CGM (Const.), OPTCL Bhubaneswar.

7. The CGM (RT&C), OPTCL, Bhubaneswar.

8. The CGM (PP), GRIDCO, Bhubaneswar.

9. The CGM (IT), OPTCL, Bhubaneswar.

10. The CGM (Telecom), OPTCL, Bhubaneswar.

11. The Sr. G.M (Const)-I, OPTCL, Bhubaneswar.

12. The Sr. G.M (Const)-II, OPTCL, Sambalpur.

13. The Sr. G.M (CPC), OPTCL, Bhubaneswar.

14. The Sr. G.M (CP), OPTCL, Bhubaneswar.

15. The Sr. G.M. (O&M), Zone-I, Narendrapur 

16. The Sr. G.M.(O&M), Zone-II, Meramundali.

17. The CEO, CESU, Bhubaneswar.

18. The A.O., WESCO, Burla

19. The A.O., NESCO, Balasore

20. The A.O., SOUTHCO, Berhampur.

21. The Member Secretary (GCC), OPTCL.

22. The ED, Power Grid Corporation of India, Bhubaneswar.

23. The Sr. G.M. (El.), BHEP, Balimela

24. The A.G.M. (El.), CHEP, Chiplima

25. The Sr. G.M. (El.), UIHEP, Mukhiguda

26. The Sr. G.M. (El.), RHEP, Rengali

27. The D.G.M. (El.), HHEP, Burla

28. The D.G.M. (El.), UKHEP, Bariniput, Koraput

29. The S.E. (O&M), Machhakund

30. The DGM (Elect.), IbTPS, OPGC, Banharpali.

31. The Vice President (O), IMFA, Choudwar.

32. The D.G.M. (O&M), NTPC (TTPS), Talcher.

33. The AGM (Elect.), JINDAL Stainless Ltd., Duburi

34. The G.M, HINDALCO, Hirakud.

35. The G.M.CPP, NALCO, Angul.

36. The Director, M/s. Jindal Steel & Power Ltd., Angul

37. The AVP-Vedanta Ltd (IPP), Jharsuguda

38. The G.M, Vedanta Ltd (CGP), Jharsuguda.

39. The DGM (Power Distribution), RSP, Rourkela.

40. Joint President, Aditya Aluminium Ltd., Lapanga, Sambalpur

41. The G.M. (Elect.),  Bhusan Steel Limited. Meramundali

42. The G.M. (Elect.), Bhusan Power & Steel Ltd, Budhipadar.
43. The G.M. (Elect.), IFFCO Limited.

44. Director & COO, GMR Kamalanga Energy Limited, Satyanagar, Bhubaneswar.

45. The CEO, Bhubaneswar Power Pvt. Ltd, IRC Village, Nayapalli, Bhubaneswar.

46. M/S Tata Power & Steel Ltd., Kalinganagar

Odisha Power Transmission Corporation Ltd. Bhubaneswar.


Minutes of 114th PSOC meeting held on 27.10.2017 at PTC, Chandaka
List of participants is at Annexure.

CGM, SLDC welcomed all the members to the 114th PSOC meeting. In his welcome address, he highlighted the system performance for the month of September’2017 and overall power scenario of the State. He also emphasized on the power drawal, made by all the Discoms during the month. 
D.G.M. (SS), SLDC took the agenda items for discussion. 

The review proceeded as follows: 
1: Confirmation of minutes of 113th PSOC meeting held on 16.09.2017
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2016/3330(46) dated 25.09.2017 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting:
The minutes of 113th PSOC meeting was confirmed. 
PART B : SYSTEM PERFORMANCE
B1: Review of Grid Performance for the month of September’2017.
(A)  Frequency 

It was noticed that, during the month of September’17, 77.41% of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 70.68 % during the month of  August’17. The maximum and minimum System frequency during the month was 50.17 Hz & 49.72 Hz respectively.

 (B)  Grid demand 

Grid demand for the month of  September’17 was reviewed. The average consumption during the month was 3567 MW. The maximum System demand of 4375 MW occurred on 26.09.17at 21:00 Hrs and minimum demand of 2523 MW occurred on 12.09.17 at 17:00 Hrs. 
Deliberation in the meeting

It is observed that the average demand during the month of  September’ 17 has been increased by 207 MW while the peak demand  was increased by 106 MW from that of August’17. The average demand during the month has been increased by 466 MW in comparison to September’16. Besides normal load growth, import of power by M/s Vedanta Ltd. through Open Access transaction is reason for increase of average demand.
 (C)  Voltage Profile of important Sub Stations in OPTCL System during the month of Sept’17.

The Voltage profile at different 220 kV buses in OPTCL system during the month of Sept’17 was reviewed. 
The maximum Voltage of 247 kV, 241.15 kV & 240.75 kV occurred at Narendrapur, Laxmipur & Jaynagar 220 kV bus. Katapalli 220 kV bus has experienced the minimum Voltage of 205.93 kV. Bus Voltages at Samgara, Lapanga and Cuttack could not be incorporated due to non availability of energy meter in those S/Ss. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Meramundali bus during the month of September 2017 in 15 minute block was reviewed.
Deliberation in the meeting:
The overall Voltage profile of 220 kV buses is satisfactory. Bus Voltage recorded at Chandaka is showing abnormally low due to PT problem. SLDC may monitor the VAr injection by generators & ICT connected to 400kV bus of Meramundali S/S.  





.

 [Action: CGM (O&M) / SLDC]
(D) Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of September’17.

Auto loading of all 220 kV S/Ss was reviewed. It was noticed that some of the Autos have not been provided with energy meter. 
Deliberation in the meeting:
It was deliberated by OPTCL that the meters existing in the panel will be tested & commissioned soon. 









        
        [Action: CGM (O&M)]

(E) DISCOM Drawal during the month of September’17 
The schedule and actual energy drawal by Discoms for the month of September’17 was reviewed. 
Deliberation in the meeting:
It was noticed that CESU had overdrawn 20.079 MU, WESCO had overdrawn 10.738 MU, NESCO had overdrawn 11.177 MU and SOUTHCO had under drawn 1.711 MU during the month. NESCO stated that the over drawal quantum should have been reduced by 4.055 MU due to less drawl by Tata Steel which has already been intimated to Gridco. SLDC stated that NESCO drawal will be revised provided the disputed quantum will be accepted by Gridco.
 [Action: All Distribution Utilities / GRIDCO / SLDC]
(F) Energy Generation / import during the month of September’17 
Energy generation and exchange during the month of  September’17 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2566 MU. 
Deliberations in the meeting
The energy demand has been increased due to import of power by M/S Vedanta Ltd. through Open Access transaction.
 (G) Drawal of Machhakund Power during the month of September’17
The drawal of Machhakund power during the month of September’17 was 18.135 MU, against AP drawal of 19.070 MU. 
Deliberations in the meeting

SLDC stated that RVDU at Jaynagar sub-station is not functioning. Telecom wing may take necessary action to rectify the same early. Construction wing of OPTCL stated that 132/ 33 kV Podagada sub-station is going to be commissioned soon after which matching load on Machhakund system is likely to be increased by 2 – 3 MW. 
 [Action: SLDC / CGM (Telecom)]
(H) Under Frequency relay operation in OPTCL System during the month of September’17.

There is no UF Relay operation during the month of September’17 as the frequency had never gone beyond 48.50 Hz. 
(I) Status of Open Access applications during the month of September’2017
Status of Open Access Applications received and disposed by SLDC during the month was reviewed.

Deliberations in the meeting
Total 209 numbers of Short Term / Medium term and Collective transaction applications have been processed by SLDC for according Approval / Consent / NoC during the month. 
PART C – Issues likely to be discussed in the 138th OCC meeting of ERPC on 30.10.2017
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting held on 29.04.16 at New Delhi, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format. 
The latest status as updated by OPTCL is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	Amount

Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	3
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	04.08.17
	162.5 Cr.


	25.16 Cr.
	Total contract awarded for

Rs. 51.35 Cr




In the 113th PSOC meeting CGM (O&M) stated that the DPR for installation of reactor has been sent to NLDC for PSDF funding as per the suggestion given by ERLDC during a joint study. CPC has been requested to take necessary action for tendering the 400 kV Bus reactor to be installed at Meramundali S/S.
Deliberations in the meeting

CGM (O&M) stated that the automation of 7 nos of 220kV sub-stations needs to be incorporated for PSDF funding. A proposal in this regard is under process to be placed before BoD for approval. 

[Action: CGM (O&M)]

C.2: Status of construction of 400 kV Sterlite-Jharsuguda D/C sections

OCC advised OPTCL and Vedanta to complete the work at the earliest and no further extension will be granted for removal of LILO.
OCC advised OPTCL and Vedanta to complete the work at the earliest and no further extension will be granted for removal of LILO.
Deliberations in the meeting

Vedanta Ltd.  stated that all works have been completed. The line will be charged after getting clearance from PGCIL.
[Action: Vedanta Ltd.]

C.3: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s

PGCIL has already commissioned the 2x315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.

In 138th OCC of ERPC, SLDC to deliberate the completion schedule of inter-connecting system as follows:

	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir S/S.
	Construction of 220 kV Sadeipali-Kesinga portion has started. Expected by March’18

	b.
	LILO of one circuit of Katapalli-Sadeipalli 220 kV D/C line at Bolangir S/S.
	Charged on 04.05.16

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Line is expected by Dec’2017

Keonjhar(220/33 kV) by Dec’17

	b.
	Keonjhar (PG)-Turumunga (220/133 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	March 2018 

	b.


	LILO of one circuit of Atri-Puri (Samangara) 220 kV D/C line at Pandiabil (PG). 
	Atri – Pandibili 220 kV one ckt charged on 19.05.2017

Pandiabili – Samangara 220 kV one ckt. charged on 20.05.17


In the 113th PSOC meeting AGM (Construction) stated that 2nd ckt of 220 kV Atri-Samangara line will be made LILO at Pandiabili. CGM (Telecom) stated that tender for installation of RTU at Samangara S/S will be opened on 20.09.2017. Installation is expected to be completed by 30.09.2017.

 Deliberations in the meeting

Telecom.  stated that installation of RTU at Samangara S/S is under progress & shall be completed by 31st October 2017.
[Action: CGM (Telecom)]

C.4: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In 113th OCC, Member Secretary informed that during interaction with consultants of Grid Study Committee, NLDC agreed that they will plan for conducting workshops on crisis management plan for Cyber Security and few workshops will also be held in Eastern Region.

In the 107th PSOC meeting, CGM (IT) informed that “Crisis management plan” work is awarded to M/s Digital Age Strategies Pvt. Ltd. The said firm has completed the study of Servers and Firewalls at SLDC, Bhubaneswar and back-up SLDC at Meramundali. Presently the data centers of SLDC and GRIDCO are being audited for IT security vulnerability assessment.

In the 113th PSOC meeting, CGM (Telecom) stated that after testing of dual reporting of RTU and back up control center and compliance of audit report, Telecom will process for tendering. 

Deliberations in the meeting

It is suggested that Telecom. may forward the report to IT wing soon as the issue has been much delayed.  
[Action: CGM (Telecom)]

C.5: Certification through BIS as per IS 18001:2007 to all generating / transmission units.
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In the 110th PSOC meeting CGM (O&M) stated that BIS office at Bhubaneswar was contacted in this regard. It was decided that OPTCL shall nominate its officers to take training. After completion of training they will conduct audit and certify.
In the 111th PSOC meeting CGM (O&M) stated that 22 nos of officers are nominated from Chandaka, Mendhasal, Atri, Kesura, Bidanasi & Cuttack S/Ss to undergo training. Awareness training shall be started from 1st week of August’17. After receiving the price offer, order will be placed. 

In the 113th PSOC meeting CGM O&M stated that certification for 6 Nos of S/Ss will be done by December’2017.
Deliberations in the meeting

CGM (O&M) stated that training has been imparted to OPTCL officers.
[Action: CGM (O&M)]

C.6: Replacement of old RTU in Eastern Region for reporting of RTU / SAS to back-up control centre
The matter for replacement of old RTU in Eastern Region for reporting to back up control centre has been discussed in a special project review meeting held on 14th February 2017 at ERPC & also on 35th TCC/ERPC meeting held on 24th / 25th February 2017, It was also mentioned that there would not be any service support for the old RTUs from POWERGRID after 15 years of operation period. It was accordingly advised to ERLDC to form a committee with POWERGRID as a nodal agency for assessment of such old RTUs vis-a-vis further action plan on replacement.

It was also advised to submit a report in the next TCC/ERPC meeting.

The matter for replacement of old RTU in Eastern Region for reporting to back up control centre has been discussed again in 19th SCADA O&M meeting held at ERLDC, Kolkata on 07th April 2017, wherein nomination of nodal person name from OPTCL, WBSETCL, DVC, BSPTCL, JUSNL, POWERGRID ERTS-1, POWERGRID ERTS-2, ERLDC, MPL & Jorethang has been collected.

Nomination from NTPC all stations including Nabinagar, NHPC all stations, Dikchu, Teesta-III, Chuzachen, JITPL, GMR, Ind Bharat & APNRL are yet to be provided. ERLDC has already issued letter ref no: ERLDC / SCADA O&M / 2017/ dated 11.04.2017 for the same. It is requested to provide the nomination from these stations.
In the 113th PSOC meeting CGM (Telecom) stated that tendering for procurement of 90 Nos of RTUs (47 for replacement and 43 new) will be done.
Deliberations in the meeting

 Telecom. stated that requirement of RTUs shall be reduced in view of the proposal for automation of 24 nos of sub-stations. The revised proposal for RTU procurement will be placed in the BoD. Tendering will be done after finalization of the proposal. 
[Action: CGM (Telecom)]

C.7: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************
The DPR for ADMS has already been approved by BoD, OPTCL. SLDC shall submit the proposal for funding by PSDF for ADMS to O&M wing of OPTCL for further action.
In the 108th PSOC meeting, SLDC stated that filling of format for PSDF and floating of tender is under process. The DPR will be sent to ERPC. CGM (Telecom) stated that SLDC may contact the consultant of PSDF for filling the format. The proposal has already been sent to NLDC to include for funding through PSDF.
In the 113th PSOC meeting SLDC stated that CPC has been requested to prepare the “Expression of Interest” before processing the tender.
Deliberations in the meeting

SLDC stated that the EoI document is yet to be prepared by CPC. It is decided that SLDC may persue the matter with CPC.
[Action: SLDC]

C.8: Pollution mapping for Eastern Region
Powergrid updated the latest status as follows: 

	
	No of locations
	Installed locations
	1st set of measurements
	2nd set of measurements
	3rd set of measurements
	4th set of measurements
	5th set of measurements

	OPTCL
	164
	102
	100
	90
	79
	78
	24


Powergrid added that they prepared an online format to submit the details of measurements.

Powergrid requested to fill the Google form (https://goo.gl/6375HJ) for onward submission of measurements for better analysis of results.

Further, the schedule for measurement as informed vide letter dated 20.01.2016 & mail dated 21.01.2016 are as follows:

Measurement Schedule

	4th set
	5th set
	6th set

	21st -30th Sep 2016
	21st -31st Jan 2017
	21st -31st May 2017


OCC advised all the constituents to complete the measurements as per the schedule.

It is also requested to send the onward measurement results to following emails in addition to current email ids

1. vbhaskar@powergridindia.com

2. ritesh.kumar@powergridindia.com

In the 110th PSOC meeting, O&M stated that data for 92 locations have been collected.

O&M stated in the 111th PSOC meeting that data from 54 Nos of locations are available during the month of June’17. Due to continuous rain, further testing has been stalled as the data so obtained will not be so much useful.

In the 112th PSOC meeting O&M stated that measurement cannot be done during rainy season. 90 Nos of locations have been completed in 5th set. It was suggested that O&M may intimate to ERPC to update the database. 
In the 113th PSOC meeting O&M stated that measurement shall be done after rainy season.
Deliberations in the meeting

O&M stated that SLDC may deliberate in the OCC meeting of ERPC for up-dation of the status of completion  in the 5th set of measurements as 90 in place of 24.

[Action: SLDC]

C.9: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2017-18 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2017
	Conducted on 30th May 2017
	Last week of January 2018
	

	3
	Rengali
	2nd week of June 2017
	Conducted on 29.06.17
	Last week of November 2017
	

	4
	U. Indravati
	3rd week of June 2017
	2nd week of July-2017
	2nd week of February 2018
	

	6
	Balimela
	3rd week of October  2017
	
	1st week of March 2018
	

	9
	Burla
	Last week of June 2017
	Can be conducted after synchronization of #2
	Last week of February 2018
	


Deliberation in the meeting
It was decided to conduct the black start exercise for Balimela & UIHEP during second week of November’17 and for Burla HEP during the month of December 2017.

[Action: OHPC / SLDC]
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of Sept’17:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	20.079
	2.74

	2
	WESCO
	7
	10.738
	1.70

	3
	NESCO
	2
	11.177
	2.35

	4
	SOUTHCO
	0
	-1.711
	0.58

	
	Total
	9
	40.283
	


Deliberations in the meeting
CESU stated that they are not able to predict their day ahead drawal due to non availability of correct drawal from SCADA. SLDC state that SCADA data is an indicative of drawal, which may not match with the meter data. CESU may collect field data and compute the correction factor or other software for their demand prediction.   

[Action: CESU/SLDC]
D.2: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl. No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220/132 kV, 100 MVA, Auto- 1 at Duburi
	Main tank severely damaged
	March-2018

	2
	220/132kV, 100MVA  Auto-2  at Bhadrak
	Fire hazard on 31.05.2017
	March-2018


[Action: CGM (O&M)]
D.3: Communication issues 
Installation of communication equipment by CGPs / IPP /  Industries.
The status of data communication from CGPs as deliberated in the last meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s IFFCO, Paradeep
	Outdoor commissioning work completed. RTU was locally tested. CVT already replaced. Data will be integrated after restoration of OPGW between New Duburi & Paradeep.

	2
	M/s MSP Mettalicks
	PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited.

	3
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	4
	M/s Rohit Ferrotech
	PLCC established and inspection by Telecom Engineers completed.  Database has already been prepared by OPTCL.    

	5
	CONCAST
	No kV/Hz. (Industry is under lock up)

	6
	VISA
	CB & Status data are not available

	7
	Paradeep
	Data not available at ERLDC (Transducers need replacement)

	8
	Vedanta (400kV) 
	Frequent interruption of Line data & Generation data 

	9
	GMR
	GMR line data not available as reported by ERLDC.

	10
	Samangar & Lapanga
	No data available as reported by ERLDC

	11
	NALCO
	No data available since 14.07.17. NALCO is not responding


In the 113th PSOC meeting GCC was requested to examine for filing a case before the OERC against the CGP / Industry, those who failed to comply establishment of communication facility as the matter has been delayed considerably. 
In the 19th SCADA O&M meeting of ER held at ERLDC, Kolkata on 07th April 2017 ERLDC informed that scheduling of GMR is being done at ERLDC so data must be reported to ERLDC directly from GMR. ERLDC requested OPTCL to take up the matter with GMR so that data & voice should be available directly to ERLDC. OPTCL agreed for the same.
Deliberations in the meeting
GMR agreed to lay OPGW for data communication to ERLDC directly. GCC stated that case will be filed against the defaulting CGP / Industry within a week.
[Action: GCC / GMR / Telecom. / RT&C]
D.4: Web based drawal / generation scheduling.

In the 107th PSOC meeting, CGM (IT) informed that Generators web based scheduling work is completed except for generation of report indicating “Final Generation Schedule” for which SLDC shall furnish the requisite format.  SLDC was requested for a report to ascertain the submission of schedule by the CGPs.

In the 108th PSOC meeting, IT stated that final report generation will be completed by April’2017. Searching and Sorting of data has been done. The status to indicate whether the CGP has done scheduling or not, will be completed. SLDC may go for parallel run of the program for the month of May and June’17. From 1st July’17 the software will be made operative. SLDC may write a letter in line with the above program.
In the 111th PSOC meeting it was decided that from 1st August 2017 the schedule submitted through web portal will be considered. The web based schedule will be implemented for TTPS and Ib TPS from 1st September’2017. SLDC may intimate all the CGP and State Thermal generators accordingly. SLDC have intimated some problems in the software which need to be rectified by IT.

In the 112th PSOC meeting SLDC stated that GMR has raised certain issues regarding the provisions. IT has assured to resolve the same. It was decided that SLDC will conduct a training program for Generators before implementation of 2nd phase web based scheduling for TTPS, IBTPS & IPPs.

In the 113th PSOC meeting it was decided that SLDC shall interact with the IPPs connected to State network, IbTPS and TTPS to furnish their schedule through SLDC portal instead of mail.

At present all State thermal generating stations including IPPs & CGPs are furnishing their schedule through web portal except IbTPS. Provisions for acceptance of backing down schedule for past block are not kept in the software. IT has already been intimated about this issue.
Deliberations in the meeting

IbTPS has agreed to depute their representatives to SLDC for interaction regarding scheduling through web portal. DGM (IT) has assured to resolve the issues identified by SLDC.
[Action: SLDC / IT / OPGC]

D.5: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

The work for Automatic Meter Reading (AMR) for all the interface points is in progress. 

It was deliberated that from 1st March onwards the AMR shall be made “Go live”. Data will be available after one hour lapses of time.

In the 112th PSOC meeting DGM (IT) stated that TCS has complied with the discrepancies in August data. 679 Nos meter data have been collected during this month. Further, 750 Nos meter data will be available by next month. It was also decided that on 1st day of the month, SLDC will download the meter data and TCS will collect data on 2nd day and complete by evening of the day. On the 3rd day, SLDC and TCS will analyze the mismatch of data, if any. Further, a meeting may be convened by GRIDCO with all the DISCOMs to discuss acceptance of meter data through Text file.

In the 113th PSOC meeting IT stated that data from 690 Nos of meters have received during last month. It was decided that the data received by 2nd working day of the month shall be considered as final. It was further decided that the script shall be stopped on the 1st working day to enable for meter data collection by SLDC. 
Deliberations in the meeting

IT stated that data from 640 no of sub-stations have been received on 2nd day of October. On 4th day data from some sub-stations was received. Data from remote sub-stations could not be collected due to communication network problem. Further, he stated that data from such sub-stations has to be collected manually each month. SLDC stated that AMR data may be provided to DISCOMs for monitoring of their real time drawal may be after lapses of 15 to 30 minutes time. TCS has agreed to incorporate the billing software of secure meter. 
[Action: IT]

D.6: Software for Deviation charge billing.

Hon’ble OERC may notify “Intra State Deviation settlement and related matters” Regulation at any time. For implementation of the regulation, required software for Deviation Charge billing need to be developed and tested. CGM (IT) may take necessary steps for development of the software.

As decided a committee has been constituted for development of the software in house. The work is in progress. 

In the 113th PSOC meeting it was deliberated that development of software is in progress.

Deliberations in the meeting

IT stated that the software will be completed by end of November 2017.
D.7.DISCOM Issues

CESU

Wide mismatch between actual drawal data and drawal displayed in the SCADA. The mismatch is to the tune of -198 to +131 MW some times. Action may be taken to reduce the mismatch. 

Deliberations in the meeting

SLDC stated that CESU may develop the demand estimation logic without depending fully on SCADA data. The SCADA display data is for monitoring purpose only, which may not match exactly with the meter data. Both data may be compared to ascertain the error correction factor. CESU may instruct their representative deployed at SLDC to match the SCADA data with the field data and intimate the discrepancy, if any, to Telecom personnel at SLDC.  

[Action: CESU / SLDC / Telecom]
NESCO Utility

1. The additional 4.055 MU of Tata Steel in the revised energy bill vide lr.no. RT&C-Bill-03/2017-18- 319(5) dt. 07.10.17 of CGM (RT&C), OPTCL Bhubaneswar can’t be taken for deviation. The deviation will be 7.12 MU approximately. 
2.  Barbil, Somnathpur Grid and third power transformer of Anandapur Grid data are to be incorporated in the RVDU.

3.  Rairangpur Grid data is always suspected in RVDU.
Deliberations in the meeting

Issues raised by NESCO vide item (i) has been deliberated at Item (E) of Part-B. Telecom. has assured to check the data suspect and examine provision of data in RVDU. 
[Action: Telecom]
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by December’ 2017.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by December’2017.

	3
	Commissioning of 132 kV Baripada (PG)-Jaleswar D/C line (One ckt. made LILO at Bhograi)
	Line idle charge on 29.07.17 from Jaleswar & Bhograi end. 

	4
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	December’17

	5
	400/220 kV, 2x315 MVA Lapanga S/S
	March’18

	6
	220/33 kV, 2x20 MVA Baliguda S/S
	Mar-18

	7
	220/33 kV, 2x20 MVA Kalimela S/S
	June-18

	8
	220/33 kV, 2x20 MVA Kasipur S/S
	June-18

	9
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	Dec’17

	10
	220/33 kV, 2x20 MVA Narasinghpur S/S
	February’18

	11
	220/132 /33 kV, 2x100 MVA Aska S/S
	June’18

	12
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	Nov’17

	13
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’18

	14
	220/132/33 kV Jayapatana S/S(320 MVA)
	Jun’18

	15
	220/132 kV Pratapassan S/S(320 MVA)
	March’18

	16
	220/132 kV Kesinga S/S (320 MVA)
	March’18

	17
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	March’18

	18
	400 KV Restoration of IB - Lapanga line D/C
	September’17

	19
	132/33 kV Ghense S/S
	December’17

	20
	132/33 kV Dhenkikote S/S 
	December’17

	21
	132/33 kV Betanati S/S
	March’18

	22
	132/33 kV Kantabanji S/S
	November’17 (Line charged)

	23
	132/33 kV Podagada S/S
	November’17

	24
	132/33 kV Muniguda S/S
	November’17

	25
	132/33 kV R.Udyagiri S/S
	March’18

	26
	132/33 kV Chikiti S/S
	March’18

	27
	132/33 kV Athagarh S/S
	December’17

	28
	132/33 kV Tirtol S/S
	December’17 (Bus charged)


Deliberations in the meeting

The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. 

[Action: All Distribution Licensees]
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC

SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators, the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the last meeting, O&M stated that IB TPS has placed requisition for 6 Nos of Apex meters. SLDC stated that for replacement of all meters including generators, 10 nos of meters will be required. IBTPS may place their requisition for 10 Nos. of meters.

In the 113th PSOC meeting O&M has agreed to install 4 Nos meters as check meter in 220 kV Ib-Budhipadar line.

Deliberations in the meeting

O & M stated that the energy meters have already been released. Ib TPS may co-ordinate with Budhipadar sub-station for installation of meters.
[Action: CGM (O&M) / OPGC]

E.3: Declaration of stand-by Energy Meter 
OPTCL should declare a meter as “Standby Meter” for Generators & EHT consumers for the purpose of energy accounting in case of failure of main & check meter. As per Section 2 (v) of Central Electricity Authority (Installation and Operation of Meters) Regulations, 2006, ‘Standby Meter’ means a meter connected to CT and VT, other than those used for main meter and check meter and shall be used for accounting and billing of electricity in case of failure of both main meter and check meter. The standby meter must be an ABT compliance meter.
Further, due to frequent problems noticed in the CVTs, it is suggested to replace the CVT by IVT for metering purpose.

Deliberations in the meeting

It is suggested that OPTCL may notify the stand by meters in consultation with SLDC.
[Action: CGM (O&M) / SLDC]

E.4: Replacement of defective meters  at Renewable sources.
It is noticed that the energy meter installed at the following renewable sources are showing “power off” mostly during night time resulting non-recording of energy imported by the renewable projects.

1. Jay Iron & Steel, Bamra

2. MGM Green Energy Ltd., Chandpur

3. Molisati Vinimay Pvt. Ltd., Barkot

4. Rajratan Energy Holding Pvt. Ltd., Bolangir

5. Abacus Holdings Pvt. Ltd., Sonepur

6. Alex Green Energy Pvt. Ltd., Patnagarh
Deliberations in the meeting

GRIDCO & DISCOMs may investigate the issue.

[Action: GRIDCO / DISCOMs]

 E.5: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same. Another meeting was proposed to be convened in the month of August’17 to finalize the mechanism of data communication. In the 113th PSOC meeting, it was decided that GRIDCO will take follow up action with all the RE generators to provide real time generation data to SLDC. ERLDC has reminded again to intimate the status.   

Deliberations in the meeting
Director (Commercial) has agreed to convene a meeting soon to discuss the issue.
[Action: GRIDCO]

E.6: Major Events in the month of September’17
08.09.2017 - 132kV Jagatsinghpur-Paradeep was made LILO at Tirtol S/s bus.

16.09.2017 - 132 kV Jaynagar – Rayagada line made LILO at Podagada sub-station.
23.09.2017 - 132kV Baripada (PG) -Jaleswar direct ckt. charged from Baripada (PG)  end.

25.09.2017 – 132kV Baripada (PG)  –Bhograi ckt. charged from Baripada (PG) end. 

E.7: Non-compliance of SLDC’s direction by OHPC stations
It is noticed that OHPC stations are availing shutdown of their units without concurrence of SLDC which hampers the real time operation of SLDC.

Deliberations in the meeting
OHPC was advised to take prior permission of SLDC for availing shutdown of their units.

 [Action: OHPC]

E.8: Short Term Load Forecasting (STLF)  by Distribution Utilities using the Weather  Forecast Portal
As per the discussion in the FOLD meeting on 12.06.17, weather forecast portal has been provided in the ERLDC as well as SLDC website. The Distribution Utilities may use the said portal for estimation of their drawal more accurately.

Subsequently, in the meeting held on 10.08.2017 at ERLDC, Kolkata, the detailed procedure was discussed. ERLDC has developed A Software for STLF at Regional level and constituent level as well. The said software can also be utilized by the Discoms with suitable modifications. The Discoms are requested to nominate their officers for attending the training programe at ERLDC to get acquainted with the software for use at their end.   

In the 113th PSOC, it was decided that SLDC will use the software for demand estimation and check the accuracy of the estimated demand with the actual and a training program may be conducted for DISCOMs. After satisfactory operation, a training program may be conducted for DISCOMs.

Deliberations in the meeting
As decided earlier SLDC shall use the demand estimation software and subsequently arrange a training programme for Discoms.

[Action: SLDC]

E.9: Important Grid Incidences during the month of September’17.
There was no reportable grid incidence in the month of September-17.
E.10: Outage of major transmission Elements during the month of September’17. (above 10 hrs).
Deliberations in the meeting
Outage of major transmission elements above 10 hours during the month was reviewed. Most of the outages are due to jumper / conductor snapping.

[Action: C.G.M. (O&M)]

E.11:  Review of Outage Program of State Generators / Transmission elements for the month of Nov’17:
Tentative Outage programme for State Generators for the month of Nov’2017 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 5

# 6
	25.10.16 to continue

16.10.15 to continue
	Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to continue
	Under R,M & U

	3
	Balimela
	# 1
# 2
	05.08.16 to continue
01.11.17 to continue
	Under R,M & U
Programming for R&M

	4
	Rengali
	# 1

# 5
	25.08.17 to 10.11.17

21.03.17 to continue
	Starter problem

Hoist gate problem

	5
	Upper Kolab
	# 2

# 4
	28.05.17 to continue
01.11.17 to 30.04.18
	MIV Problem

Programming for Capital maintenance

	6
	Upper Indravati
	# 1
	01.11.17 to 30.11.17
	Annual Maintenance

	7
	IbTPS
	# 1
	01.11.17 to 20.11.17
	Boiler License renewal & AM


Deliberations in the meeting
SLDC stated that shutdown of IbTPS unit #1 may be deferred to 10.11.2017 i.e. after synchronization of TTPS # 5.
[Action: OPGC / OHPC / SLDC]

E.12: Generation Program for the month of November’17.
Generation schedule for the month of November’17 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.10.16
	Reservoir Level as on 01.10.17
	MDDL
	High Flood    Reservoir Level

	
	Nov’17

(1st fortnight)
	Nov’17

(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	30
	30
	629.95 ft 
	 630.15 ft
	590 ft.
	630 ft.

	HPS-II, Chiplima
	20
	20
	-
	-
	-
	-

	Balimela
	90
	90
	1505.40 ft 
	1479.70 ft
	1440 ft.
	1516 ft.

	Rengali
	40
	40
	122.58 mt

1.78mt mtr mt
	122.97 mt mt
	109.72mtr 
	123.5 mtr.

	U.Kolab
	60
	60
	856.31 mt mt
	852.63 mt
	844 mtr 
	858 mtr.

	U. Indravati
	210
	210
	639.11 mt
	636.02 mt mt
	625mtr 
	642 mtr

	MKD (O/D)
	40
	40
	2746.80 ft 
	2745.00 ft
	2685 ft.
	2750 ft.

	TOTAL
	490
	490
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

E.13: Anticipated power generation and demand for the month of November’2017.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	900
	1100

	2
	WESCO
	800
	1000

	3
	NESCO
	650
	850

	4
	SOUTHCO
	400
	500

	6
	Total Discom
	2750
	3450

	
	System Loss & others
	190
	200

	
	Total Demand
	2940
	3650

	Availability
	
	

	1
	Hydro
	490
	1200

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	400
	400

	4
	ISGS share (including OA)
	1100
	1100

	5
	CGP support (OA)
	200
	200

	6
	Total availability
	2940
	3650

	7
	Surplus / Deficit
	0
	0


PART F: OTHER ISSUES

F.1: Agenda by SOUTHCO
Since, energy meter has been installed on the LT side of Station transformers of OPTCL grid substations, the transformer loss need to be considered while computing net energy drawal by Discoms. 
Deliberations in the meeting
It was decided that DISCOMs may take up the matter with GRIDCO in a separate meeting.
[Action: GRIDCO / DISCOMS]  

F.2: Removal of old energy meters from OHPC stations - Agenda by OHPC
OHPC suggested for removal of all the old meters from their panel as apex meters have already been installed for recording of energy to reduce the burden of CT.
Deliberations in the meeting
It was decided that OPTCL may take action for removal of old meters.
[Action: C.G.M. (O&M)]

F.3: Shutdown of Unit-1 of power plant - Agenda by RSP
RSP stated that # 1 of their power plant will remain out of service for 40 days with effect from 25.11.2017. WESCO has already given their consent. During this period, RSP shall draw power up to their contract demand.

Deliberations in the meeting
SLDC stated that RSP should cooperate SLDC in contingency condition to which RSP has agreed.
[Action: RSP / SLDC]

F.4: Evacuation of power - Agenda by BPPL
As per advise of Bidanasi Grid substation, most of the days, Chandaka-BPPL 132 kv circuit remains on idle charge condition from Chandaka end and line breaker at BPPL end kept on open condition as a result, BPPL power station gets only one path (BPPL-Bidanasi) to evacuate and in case, above path gets disturbed, BPPL’s Power Station remains in islanding position which leads to   lots of financial loss.

 Hence it is requested to consider the above and ensure the LILO connectivity may be kept intact at BPPL LILO sub-station, in order to maintain uninterrupted power evacuation.

Deliberations in the meeting
O&M stated that BPPL may go for a fresh system study to ascertain the line loading.
[Action: BPPL]

F.5:  Date and Venue of the next (115th) PSOC meeting.
It was proposed by the members that RSP may organize the 115th PSOC meeting at Rourkela on 24.11.2017. SLDC shall write a letter to RSP for their consent & confirmation.

ANNEXURE

[image: image2.png]114th Power System Operational Co-ordination Committee Meeting
[ At 11:00 A.M. on 27.10.2017]
[At PTC, Chandaka]

fllc;. 44(’“‘ Name Designation | Organisation Mobile No. E-mail Address Signature
VP 5. Cakw |SramE9] S0 | qursactrrs [eke paabiaapted Bako

2| UM Midhes |CamBlac| croc | 94299 999y S+ W@ gr5elcer o in D —

S MK Do | Divleom)| Grunco | THO bOTUZ3F |dliv.com egeidenty  MeDr—
R fhnda D?y((’w)(c{sj OPTLL |09428907 97T _|din progett @ mM-b.i;‘;%ﬂp
510K SamaQ  |Divp) | ofel - |9438509236 |dur opestint @ prLg @z/
8 | BP Mishrov Cam(RIe) OPTCL | 9438907019 | ele-brmishad | @

7| B-K. gk Chn(oar)|  opTCL | 9488907919 |cgmonapoflel b)Y ha

s N R Bicud [NGHEw L 0IT ) Torsu0ass npsdilene, | R |
o [ 8.0 Pndy |Vt wD|UKIEP | assgnysig frekvdgeotpt | = |
0lea Bh"’y Unet Peogl U1 EL YQM&ngﬁwwa@m;m Js|
11 b}\aw%%%' ”\B':?r/ (c;g?C F32aglio0r0 M%a%cm WA

7 P&%>k/wﬂw DAY bP6c  [132871S50] gwp{f@}g.w,%ﬂ kv‘aﬂ/‘ﬁ‘@f)ﬂ'
5| Ok MigHRA D mler) N;ng q42€2 312207 fw{ﬁﬁhﬁf{@;n Q&}\}g/’-
1| Skmsvvar |fou(o=) Bpp | 82803 YY) Skmattns€ bheb | e
15 [Remeth fe o Dagn [ el [17202600 71 WS Etnal. §2 0
6| b K Baol | Ae(T)] ortec o yssgoryrs [7L,a59°%2 ), | Qlpet
MK Rnda MM Jrbedy atmdepas RO | 5 )

s R K Shak |DaM | RSP |seossolifs SRIAENE ;| G-
9 h W gehow  Mpvorgy) NEsco (45890400 | M swatdim, (& B
0|20 Sl | GH. | VeI 243890600 | —— W

2 | S v Caoe onapt | WE Sco "143705-7205/:;“:;‘_*&%‘ 2(
2§ ") chaahy B Sowhew |IUDFYS Qbed | Smyedmeboty € oy ng‘
3P L Grauda AFM PP | quasq0idyo [l PR &R @3’//
2 k,,’,/?"/.tcm%fiy Dom |op7e 1 (94357050 33|l btrachary | gd e
5| 0 oR Mighon [ ) | epred |AU2R907 o | HESENER] O,
| crladeha LGty Lo [Tnseogso PRAugletgne | Gonn
S e G DS R S T P 4_2%
28 Pgﬁﬁgffﬁbﬁ% Qrl | s C | 9429907220 eleé ]’cfm%“z:,“ﬁ‘ g‘;::\’w\%





                   [image: image3.png]P | Sodenand Reda| Gm [(R709 o] 993890209 |l AR opreL ng
30 | petete RumarRebun| G M Slbe | Y9040, m.m@mcm-hw Reln,
3| Compundy Lolp| —ho— | —cho— | 9429907902 ue'u%f;ﬁfé;‘?m 44
321 Dopmbsc b | um s QY392 5P | beoh@ cosceoripa am ‘MU

] - T
P Pk jedhy | G | gce | a(3867sey| obbl ceserery /
w| ¢ phock | g5n | Scc |9 38550 \geccapera Y

=

35| Ok Behove (7)) | ppre L | 4438907251 |t -sxbeheva@eparc| Dum
6| S Migk= | DM 7| v A% |4l Scar sk G\
S S Y 6/7 ef | wcpyozr C hm ooy N\\\w
s & -Qﬁwij- %mait ﬁf,ﬂp_ 423503 6] Spin-gpet 4 e %;//7
I Ty gy Ee. Seubivn | aGpC P1296 | altSodhe p Guuny 53 d\\m
01 ¢k DASH SLD¢ QU 37 B0R6 [ | 2 grbiason® s impos, DY~
Al p oK Mz‘s)qrw\ CuM Stoe 9Y 58904409 | e phrishn@siden, oL &{\\/
21 p Kk DAS DM Sepe qY48907 Y0 8 | pe-prsnis psidcarsen Q,
9| safaselly | py | dwe | gysgqoq948 | - S
#| Sk 5. Ahemed | MaPT | GREL | TRPHHO82 [k Mnmalegrmpagil Csd=




    
