[image: image1.png]STATE LOAD DESPATCH CENTRE
OFFICE OF THE CHIEF LOAD DESPATCHER

ODISHA POWER TRANSMISSION CORPORATION LIMITED
=« GRIDCO Colony, P.O.- Mancheswar Rly. Colony, Bhubaneswar-17, FAX-0674- 2748509

#)ZORZU()JSG('UO?’SF&

it CIN - U40,
AL
No-SGM (PS)-PL-152016/ L 2346

Dated: ]J.12.2017

From:

The Chief Load Despatcher
SLDC, OPTCL, Bhubaneswar-17.

To:
As per distribution list

Sub: Minutes of 115" PSOC meeting held on 24.11.2017 at CPTI, RSP, Rourkela

Sir,
Please find enclosed herewith the minutes of 115" Power System Operational Co-

ordination meeting held on 24.11.2017 at CPTI, RSP, Rourkela.

This is for your information & necessary action.

Yours faithfully;

Encl: As above

Chief Load Despatcher,
SLDC, OPTCL

Copy along with enclosures forwarded to the Executive Assistant to CMD, Gridco / OPTCL
for kind information of CMD.




Distribution list

1. The Director (Commercial), Gridco, Bhubaneswar

2. The Director (Operation), OPTCL, Bhubaneswar

3. The Director (Projects), OPTCL, Bhubaneswar

4. The Director (Operation), OHPC, Bhubaneswar

5. The CGM (O&M), OPTCL, Bhubaneswar.

6. The CGM (Const.), OPTCL Bhubaneswar.

7. The CGM (RT&C), OPTCL, Bhubaneswar.

8. The CGM (PP), GRIDCO, Bhubaneswar.

9. The CGM (IT), OPTCL, Bhubaneswar.

10. The CGM (Telecom), OPTCL, Bhubaneswar.

11. The Sr. G.M (Const)-I, OPTCL, Bhubaneswar.

12. The Sr. G.M (Const)-II, OPTCL, Sambalpur.

13. The Sr. G.M (CPC), OPTCL, Bhubaneswar.

14. The Sr. G.M (CP), OPTCL, Bhubaneswar.

15. The Sr. G.M. (O&M), Zone-I, Narendrapur 

16. The Sr. G.M.(O&M), Zone-II, Meramundali.

17. The CEO, CESU, Bhubaneswar.

18. The A.O., WESCO, Burla

19. The A.O., NESCO, Balasore

20. The A.O., SOUTHCO, Berhampur.

21. The Member Secretary (GCC), OPTCL.

22. The ED, Power Grid Corporation of India, Bhubaneswar.

23. The Sr. G.M. (El.), BHEP, Balimela

24. The A.G.M. (El.), CHEP, Chiplima

25. The Sr. G.M. (El.), UIHEP, Mukhiguda

26. The Sr. G.M. (El.), RHEP, Rengali

27. The D.G.M. (El.), HHEP, Burla

28. The D.G.M. (El.), UKHEP, Bariniput, Koraput

29. The S.E. (O&M), Machhakund

30. The DGM (Elect.), IbTPS, OPGC, Banharpali.

31. The Vice President (O), IMFA, Choudwar.

32. The D.G.M. (O&M), NTPC (TTPS), Talcher.

33. The AGM (Elect.), JINDAL Stainless Ltd., Duburi

34. The G.M, HINDALCO, Hirakud.

35. The G.M.CPP, NALCO, Angul.

36. The Director, M/s. Jindal Steel & Power Ltd., Angul

37. The AVP-Vedanta Ltd (IPP), Jharsuguda

38. The G.M, Vedanta Ltd (CGP), Jharsuguda.

39. The DGM (Power Distribution), RSP, Rourkela.

40. Joint President, Aditya Aluminium Ltd., Lapanga, Sambalpur

41. The G.M. (Elect.),  Bhusan Steel Limited. Meramundali

42. The G.M. (Elect.), Bhusan Power & Steel Ltd, Budhipadar.
43. The G.M. (Elect.), IFFCO Limited.

44. Director & COO, GMR Kamalanga Energy Limited, Satyanagar, Bhubaneswar.

45. The CEO, Bhubaneswar Power Pvt. Ltd, IRC Village, Nayapalli, Bhubaneswar.

46. M/S Tata Power & Steel Ltd., Kalinganagar

Odisha Power Transmission Corporation Ltd. Bhubaneswar.


Minutes of 115th PSOC meeting held on 24.11.2017 at CPTI, RSP, RKL
List of participants is at Annexure.

G.M (Electrical), RSP welcomed all the members of PSOC. CGM, SLDC welcomed all the members to the 115th PSOC meeting organized by RSP, at CPTI, Rourkela. In his welcome address, he highlighted the system performance for the month of October’2017 and overall power scenario of the State. He also emphasized on the power drawal, made by all the Discoms during the month. 
D.G.M. (SS), SLDC took the agenda items for discussion. 

The review proceeded as follows: 
1: Confirmation of minutes of 114th PSOC meeting held on 27.10.2017
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2016/3785(46) dated 03.11.2017 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting:
The minutes of 114th PSOC meeting was confirmed. 
PART B : SYSTEM PERFORMANCE
B1: Review of Grid Performance for the month of October’2017.
(A)  Frequency 

It was noticed that, during the month of October’17, 76.19 % of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 77.41 % during the month of  September’17. The maximum and minimum System frequency during the month was 50.10 Hz & 49.76 Hz respectively.

 (B)  Grid demand 

Grid demand for the month of  October’17 was reviewed. The average consumption during the month was 3569 MW. The maximum System demand of 4491 MW occurred on 23.10.17at 20:00 Hrs and minimum demand of 2763 MW occurred on 20.10.17 at 06:00 Hrs. 
Deliberation in the meeting

It is observed that the average demand during the month of  October’ 17 has been increased by 2 MW while the peak demand  was increased by 116 MW from that of September’17. The average demand during the month has been increased by 543 MW in comparison to October’16. Besides normal load growth, import of power by M/s Vedanta Ltd. through Open Access transaction is reason for increase of average demand.
 (C)  Voltage Profile of important Sub Stations in OPTCL System during the month of Oct’17.

The Voltage profile at different 220 kV buses in OPTCL system during the month of Oct’17 was reviewed. 
The maximum Voltage of 240 kV occurred at Jayanagar & Joda 220 kV bus. Narendrapur 220 kV bus has experienced the minimum Voltage of 211.88 kV. Bus Voltages at Samgara, Lapanga and Cuttack could not be incorporated due to non availability of energy meter in those S/Ss. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Meramundali bus during the month of October 2017 in 15 minute block was reviewed.
Deliberation in the meeting:
The overall Voltage profile of 220 kV buses is satisfactory. 





.

 [Action: CGM (O&M) / SLDC]
(D) Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of October’17.

Auto loading of all 220 kV S/Ss was reviewed. It was noticed that some of the Autos have not been provided with energy meter. 
Deliberation in the meeting:
It was deliberated by OPTCL that commissioning of meters for all the remaining Auto is under process. 









        
        [Action: CGM (O&M)]

(E) DISCOM Drawal during the month of October’17 
The schedule and actual energy drawal by Discoms for the month of October’17 was reviewed. 
Deliberation in the meeting:
It was noticed that NESCO had overdrawn 23.529 MU, CESU  had overdrawn 8.495 MU & SOUTHCO had overdrawn 2.184 MU while WESCO had under drawn 5.001 MU during the month. 
 [Action: All Distribution Utilities / SLDC]
(F) Energy Generation / import during the month of October’17 
Energy generation and exchange during the month of  October’17 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2655.60 MU. 
Deliberations in the meeting
The energy demand has been increased due to import of power by M/S Vedanta Ltd. through Open Access transaction.CGM (PP), Gridco stated that due to non-injection of State’s share by the IPPs, the demand is being met by procuring costly URS power and sometimes by overdrawing from the Grid. All IPPs are advised to inject the State share of power. 
 (G) Drawal of Machhakund Power during the month of October’17
The drawal of Machhakund power during the month of October’17 was 16.510 MU, against AP drawal of 16.164 MU. 
Deliberations in the meeting

O&M stated that Machhakund drawal shall be increased after commissioning of Podagada S/S by 15th December. 
On commissioning of a new S/S, 33 kV feeder loads are to be shifted to these S/Ss. It is noticed that the Discoms are dismantling the old lines. All Discoms were advised not to dismantle those lines so that flexibility of power supply will be maintained in contingency conditions.  

[Action: SLDC / CGM (Telecom)]
(H) Under Frequency relay operation in OPTCL System during the month of October’17.

There is no UF Relay operation during the month of October’17 as the frequency had never gone beyond 48.50 Hz. 
(I) Status of Open Access applications during the month of October’2017
Status of Open Access Applications received and disposed by SLDC during the month was reviewed.

Deliberations in the meeting
Total 164 numbers of Short Term / Medium term and Collective transaction applications have been processed by SLDC for according Approval / Consent / NoC during the month. 
PART C – Issues likely to be discussed in the 139th OCC meeting of ERPC on 27.11.2017
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting held on 29.04.16 at New Delhi, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format. 
The latest status as updated by OPTCL is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	Amount

Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	3
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	10.05.15
	10.05.17
	162.5 Cr.


	25.16 Cr.
	Total contract awarded for

Rs. 51.35 Cr




In the 113th PSOC meeting CGM (O&M) stated that that the DPR for installation of reactor has been sent to NLDC for PSDF funding as per the suggestion given by ERLDC during a joint study. CPC has been requested to take necessary action for tendering the 400 kV Bus reactor to be installed at Meramundali S/S.
In the 114th PSOC meeting CGM (O&M) stated that the automation of 7 nos of 220kV sub-stations needs to be incorporated for PSDF funding. A proposal in this regard is under process to be placed before BoD for approval. 

Deliberations in the meeting
GM (O&M) stated that the approved amount has been scaled down. The actual amount will be intimated to ERPC. Further, proposal for installation of 400 kV reactors at Meramundali S/S has been discussed and finalized in the meeting conducted by NLDC. After approval by the Appraisal committee, the same will be included for funding through PSDF. 
[Action: CGM (O&M)] 
C.2: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.

In 138th OCC of ERPC, SLDC to deliberate the completion schedule of inter-connecting system as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by June’18. 220 kV Sadeipali-Bolangir(PG) portion of the line is expected by Feb’18. 

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Line is expected by Dec’2017

Keonjhar S/S(220/33 kV) by February’18.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	March 2018 

	b.


	LILO of one circuit of Atri-Puri (Samangara) 220 kV D/C line at Pandiabil (PG). 
	Atri – Pandibili 220 kV one ckt charged on 19.05.17

Pandiabili – Samangara 220 kV one ckt. charged on 20.05.17. LILO of 2nd ckt is ready and will be charged after getting approval from ERLDC. 


In the 113th PSOC meeting AGM (Construction) stated that 2nd ckt of 220 kV Atri-Samangara line will be made LILO at Pandiabili. CGM (Telecom) stated that tender for installation of RTU at Samangara S/S will be opened on 20.09.2017. Installation is expected to be completed by 30.09.2017.

In the 114th PSOC meeting Telecom stated that installation of RTU at Samangara S/S is under progress & shall be completed by 31st October 2017.

Deliberations in the meeting
CGM (Const) stated that NESCO may initiate for 33 kV connectivity with 220/33 kV S/S Keonjhar S/S on priority basis to draw power. CGM (Telecom) intimated that RTU at Samangara sub-station has already been installed.
[Action: CGM (Const) / NESCO]
C.3: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In the 107th PSOC meeting, CGM (IT) informed that “Crisis management plan” work is awarded to M/s Digital Age Strategies Pvt. Ltd. The said firm has completed the study of Servers and Firewalls at SLDC, Bhubaneswar and back-up SLDC at Meramundali. Presently the data centers of SLDC and GRIDCO are being audited for IT security vulnerability assessment.

SLDC is requested to nominate one officer for attending the Cyber Security training to be held at Bengaluru during 11th to 15th April’2017. Nominations from GRIDCO and OPTCL have since been received. Top management awareness-cum Seminar on the subject shall be organized subsequently.

In the 110th PSOC meeting, IT stated that the meeting was held on 23.06.2017. SLDC shall comply with the action to be taken relating to SCADA.

In the 111th PSOC meeting DGM (Telecom) stated that the compliance of action to be taken on SCADA related issues is under process.
In the 113th PSOC meeting CGM (Telecom) stated that after testing of dual reporting of RTU and back up control center and compliance of audit report, Telecom will process for tendering. 

In the 114th PSOC meeting it is suggested that Telecom. may forward the report to IT wing soon as the issue has been much delayed.  
Deliberations in the meeting

IT stated that the report has been furnished by Telecom. Tendering for ‘Auditor certification’ has been finalized. Work order will be placed soon.
[Action: CGM (IT) / Telecom]
C.4: Certification through BIS as per IS 18001:2007 to all generating / transmission units.
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In the 110th PSOC meeting CGM (O&M) stated that BIS office at Bhubaneswar was contacted in this regard. It was decided that OPTCL shall nominate its officers to take training. After completion of training they will conduct audit and certify.
In the 111th PSOC meeting CGM (O&M) stated that 22 nos of officers are nominated from Chandaka, Mendhasal, Atri, Kesura, Bidanasi & Cuttack S/Ss to undergo training. Awareness training shall be started from 1st week of August’17. After receiving the price offer, order will be placed. 

In the 113th PSOC meeting CGM (O&M) stated that certification for 6 Nos of S/Ss will be done by December’2017.
In the 114th PSOC meeting CGM (O&M) stated that training has already been imparted to OPTCL officers.

Deliberations in the meeting
GM (O&M) stated that 2nd phase training has been completed. Modality for 6 Nos of S/Ss will be prepared by December’2017.
[Action: CGM (O&M)]
C.5: Replacement of old RTU in Eastern Region for reporting of RTU / SAS to back-up control centre
The matter for replacement of old RTU in Eastern Region for reporting to back up control centre has been discussed in a special project review meeting held on 14th February 2017 at ERPC & also on 35th TCC/ERPC meeting held on 24th / 25th February 2017, It was also mentioned that there would not be any service support for the old RTUs from POWERGRID after 15 years of operation period. It was accordingly advised to ERLDC to form a committee with POWERGRID as a nodal agency for assessment of such old RTUs vis-a-vis further action plan on replacement.

It was also advised to submit a report in the next TCC/ERPC meeting.

The matter for replacement of old RTU in Eastern Region for reporting to back up control centre has been discussed again in 19th SCADA O&M meeting held at ERLDC, Kolkata on 07th April 2017, wherein nomination of nodal person name from OPTCL, WBSETCL, DVC, BSPTCL, JUSNL, POWERGRID ERTS-1, POWERGRID ERTS-2, ERLDC, MPL & Jorethang has been collected.

Nomination from NTPC all stations including Nabinagar, NHPC all stations, Dikchu, Teesta-III, Chuzachen, JITPL, GMR, Ind Bharat & APNRL are yet to be provided. ERLDC has already issued letter ref no: ERLDC / SCADA O&M / 2017/ dated 11.04.2017 for the same. It is requested to provide the nomination from these stations.
In the 112th PSOC meeting CGM (Telecom) stated that RTU specification has been finalized on 7th August’17. Tendering will be done after approval of CMD, OPTCL.

In the 114th PSOC meeting Telecom. stated that requirement of RTUs shall be reduced in view of the proposal for automation of 24 nos of sub-stations. The revised proposal for RTU procurement will be placed in the BoD. Tendering will be done after finalization of the proposal. 

Deliberations in the meeting

Replacement of 51 Nos of old RTU and 27 Nos of new RTU proposal has been placed in the BoD. After receiving approval, order will be placed.
[Action: CGM (Telecom)]
C.6: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************
The DPR for ADMS has already been approved by BoD, OPTCL. SLDC shall submit the proposal for funding by PSDF for ADMS to O&M wing of OPTCL for further action.
In the 108th PSOC meeting, SLDC stated that filling of format for PSDF and floating of tender is under process. The DPR will be sent to ERPC. CGM (Telecom) stated that SLDC may contact the consultant of PSDF for filling the format. The proposal has already been sent to NLDC to include for funding through PSDF.
In the 113th PSOC meeting SLDC stated that CPC has been requested to prepare the “Expression of Interest” before processing the tender.
In the 114th PSOC meeting SLDC stated that the EoI document is yet to be prepared by CPC. It is decided that SLDC may persue the matter with CPC.

Deliberations in the meeting
SLDC stated that EoI document is being prepared by CPC. GM (O&M) stated that the item has not been listed in PSDF. SLDC may investigate and resend the proposal.
[Action: SLDC]
C.7: Pollution mapping for Eastern Region
Powergrid updated the latest status as follows: 

	
	No of locations
	Installed locations
	1st set of measurements
	2nd set of measurements
	3rd set of measurements
	4th set of measurements
	5th set of measurements

	OPTCL
	164
	102
	100
	90
	79
	78
	24


Powergrid added that they prepared an online format to submit the details of measurements.

Powergrid requested to fill the Google form (https://goo.gl/6375HJ) for onward submission of measurements for better analysis of results.

Further, the schedule for measurement as informed vide letter dated 20.01.2016 & mail dated 21.01.2016 are as follows:

Measurement Schedule

	4th set
	5th set
	6th set

	21st -30th Sep 2016
	21st -31st Jan 2017
	21st -31st May 2017


OCC advised all the constituents to complete the measurements as per the schedule.

It is also requested to send the onward measurement results to following emails in addition to current email ids

1. vbhaskar@powergridindia.com

2. ritesh.kumar@powergridindia.com

In the 114th PSOC meeting O&M stated that measurement shall be done after rainy season.
O&M stated that SLDC may deliberate in the OCC meeting of ERPC for up-dating the status of completion in the 5th set of measurements as 90 in place of 24.

Deliberations in the meeting

GM (O&M) stated that 54 Nos measurement has been done in 6th set. 

[Action: CGM (O&M)]
C.8: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2017-18 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2017
	Conducted on 30th May 2017
	Last week of January 2018
	

	3
	Rengali
	2nd week of June 2017
	Conducted on 29.06.17
	Last week of November 2017
	

	4
	U. Indravati
	3rd week of June 2017
	2nd week of July-2017
	2nd week of February 2018
	

	6
	Balimela
	3rd week of October  2017
	
	1st week of March 2018
	

	9
	Burla
	Last week of June 2017
	Can be conducted after synchronization of #2
	Last week of February 2018
	


In the 114th PSOC meeting it was decided to conduct the black start exercise for Balimela & UIHEP during second week of November’17 and for Burla HEP during the month of December 2017.

Deliberations in the meeting

SLDC stated that mock black start for Rengali HEP will be done by 30th November’2017.

[Action: OHPC / SLDC]
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of Oct’17:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	8.495
	1.156

	2
	WESCO
	2
	-5.001
	0.782

	3
	NESCO
	0
	23.529
	5.133

	4
	SOUTHCO
	0
	2.184
	0.752

	
	Total
	2
	29.207
	


It is noticed that NESCO & CESU had overdrawn during the month.
Deliberations in the meeting

NESCO stated that the data for 3rd Auto at Balasore and power drawal from Baripada (PG) through the newly charged 132 kV Baripada (PG) –Jaleswar line was not incorporated in their drawal display, basing on which they have forecasted day-ahead drawal schedule during the month. SLDC suggested to the Discoms to develop their database and methodology for day-ahead demand estimation without depending fully on SCADA display.
[Action: All Discoms]
D.2: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl. No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220/132 kV, 100 MVA, Auto- 1 at Duburi
	Main tank severely damaged
	March-2018

	2
	220/132kV, 100MVA  Auto-2  at Bhadrak
	Fire hazard on 31.05.2017
	March-2018


[Action: CGM (O&M)]
D.3: Communication issues 
The status of data communication from CGPs as updated by Telecom is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s IFFCO, Paradeep
	Outdoor commissioning work completed. RTU was locally tested. CVT already replaced. Data will be integrated after restoration of OPGW between New Duburi & Paradeep.

	2
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	3
	M/s Rohit Ferrotech
	PLCC established and inspection by Telecom Engineers completed.  Database has already been prepared by OPTCL.    

	4
	VISA
	CB & Status data are not available

	5
	Paradeep
	Duburi-Paradeep Line shut down required for drawing OPGW. After which data can be displayed. Dec’2017

	6
	GMR
	GMR on line data is available at SLDC but not available directly to ERLDC. GMR agreed to lay OPGW for data communication to ERLDC

	7
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 113th PSOC meeting GCC was requested to examine for filing a case before the OERC against the CGP / Industry, those who failed to comply establishment of communication facility as the matter has been delayed considerably. 
In the 19th SCADA O&M meeting of ER held at ERLDC, Kolkata on 07th April 2017 ERLDC informed that scheduling of GMR is being done at ERLDC so data must be reported to ERLDC directly from GMR. ERLDC requested OPTCL to take up the matter with GMR so that data & voice should be available directly to ERLDC. OPTCL agreed for the same.
In the 114th PSOC meeting GMR agreed to lay OPGW for data communication to ERLDC directly. GCC stated that case will be filed against the defaulting CGP / Industry within a week.

GCC has requested CGM (Telecom) to furnish the updated status of the defaulting CGP / Industry to file a case before OERC.
Deliberations in the meeting
GCC will file a case before the OERC soon.
[Action: CGM (Telecom) / GCC / RT&C]
D.4: Web based drawal / generation scheduling.

In the 111th PSOC meeting it was decided that from 1st August 2017 the schedule submitted through web portal will be considered. The web based schedule will be implemented for TTPS and Ib TPS from 1st September’2017. 
At present all State thermal generating stations including IPPs & CGPs are furnishing their schedule through web portal except IbTPS. Provisions for acceptance of backing down schedule for past block are not kept in the software. IT has already been intimated about this issue. Provision for automatic extraction of Power Exchange schedule for incorporation in the schedule of respective Generator / CGP may be kept in the software.
In the 114th PSOC meeting IbTPS has agreed to depute their representatives to SLDC for interaction regarding scheduling through web portal. DGM (IT) has assured to resolve the issues identified by SLDC.
Deliberations in the meeting
OPGC stated that IbTPS has started scheduling through web portal. IT may explore to resolve the problems identified by SLDC.
[Action: SLDC / IT]
D.5: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

The work for Automatic Meter Reading (AMR) for all the interface points is in progress. 

It was deliberated that from 1st March onwards the AMR shall be made “Go live”. Data will be available after one hour lapses of time.

In the 112th PSOC meeting DGM (IT) stated that TCS has complied with the discrepancies in August data. 679 Nos meter data have been collected during this month. Further, 750 Nos meter data will be available by next month. It was also decided that on 1st day of the month, SLDC will download the meter data and TCS will collect data on 2nd day and complete by evening of the day. On the 3rd day, SLDC and TCS will analyze the mismatch of data, if any. Further, a meeting may be convened by GRIDCO with all the DISCOMs to discuss acceptance of meter data through Text file.
In the 113th PSOC meeting IT stated that data from 690 Nos of meters have received during last month. It was decided that the data received by 2nd working day of the month shall be considered as final. It was further decided that the script shall be stopped on the 1st working day to enable for meter data collection by SLDC. 
In the 114th PSOC meeting IT stated that data from 640 no of sub-stations have been received on 2nd day of October. On 4th day data from some sub-stations was received. Data from remote sub-stations could not be collected due to communication network problem. Further, he stated that data from such sub-stations has to be collected manually each month. TCS has agreed to incorporate the billing software of secure meter. SLDC suggested to provide the AMR data to DISCOMs for monitoring of their real time drawal may be after lapses of 15 to 30 minutes time.
Deliberations in the meeting

DGM (IT) stated the status of AMR as follows

Total Nos of meters:

840 Nos

Data collected for October:
756 Nos

Out of 756 Nos meter data collected, 64 Nos meter data could not be collected during shutdown period. The logic for data collection during the shutdown period needs to be developed.

Regarding providing the real time data to Discoms, it was deliberated that out of 840 Nos of meters, 640 Nos are APEX-200 and remaining 200 Nos are of APEX-100. The baud rate of above two types of meters is different. Data can be provided to the Discoms, when all APEX- 200 type meters are replaced by APEX -100. 

 [Action: O&M/ IT/SLDC/GRIDCO]
D.6: Software for Deviation charge billing.

Hon’ble OERC may notify “Intra State Deviation settlement and related matters” Regulation at any time. For implementation of the regulation, required software for Deviation Charge billing need to be developed and tested. CGM (IT) may take necessary steps for development of the software.

As decided a committee has been constituted for development of the software in house. The work is in progress. 

In the 114th PSOC meeting, IT stated that the software will be completed by end of Nov’ 2017.

Deliberations in the meeting

IT stated that the software is expected to be completed by end of December’2017

[Action: CGM (IT) / SLDC]
D.7.DISCOM Issues

CESU

1. Wide mismatch of drawal display through SCADA with actual meter data to the tune of 259MW on one side and 71MW on the other side. 
2. Necessary action may please be taken to reduce the gap between SLDC dash board drawal data and actual (dump) drawal data of CESU on every 15minute block basis to enable CESU to give more accurate day ahead schedule forecast.
NESCO Utility

It is ascertained from the meter data for the month of October’17 that there is a wide variation between RVDU drawal data and actual drawal data. The drawal in RVDU is showing less in comparison to actual drawal resulting more deviation. NESCO is unable to calculate the actual deviation due to abnormal low recording in the RVDU. Therefore, NESCO requests to waive out the deviation for the month of October’17. The detail calculation sheet of Schedule Vs RVDU Drawal Vs Actual Drawal is enclosed for your kind ready reference.

Deliberations in the meeting
SLDC stated that the Discoms may develop the demand estimation logic without depending fully on SCADA data. The SCADA display data is for monitoring purpose only, which may not match exactly with the meter data. Both data may be compared to ascertain the error correction factor. They may instruct their representative deployed at SLDC to match the SCADA data with the field data and intimate the discrepancy, if any, to Telecom personnel at SLDC.  

[Action: CESU / NESCO]
WESCO Utility

1. The power import by GEDCOL Solar is not being deducted from WESCO energy drawal since April’2016

2. CESU has not made claim for the energy exported by CESU to WESCO control area for the month of November’2016. 

3. Power restriction to Industrial area may be avoided as WESCO is losing reliability surcharge. 
Deliberations in the meeting
Members advised that WESCO may take up the bilateral issues with GRIDCO and CESU through a different meeting. SLDC stated that there is no power restriction to Industrial consumers by SLDC. 
[Action: WESCO / GRIDCO/ CESU]

SOUTHCO Utility

1. Deduction of the station transformer loss from SOUTHCO drawal for energy accounting & replacement of defective meters used for station consumption at OPTCL Grid sub stations.

2.  Deduction of energy export to WESCO through Mukhiguda feeder from Tentulikhunti Grid substation and to Mega lift project of WESCO from Kantamala 33 / 11kV substation from SOUTHCO drawal.

3. Providing adopted CT / PT ratio for all interface metering points of SOUTHCO.

4. Provision for indicating the status of transmission elements of OPTCL system in the RVDU.
Deliberations in the meeting

SLDC stated that GRIDCO may organize a meeting with all Discoms to resolve the Item-1 and 2 issues. CT /PT ratio is being provided to the Discoms. SOUTHCO may come up with specific issue if any. The issue raised at item 4 is not clear. SOUTHCO was requested to specify the requirement of transmission element status of OPTCL network to them.   
[Action: CESU / NESCO / WESCO / SOUTHCO / GRIDCO / SLDC] 
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by March’ 2018.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by March’2018.

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	March’18

	4
	400/220 kV, 2x315 MVA Lapanga S/S
	June’18

	5
	220/33 kV, 2x20 MVA Baliguda S/S
	December’17

	6
	220/33 kV, 2x20 MVA Kalimela S/S
	June’18

	7
	220/33 kV, 2x20 MVA Kasipur S/S
	December’17

	8
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	February’18

	9
	220/33 kV, 2x20 MVA Narasinghpur S/S
	March’18

	10
	220/132 /33 kV, 2x100 MVA Aska S/S
	June’18

	11
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	January’18

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	December’18

	13
	220/132/33 kV Jayapatana S/S(320 MVA)
	December’18

	14
	220/132 kV Pratapassan S/S(320 MVA)
	March’18

	15
	220/132 kV Kesinga S/S (320 MVA)
	March’18

	16
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	March’18

	17
	132/33 kV Ghense S/S
	March’18

	18
	132/33 kV Dhenkikote S/S 
	January’18

	19
	132/33 kV Betanati S/S
	March’18

	20
	132/33 kV Kantabanji S/S
	January’18 (Line charged)

	21
	132/33 kV Podagada S/S
	December’17

	22
	132/33 kV Muniguda S/S
	December’17

	23
	132/33 kV R.Udyagiri S/S
	March’18

	24
	132/33 kV Chikiti S/S
	March’18

	25
	132/33 kV Athagarh S/S
	February’18

	26
	132/33 kV Tirtol S/S
	January’18 (Bus charged)


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. 

[Action: CESU / NESCO / WESCO / SOUTHCO] 
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC

SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators, the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the last meeting, O&M stated that IB TPS has placed requisition for 6 Nos of Apex meters. SLDC stated that for replacement of all meters including generators, 10 nos of meters will be required. IBTPS may place their requisition for 10 Nos. of meters.

In the 113th PSOC meeting O&M has agreed to install 4 Nos meters as check meter in 220 kV Ib-Budhipadar line.

In the 114th PSOC meeting O & M stated that the energy meters have already been released. Ib-TPS was advised to co-ordinate with Budhipadar sub-station for installation of meters.
Deliberations in the meeting
The energy meters are yet to be installed. O&M was requested to explore the installation process.
[Action: OPTCL / IB TPS]    
E.3: Declaration of stand-by Energy Meter 
OPTCL should declare a meter as “Standby Meter” for Generators & EHT consumers for the purpose of energy accounting in case of failure of main & check meter. As per Section 2 (v) of Central Electricity Authority (Installation and Operation of Meters) Regulations, 2006, ‘Standby Meter’ means a meter connected to CT and VT, other than those used for main meter and check meter and shall be used for accounting and billing of electricity in case of failure of both main meter and check meter. The standby meter must be a ABT compliance meter.
Further, due to frequent problems noticed in the CVTs, it is suggested to replace the CVT by IVT for metering purpose. In the 114th PSOC meeting it was suggested that OPTCL may notify the stand by meters.

Deliberations in the meeting

It was decided that a separate meeting will be convened by GRIDCO with OPTCL (O&M) and SLDC to finalise the issue.

[Action: GRIDCO/ O&M/SLDC]
E.4: Replacement of defective meters  at Renewable sources.

It is noticed that the energy meter installed at the following renewable sources are showing “power off” mostly during night time resulting non-recording of energy imported by the renewable projects.

1. Jay Iron & Steel, Bamra

2. MGM Green Energy Ltd., Chandpur

3. Molisati Vinimay Pvt. Ltd., Barkot

4. Rajratan Energy Holding Pvt. Ltd., Bolangir

5. Abacus Holdings Pvt. Ltd., Sonepur

6. Alex Green Energy Pvt. Ltd., Patnagarh
In the 114th PSOC meeting it was suggested to investigate the issue by GRIDCO & DISCOMs 

Deliberations in the meeting

GRIDCO stated that the investigation is under process.

[Action: GRIDCO / WESCO/CESU]
E.5: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same. Another meeting was proposed to be convened in the month of August’17 to finalize the mechanism of data communication. In the 113th PSOC meeting, it was decided that GRIDCO will take follow up action with all the RE generators to provide real time generation data to SLDC. ERLDC has reminded again to intimate the status.   

In the 114th PSOC meeting Director (Commercial) has agreed to convene a meeting soon to discuss the issue.

Deliberations in the meeting
GRIDCO stated that the meeting will be convened soon.

[Action: GRIDCO/ Telecom / SLDC]
E.6: Major Events in the month of October’17
03.10.2017 – 220/132 kV, 160 MVA Auto at Balasore charged

16.10.2017 – 220/33 kV, 20 MVA 2nd Tfr at Bonei Charged

26.10.2017 – 132 kV Rairakhol Traction feeder charged

E.7: Important Grid Incidences during the month of October’17.
There was only one incident during the month with tripping of all 220 kV feeders at Budhipadar S/S bus-1. The disturbance was due to insulator damage at Loc. No. -8, 9 and 10 of 220 kV Budhipadar-Korba Ckt-III.
E.8: Outage of major transmission Elements during the month of October’17. (above 10 hrs).
Deliberations in the meeting
Outage of major transmission elements above 10 hours during the month was reviewed. Most of the outages are due to insulator damage /jumper / conductor snapping.

[Action: C.G.M. (O&M)]
E.9:  Review of Outage Program of State Generators / Transmission elements for the month of Dec’17:
Tentative Outage programme for State Generators for the month of Dec’2017 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1

# 5

# 6
	01.12 to 31.12.17

25.10.16 to continue

16.10.15 to continue
	Annual Maintenance

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to continue
	Under R,M & U

	3
	Balimela
	# 1
# 2

# 7
	05.08.16 to continue
01.11.17 to continue

12.10.17 to 25.12.17
	Under R,M & U
Programming for R&M

Governor problem 

	4
	Rengali
	# 5
	21.03.17 to 16.12.17
	Hoist gate problem

	5
	Upper Kolab
	# 2
	28.05.17 to 30.04.18
	MIV Problem

	6
	Upper Indravati
	# 1

# 3
	01.12.17 to 31.12.17

01.01.18 to 31.01.18
	Annual Maintenance

Annual Maintenance


E.10: Generation Program for the month of December’17.
Generation schedule for the month of November’17 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.11.16
	Reservoir Level as on 01.11.17
	MDDL
	High Flood    Reservoir Level

	
	Dec’17

(1st fortnight)
	Dec’17

(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	30
	30
	630.06 ft 
	 629.25 ft
	590 ft.
	630 ft.

	HPS-II, Chiplima
	20
	20
	-
	-
	-
	-

	Balimela
	30
	30
	1507.20 ft 
	1486.50 ft
	1440 ft.
	1516 ft.

	Rengali
	10
	10
	123.00 mt

1.78mt mtr mt
	123.28 mt mt
	109.72mtr 
	123.5 mtr.

	U.Kolab
	20
	20
	856.65 mt mt
	854.06 mt
	844 mtr 
	858 mtr.

	U. Indravati
	50
	50
	639.28 mt
	634.40 mt mt
	625mtr 
	642 mtr

	MKD (O/D)
	40
	40
	2747.40 ft 
	2748.90 ft
	2685 ft.
	2750 ft.

	TOTAL
	200
	200
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

E.11: Anticipated power generation and demand for the month of December’2017.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	800
	1000

	2
	WESCO
	700
	900

	3
	NESCO
	550
	750

	4
	SOUTHCO
	400
	500

	6
	Total Discom
	2450
	3150

	
	System Loss & others
	150
	200

	
	Total Demand
	2600
	3350

	Availability
	
	

	1
	Hydro
	200
	900

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	400
	400

	4
	ISGS share (including OA)
	1050
	1100

	5
	CGP support (OA)
	200
	200

	6
	Total availability
	2600
	3350

	7
	Surplus / Deficit
	0
	0


PART F: OTHER ISSUES

F.1:  Installation of OPGW in 400kV Indravati (PG) – Indravati (OHPC).

POWERGRID shall install OPGW in 400KV Indravati(PG) - Indravati(HPS) as per the  Fibre Optic Expansion package of ER in the month of December 2017. POWERGRID have requested ERLDC for issue of clearance for availing shutdown on the said line with effect from 06-12-2017 to 10-12-2017 from 08:00 hrs to 17:00 hrs on daily basis which needs approval basing on the consent of OPTCL in the upcoming 139th OCC meeting of ERPC scheduled to be held on 27.11.17. 

Deliberations in the meeting
CGM (Telecom) stated that OPTCL shall take up the work as 400KV Indravati(PG) - Indravati(HPS) line belongs to OPTCL. 


[Action: C.G.M. (Telecom)]

ANNEXURE

[image: image2.png]115th Power System Operational Co-ordination Committee Meeting

At 10:30 A.M. on 24.11.2017]
[At CPTI, RSP, Rourkela]

:l‘;. Name Designation | Organisation Mobile No. E-mail Address Signature
: Qqon-Hrmz.mrm @
| GD PATEL | oy oPTeL | 9438907829 2P =
2 | H-K- Samandorgn, |ComCd) | P70 |A4389 07720 |Samrtol@obtel-eai | B
3| NLC Swosw Cam tomsh| oRTCL | 94389079¢/ | tgm 6 @ ol -6 4@‘
W Grine = -
0N Mishe | Comgae Qu3gGeTYy | S WG welto iy Dun
5 [P Mishae eLD SLIDIC SY28%0 TMO 2 | sgm pQsllorisnas s Nm/
6| P 5. Sk if_ﬁa"s‘f‘:‘“ optel, | Q438904FF8 |-ele prsabu@optet. costn
' [RK shak |TEN | RSP |s99556/473 15k STehes,
8 | T B MsHRG |co® | wesed | P37 250 me@uﬂfﬁiﬁfi\a / &
9 | S-F-Fanda U“‘““S”:’»@ OWpe i |T2a88Y0 300 S-rrxd’(//;&afw,,%;g_ _9\—4_-
10 H P’Mmﬁm_g&ﬂ M?CM 7318*8’%00!5’ /YM,WC@;M‘W W —1
T
i ﬁKrM/loLaWﬁf % e | F2 298 ot |alm EF@%Ls ,24;
2 |G K Mishiz | B T | gpter |ueeqoTe it smita ] g
5| S P Aadh, |499 )54 ”?JL,% 77T TR g ccapiitod Yy
14 5 . Q/W‘/(/*W/{v g(‘émﬂ—; ﬁ”PTC(/ 2‘4}%0%@01 %ﬁfb’o”””;m %2/
o /~<-N' flz |6m ermfgrac 30009, |ele-Apin o orre | MO
T T AN kDY b cuin ]S cults o 4775 ©129( &W“"}fﬁ- %},”,”“4‘ &A&W
7 kTR Beaiary | Dpm 7)) OFTC'/;%"[W&SQ‘MMM”?W‘Q?@ %% ’
18 |S-K Mohaity — Pgmre) |Oprel . |q438707505 . fzé‘ﬁwwe,‘:f.‘:f-ﬁw&%ﬁﬂ
19 DF- MSh na Dom(ED [ CEsU  |G8610M28YL PR Eikssto-pf o“»"’/(,
0 Bt pabro  |EE (MY 0@ Sco | 44371 S0l U4 | pabedam @ grath] SLET
? o O |5 wamzebl O
21 |S K- Pakve Monagtr | Lugscd qqu270 S72°¥% s \w“@lmbcm %
2| A 2.5 C?J::;Su o Pt ¢ 93371 ¥ é’go';’;;‘“& v %‘-yv})
5 fneon crmedl B m | \WESLE |qusaqocerg |mmegelt | Hanilf,,
o @l\/ﬂlyﬂm % a’%u} zy qli3890 62/ ?__/M/b»mﬂ-t&gﬁ/)w( W
[ ) T oc = v
5 R MG | AGLM sprel QULR9o+> euéw& C Mkl
5|6 K, Devy  Htam | BpTUL| TARET Y “@W A
\ y -
7 |5 K Manatende | G M Apier [A43%i0T04> U"'WI‘MM Sy &5
|
BlLNayar | GM eprel | 382l pleleragete



    
[image: image3.png]R ' o/0. Usaendysats,

9 | Cemawodi Ledio @44(0) S, b%gﬁp?j@ A J/deo’;:alwv-('» 4
30 | Baosh Kovenost Dewr | Comaclont | SLD2 9437000 26) Aoabosoas e o A0
3| Prashent Wumee Do | Dgucer) . R R s > O &

32 | Manas Kawer Gock | B m Cs1ct Vedssty | AA3724754S  ransbancr per el
3R WAL [ROMEMD| yedader| 9879021579| 7 meli@uedonta ch o T
| C G e Aot | Sinobia | D090 79509 ﬁﬁ;ﬂj" 2 \}\0%





