[image: image1.png]STATE LOAD DESPATCH CENTRE
OFFICE OF THE CHIEF LOAD DESPATCHER
ODISHA POWER TRANSMISSION CORPORATION LIMITED

: ‘m. ) GRIDCO Colony, P.O.- .\lf\l!cllt‘sxvzlr Rly. Colony, Effl”‘lzlil[‘_&\_ﬂ ar-17, FAX-0674- 2748509
i ok CIN - U401020R2004SGC007553
v
No-SGM (PS)-PL-15/2016 / 2 I Dated:7/.01.2018
From:

The Chief Load Despatcher
SLDC, OPTCL, Bhubaneswar-17.

To:

As per distribution list

Sub: Minutes of 116™ PSOC meeting held on 27.12.2017 at PTC, Chandaka

Sir,
Please find enclosed herewith the minutes of 116" Power System Operational Co-
ordination meeting held on 27.12.2017 at PTC, Chandaka, Bhubaneswar.

This is for your information & necessary action.

Yours faithfully;

Encl: As above %ﬁ

A
Chief Load Despatcher,
SLDC, OPTCL

Copy along with enclosures forwarded to the Executive Assistant to CMD, Gridco / OPTCL
for kind information of CMD.




Distribution list

1. The Director (Commercial), Gridco, Bhubaneswar

2. The Director (Operation), OPTCL, Bhubaneswar

3. The Director (Projects), OPTCL, Bhubaneswar

4. The Director (Operation), OHPC, Bhubaneswar

5. The CGM (O&M), OPTCL, Bhubaneswar.

6. The CGM (Const.), OPTCL Bhubaneswar.

7. The CGM (RT&C), OPTCL, Bhubaneswar.

8. The CGM (PP), GRIDCO, Bhubaneswar.

9. The CGM (IT), OPTCL, Bhubaneswar.

10. The CGM (Telecom), OPTCL, Bhubaneswar.

11. The Sr. G.M (Const)-I, OPTCL, Bhubaneswar.

12. The Sr. G.M (Const)-II, OPTCL, Sambalpur.

13. The Sr. G.M (CPC), OPTCL, Bhubaneswar.

14. The Sr. G.M (CP), OPTCL, Bhubaneswar.

15. The Sr. G.M. (O&M), Zone-I, Narendrapur 

16. The Sr. G.M.(O&M), Zone-II, Meramundali.

17. The CEO, CESU, Bhubaneswar.

18. The A.O., WESCO, Burla

19. The A.O., NESCO, Balasore

20. The A.O., SOUTHCO, Berhampur.

21. The Member Secretary (GCC), OPTCL.

22. The ED, Power Grid Corporation of India, Bhubaneswar.

23. The Sr. G.M. (El.), BHEP, Balimela

24. The A.G.M. (El.), CHEP, Chiplima

25. The Sr. G.M. (El.), UIHEP, Mukhiguda

26. The Sr. G.M. (El.), RHEP, Rengali

27. The D.G.M. (El.), HHEP, Burla

28. The D.G.M. (El.), UKHEP, Bariniput, Koraput

29. The S.E. (O&M), Machhakund

30. The DGM (Elect.), IbTPS, OPGC, Banharpali.

31. The Vice President (O), IMFA, Choudwar.

32. The D.G.M. (O&M), NTPC (TTPS), Talcher.

33. The AGM (Elect.), JINDAL Stainless Ltd., Duburi

34. The G.M, HINDALCO, Hirakud.

35. The G.M.CPP, NALCO, Angul.

36. The Director, M/s. Jindal Steel & Power Ltd., Angul

37. The AVP-Vedanta Ltd (IPP), Jharsuguda

38. The G.M, Vedanta Ltd (CGP), Jharsuguda.

39. The DGM (Power Distribution), RSP, Rourkela.

40. Joint President, Aditya Aluminium Ltd., Lapanga, Sambalpur

41. The G.M. (Elect.),  Bhusan Steel Limited. Meramundali

42. The G.M. (Elect.), Bhusan Power & Steel Ltd, Budhipadar.
43. The G.M. (Elect.), IFFCO Limited.

44. Director & COO, GMR Kamalanga Energy Limited, Satyanagar, Bhubaneswar.

45. The CEO, Bhubaneswar Power Pvt. Ltd, IRC Village, Nayapalli, Bhubaneswar.

46. M/S Tata Power & Steel Ltd., Kalinganagar

Odisha Power Transmission Corporation Ltd. Bhubaneswar.


Minutes of 116th PSOC meeting held on 27.12.2017 at PTC, Chandaka, BBSR
List of participants is at Annexure.

CLD, SLDC welcomed all the members to the 116th PSOC meeting. In his welcome address, he highlighted the system performance for the month of November’2017 and overall power scenario of the State. He also emphasized on the power drawal, made by all the Discoms during the month. 
D.G.M. (SS), SLDC took the agenda items for discussion.
The review proceeded as follows: 
1: Confirmation of minutes of 115th PSOC meeting held on 24.11.2017
The minutes of meeting was circulated vide letter No. SGM (PS)-PL-15/2016/4236(46) dated 12.12.2017 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting:
The minutes of 115th PSOC meeting was confirmed. 
PART B : SYSTEM PERFORMANCE
B1: Review of Grid Performance for the month of November’2017.
(A)  Frequency 

It was noticed that, during the month of November’17, 72.83 % of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 76.19 % during the month of  October’17. The maximum and minimum System frequency during the month was 50.12 Hz & 49.70 Hz respectively.

 (B)  Grid demand 

Grid demand for the month of  November’17 was reviewed. The average consumption during the month was 2938 MW. The maximum System demand of 4158 MW occurred on 01.11.17at 19:00 Hrs and minimum demand of 2231 MW occurred on 24.11.17 at 06:00 Hrs. 
Deliberation in the meeting

It is observed that the average demand during the month of  November’ 17 has been decreased by 631 MW while the peak demand  was decreased by 333 MW from that of October’17. The average demand during the month has been increased by 188 MW in comparison to November’16. Due to weather condition & reduction of import of power by M/s Vedanta Ltd. through Open Access transaction are the reasons for decrease of average demand.
 (C)  Voltage Profile of important Sub Stations in OPTCL System during the month of Nov’17.

The Voltage profile at different 220 kV buses in OPTCL system during the month of Nov’17 was reviewed. 
The maximum Voltage of 240.98  kV occurred at Jayanagar 220 kV bus. Meramundali 220 kV bus has experienced the minimum Voltage of 209.75 kV. The 220 kV Voltage profile of Jayanagar & Narendrapur and 400 kV Voltage profile of Meramundali  & New Duburi bus during the month of November 2017 in 15 minute block was reviewed.
Deliberation in the meeting:
It was decided that SLDC shall monitor the VAR injection by JSPL & BSL on real time basis and issue instruction to absorb VAr at high voltage condition failing which one ckt. of the above industries shall be disconnected from both the ends. JSPL requested to review the matter of isolation and assured to absorb VAr as per the instruction of SLDC.





.

 [Action: JSPL / BSL / SLDC]
(D) Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of November’17.

Auto loading of all 220 kV S/Ss was reviewed. 
(E) DISCOM Drawal during the month of November’17 
The schedule and actual energy drawal by Discoms for the month of November’17 was reviewed. 
Deliberation in the meeting:
It was noticed that the total energy drawal by all the Distribution Utilities  during the month was in line with the scheduled energy. 
(F) Energy Generation / import during the month of November’17 
Energy generation and exchange during the month of  November’17 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2115.61 MU. 
Deliberations in the meeting
The energy demand has been decreased due to reduction of import of power by M/S Vedanta Ltd. through Open Access transaction & weather condition. 
 (G) Drawal of Machhakund Power during the month of November’17
The drawal of Machhakund power during the month of November’17 was 8.7 MU, against AP drawal of 14.885 MU. 
Deliberations in the meeting

Due to low generation at Machhakund PH, Machhakund did not allow to draw the State’s share during the month.  
(H) Under Frequency relay operation in OPTCL System during the month of November’17.

There is no UF Relay operation during the month of November’17 as the frequency had never gone beyond 48.50 Hz. 
(I) Status of Open Access applications during the month of November’2017
Status of Open Access Applications received and disposed by SLDC during the month was reviewed.

Deliberations in the meeting
Total 107 numbers of Short Term / Medium term and Collective transaction applications have been processed by SLDC for according Approval / Consent / NoC during the month. 
PART C – Issues discussed in the 140th OCC meeting of ERPC on 19.12.2017
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting held on 29.04.16 at New Delhi, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format. 
The latest status as updated by OPTCL is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	Amount

Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	3
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	10.05.15
	10.05.17
	162.5 Cr.


	25.16 Cr.
	Total contract awarded for

Rs. 51.35 Cr




In the 113th PSOC meeting CGM (O&M) stated that that the DPR for installation of reactor has been sent to NLDC for PSDF funding as per the suggestion given by ERLDC during a joint study. CPC has been requested to take necessary action for tendering the 400 kV Bus reactor to be installed at Meramundali S/S.
In the 114th PSOC meeting CGM (O&M) stated that the automation of 7 nos of 220kV sub-stations needs to be incorporated for PSDF funding. A proposal in this regard is under process to be placed before BoD for approval. 

In the 115th PSOC meeting, GM (O&M) stated that the approved amount has been scaled down. The actual amount will be intimated to ERPC. Further, proposal for installation of 400 kV reactors at Meramundali S/S has been discussed and finalized in the meeting conducted by NLDC. After approval by the Appraisal committee, the same will be included for funding through PSDF.
In the 140th ERPC meeting, Member Secretary advised to furnish revised target date along with the details of work.
Deliberations in the meeting
OPTCL stated that they are linking another project for funding through PSDF and the target date will be changed. The revised target date for completion will be intimated to ERPC. 
Further, technical specification for 400 kV bus reactors at Meramundali S/S is yet to be prepared. It was suggested that CPC may expedite the same. 
[Action: Sr. G.M. (CPC) / CGM (O&M)] 
C.2: Persistent over drawl by West Bengal and Odisha
Odisha overdrawl pattern was also deliberated in 139th OCC. SLDC, Odisha informed that the over drawl was mainly due to forced outage of units at GMR and Vedanta units. GMR Unit – 3 of 350 MW which was out since 15-11-2017 on coal shortage, synchronized on 29-11-17 at 00:26 Hrs. Vedanta all units except Unit – 2 were also in service from 29-11-17 onward. Vedanta U-2 was out for maintenance work from 28-Jun-2017. However, even after synchronization of above units there is no reduction in Odhsa overdrawal.
West Bengal and Odisha are also advised to maximize their internal generation and increase their power purchase quantum in STOA/Power Exchange or from any other source to maintain their drawal as per schedule. In case of repetitive non-compliance of ERLDC instruction to curtail overdrawal during real time operation continues in future, ERLDC will have no other option but to approach appropriate commission with respect to erring entities.

In view of the above, Gridco is requested to explore import of power from any other sources to meet the State’s demand and to avoid appearance before the CERC.

Deliberations in the meeting

GRIDCO stated that they are take necessary action for procurement of power from other sources to meet the State’s requirement.

[Action: GRIDCO] 

C.3: PPA details for the years 2017-18 to 2019-20
CEA vide mail dated 21st November 2017 informed that it has been decided to estimate the demand and availability of power (energy and peak), initially for the year 2017-18 and subsequently for the years 2018-19 and 2019-20. In this regard, PPA details for the years 2017- 18 to 2019-20 are required as per the format available in the ERPC agenda.
All the constituents furnish the data as per the format to CEA by email: rk.jena@gov.in.

Deliberations in the meeting

GRIDCO stated that they shall furnish the required data.

[Action: GRIDCO] 

C.4: Data for preparation Load Generation Balance Report (LGBR) of ER for the year 2018-19
As per the IEGC, RPC Secretariat is responsible for finalization of the Annual Load Generation Balance Report (LGBR) for Peak as well as Off-peak scenarios and the annual outage plan for the respective region. Vedanta / GMR / OPGC are requested to furnish their realistic generation programme for FY 2018-19.

Deliberations in the meeting

It was deliberated that Vedanta / GMR / OPGC shall furnish the required data directly to ERPC under intimation to SLDC.

[Action: Vedanta / GMR / OPGC] 

C.5: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 116th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by June’18. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by Feb’18. 

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Keonjhar S/S (220/33 kV) by March’18.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	March 2018 

	b.


	LILO of one circuit of Atri-Puri (Samangara) 220 kV D/C line at Pandiabil (PG). 
	Atri – Pandibili 220 kV one ckt charged on 19.05.17

Pandiabili – Samangara 220 kV one ckt. charged on 20.05.17. LILO of 2nd ckt has been completed. 


Deliberations in the meeting
NESCO intimated that they are ready to draw power from the proposed 220/33 kV S/S Keonjhar S/S.

[Action: CGM (Const) / NESCO]
C.6: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In the 107th PSOC meeting, CGM (IT) informed that “Crisis management plan” work is awarded to M/s Digital Age Strategies Pvt. Ltd. The said firm has completed the study of Servers and Firewalls at SLDC, Bhubaneswar and back-up SLDC at Meramundali. Presently the data centers of SLDC and GRIDCO are being audited for IT security vulnerability assessment.

SLDC is requested to nominate one officer for attending the Cyber Security training to be held at Bengaluru during 11th to 15th April’2017. Nominations from GRIDCO and OPTCL have since been received. Top management awareness-cum Seminar on the subject shall be organized subsequently.

In the 115th PSOC meeting, IT stated that the report has been furnished by Telecom. Tendering for ‘Auditor certification’ has been finalized. Work order will be placed soon.  
Deliberations in the meeting

IT stated that audit has been completed and recommended for “ISO 270001 certificate”. Certificate will be received by the end of February’2018. 
[Action: CGM (IT) / Telecom]
C.7: Certification through BIS as per IS 18001:2007 to all generating / transmission units.
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In the 110th PSOC meeting CGM (O&M) stated that BIS office at Bhubaneswar was contacted in this regard. It was decided that OPTCL shall nominate its officers to take training. After completion of training they will conduct audit and certify.
In the 111th PSOC meeting CGM (O&M) stated that 22 nos of officers are nominated from Chandaka, Mendhasal, Atri, Kesura, Bidanasi & Cuttack S/Ss to undergo training. Awareness training shall be started from 1st week of August’17. After receiving the price offer, order will be placed. 

In the 113th PSOC meeting CGM (O&M) stated that certification for 6 Nos of S/Ss will be done by December’2017.
In the 115th PSOC meeting GM (O&M) stated that 2nd phase training has been completed. Modality for 6 Nos of S/Ss will be prepared by December’2017.

Deliberations in the meeting
CGM (O&M) stated that draft modality has been prepared. Order for Mendhasal S/S will be issued as a pilot project.
[Action: CGM (O&M)]
C.8: Updating of GT and ICT Tap position of all EHV transformers

All the generation, transmission and distribution utilities have been requested to go through Annexure-B19 of the 140th OCC agenda of ERPC related to last updated information related to GT/ICT/ATRs available at ERLDC and update the capacity, number, tap details, make (Company name) and other information including addition of new transformers, wherever felt necessary.
Deliberations in the meeting

It was suggested that OPTCL / OHPC & other State Generators shall check & update.
[Action: CGM (O&M) / OHPC / OPGC / TTPS / Vedanta / GMR]

C.9: Checklist for submission of updated data for Protection Database

The network data in Protection Database needs to be updated on regular basis on account of commissioning of new elements in the CTU as well as STU networks. Accordingly, a checklist has been prepared which is indicated below.

All the constituents are requested to submit the checklist on monthly bases in every OCC/PCC meetings.

In 139th OCC, all the constituents were advised to submit the data to ERPC vide mail (mserpcpower@nic.in) as per the checklist for last three months.

Deliberations in the meeting

CGM (O&M) stated that they are updating the database.

[Action: CGM (O&M)]

C.10: Status of Disturbance Recorder, Stand alone Event Logger and Time Synchronization equipment.

The status of DR/EL and GPS as updated in previous OCCs is given below. Constituents are also requested to furnish their list of new DR/EL which are not included in the list.

Deliberations in the meeting

CGM (O&M) stated that EL at Meramundali sub-station for 220kV side has been installed and EL for Mendhasal sub-station has been included in the automation project. OHPC stated that DR of Indravati PH has been rectified.

[Action: CGM (O&M)]

C.11: Status of Emergency Restoration System (ERS Towers) for Eastern Region constituents

CEA vide letter dated 21.07.2017 requested to send the status of state-wise availability of ERS towers and requirement of ERS towers.

In 136th OCC, MS, ERPC informed that CEA vide letter dated 21.07.2017 has sought the latest status on ERS. Therefore, OCC advised all constituents to send the updated status to ERPC secretariat vide mail (mserpc-power@nic.in).

Deliberations in the meeting

      CGM (O&M) stated that the status of ERS is the same as indicated.

C.12: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************
The DPR for ADMS has already been approved by BoD, OPTCL. SLDC shall submit the proposal for funding by PSDF for ADMS to O&M wing of OPTCL for further action.
In the 108th PSOC meeting, SLDC stated that filling of format for PSDF and floating of tender is under process. The DPR will be sent to ERPC. CGM (Telecom) stated that SLDC may contact the consultant of PSDF for filling the format. The proposal has already been sent to NLDC to include for funding through PSDF.
In the 115th PSOC meeting, SLDC stated that EoI document is being prepared by CPC. GM (O&M) stated that the item has not been listed in PSDF. SLDC may investigate and resend the proposal.
Deliberations in the meeting

CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC. 
[Action: SLDC]

C.13: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2017-18 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2017
	Conducted on 30th May 2017
	Last week of January 2018
	January 2018

	3
	Rengali
	2nd week of June 2017
	Conducted on 29.06.17
	Last week of November 2017
	Conducted on 30.11.17

	4
	U. Indravati
	3rd week of June 2017
	2nd week of July-2017
	2nd week of February 2018
	January 2018

	6
	Balimela
	3rd week of October  2017
	
	1st week of March 2018
	January 2018

	9
	Burla
	Last week of June 2017
	Can be conducted after synchronization of #2
	Last week of February 2018
	Date to be finalized by SLDC


[Action: SLDC]

PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of Nov’17:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	1
	-0.027
	0.004

	2
	WESCO
	0
	-4.425
	0.808

	3
	NESCO
	1
	-1.566
	0.368

	4
	SOUTHCO
	0
	-1.694
	0.634

	
	Total
	2
	-7.712
	


It is noticed that all utilities had under drawn during the month.
Deliberations in the meeting

The energy drawal by all the Distribution Utilities during the month was in line with the scheduled energy. 
[Action: All Discoms]
D.2: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl. No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220/132 kV, 100 MVA, Auto- 1 at Duburi
	Main tank severely damaged
	March-2018

	2
	220/132kV, 100MVA  Auto-2  at Bhadrak
	Fire hazard on 31.05.2017
	March-2018


[Action: CGM (O&M)]
D.3: Communication issues 
The status of data communication from CGPs as deliberated in the last meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s IFFCO, Paradeep
	Outdoor commissioning work completed. RTU was locally tested. CVT already replaced. Data will be integrated after restoration of OPGW between New Duburi & Paradeep.

	2
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	3
	M/s Rohit Ferrotech
	PLCC established and inspection by Telecom Engineers completed.  Database has already been prepared by OPTCL.    

	4
	VISA
	New RTU installed

	5
	Paradeep
	Duburi-Paradeep Line shutdown arranged for drawing OPGW after which data can be displayed. To be completed by January 2018.

	6
	GMR
	GMR on line data is available at SLDC but not available directly to ERLDC. GMR entrusted the work on Powergrid.

	7
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 113th PSOC meeting GCC was requested to examine for filing a case before the OERC against the CGP / Industry, those who failed to comply establishment of communication facility as the matter has been delayed considerably. 
In the 19th SCADA O&M meeting of ER held at ERLDC, Kolkata on 07th April 2017 ERLDC informed that scheduling of GMR is being done at ERLDC so data must be reported to ERLDC directly from GMR. ERLDC requested OPTCL to take up the matter with GMR so that data & voice should be available directly to ERLDC. OPTCL agreed for the same.
In the 114th PSOC meeting GMR agreed to lay OPGW for data communication to ERLDC directly. GCC stated that case will be filed against the defaulting CGP / Industry within a week.

GCC has requested CGM (Telecom) to furnish the updated status of the defaulting CGP / Industry to file a case before OERC. In the 115th PSOC meeting, GCC intimated that they will file a case before the OERC soon.
Deliberations in the meeting
GCC stated that they will file a case against NINL & IRE before the OERC soon.
[Action: CGM (Telecom) / GCC / RT&C]
D.4: Web based drawal / generation scheduling.

In the 111th PSOC meeting it was decided that from 1st August 2017 the schedule submitted through web portal will be considered. The web based schedule will be implemented for TTPS and Ib TPS from 1st September’2017. 
At present all State thermal generating stations including IPPs & CGPs are furnishing their schedule through web portal except IbTPS. Provisions for acceptance of backing down schedule for past block are not kept in the software. IT has already been intimated about this issue. Provision for automatic extraction of Power Exchange schedule for incorporation in the schedule of respective Generator / CGP may be kept in the software.
In the 115th PSOC meeting OPGC stated that IbTPS has started scheduling through web portal. IT may explore to resolve the problems identified by SLDC.
Deliberations in the meeting

IT stated that the issue has already been resolved.
D.5: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

The work for Automatic Meter Reading (AMR) for all the interface points is in progress. 

It was deliberated that from 1st March onwards the AMR shall be made “Go live”. Data will be available after one hour lapses of time.

In the 112th PSOC meeting DGM (IT) stated that TCS has complied with the discrepancies in August data. 679 Nos meter data have been collected during this month. Further, 750 Nos meter data will be available by next month. It was also decided that on 1st day of the month, SLDC will download the meter data and TCS will collect data on 2nd day and complete by evening of the day. On the 3rd day, SLDC and TCS will analyze the mismatch of data, if any. Further, a meeting may be convened by GRIDCO with all the DISCOMs to discuss acceptance of meter data through Text file.
In the 113th PSOC meeting IT stated that data from 690 Nos of meters have received during last month. It was decided that the data received by 2nd working day of the month shall be considered as final. It was further decided that the script shall be stopped on the 1st working day to enable for meter data collection by SLDC. 
In the 114th PSOC meeting IT stated that data from 640 no of sub-stations have been received on 2nd day of October. On 4th day data from some sub-stations was received. Data from remote sub-stations could not be collected due to communication network problem. Further, he stated that data from such sub-stations has to be collected manually each month. TCS has agreed to incorporate the billing software of secure meter. SLDC suggested to provide the AMR data to DISCOMs for monitoring of their real time drawal may be after lapses of 15 to 30 minutes time.
In the 115th PSOC meeting, revised deliberation of IT is as given below.

Total Number of meters integrated with AMI:
840 (Including 6 Power Houses)

Complete data available for Oct-17:

756
Out of 756 Nos of meters for which complete data is available, PRNs for testing could not be generated for 64 Nos of meters where meter power off event was observed. As per the given logic by SLDC, PRNs are generated for meters when complete data is available for whole month (96 blocks of data daily). Due to meter power off 96 daily blocks were not available for 64 meters and hence PRN was not generated.

As this is a genuine case and cannot be avoided, TCS has been advised to revisit the logic of PRN generation to include those meters or provide some alternative arrangement.
Regarding providing real time data to DISCOMs, IT stated that out of 840 total meters in AMI 600+ meters are old APEX type having very low baud rate which provide data at very slower rate. Needless to mention here that the meters are not polled one to one basis and are connected over a daisy chain resulting in sizable latency. Hence, real-time data publishing with the existing technology is not feasible.
The same can be attempted with minimal delay when the meters are replaced with modern meters having higher baud rate.

Deliberations in the meeting

IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.
[Action: O&M/ IT/SLDC/GRIDCO]
D.6: Software for Deviation charge billing.

Hon’ble OERC may notify “Intra State Deviation settlement and related matters” Regulation at any time. For implementation of the regulation, required software for Deviation Charge billing need to be developed and tested. CGM (IT) may take necessary steps for development of the software.

As decided a committee has been constituted for development of the software in house. The work is in progress. 

In the 115th PSOC meeting, IT stated that the software is expected to be completed by end of Dec’17.

Deliberations in the meeting

IT stated that the software is completed except calculation portion, which will be done as per the draft Regulation of OERC.
[Action: CGM (IT) / SLDC]
D.7.DISCOM Issues

CESU

1. Wide mismatch of drawal display through SCADA with actual meter data. It is requested to provide AMR data for realistic forecast.

2. To provide main & check meter reading of all APEX meters to check the accuracy of meters and also to provide the initial & final meter reading of all grid input points in the BSP bill to compare with the input given by all Circle Managers.

3. Construction of new 220/33kV grid at Chhendipada, 132/33kV grid at Parjanga & Khurda.
4. Connectivity of Ransingpur sub-station with Argul for stand by supply for Ransinghpur from which AIIMs is availing power supply.
Deliberations in the meeting

Since real time data through AMR are yet to be retrieved fully, it is not possible to provide the same to the DISCOMs. The energy accounting is being done as per the Central Electricity Authority (Installation and Operation of meters) (Amendment) Regulations 2014 and the required data are being provided to all the Distribution Utilities. As such providing of main & check meter readings are not required to be sent to Discoms. Since, 15 minutes block wise meter data are provided to the Discoms initial & final meter reading has got no relevancy. If required, CESU may compute circle wise energy input from the above data. CESU may take up the issues raised at 3 & 4 with OPTCL. Further, CESU may explore for takeoff arrangement from the new grid sub-stations, already connected.
[Action: CESU] 
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by March’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by March’2018.

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	March’18

	4
	400/220 kV, 2x315 MVA Lapanga S/S
	June’18

	5
	220/33 kV, 2x20 MVA Baliguda S/S
	December’18

	6
	220/33 kV, 2x20 MVA Kalimela S/S
	June’18

	7
	220/33 kV, 2x20 MVA Kasipur S/S
	March’18

	8
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	March’18

	9
	220/33 kV, 2x20 MVA Narasinghpur S/S
	March’18

	10
	220/132 /33 kV, 2x100 MVA Aska S/S
	June’18

	11
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	January’18

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	December’18

	13
	220/132/33 kV Jayapatana S/S(320 MVA)
	December’18

	14
	220/132 kV Pratapsasan S/S(320 MVA)
	March’19

	15
	220/132 kV Kesinga S/S (320 MVA)
	June’18

	16
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	March’18

	17
	132/33 kV Ghense S/S
	March’18

	18
	132/33 kV Dhenkikote S/S 
	January’18

	19
	132/33 kV Betanati S/S
	March’18

	20
	132/33 kV Kantabanji S/S
	January’18 

	21
	132/33 kV Podagada S/S
	December’17

	22
	132/33 kV Muniguda S/S
	Charged

	23
	132/33 kV R.Udyagiri S/S
	March’18

	24
	132/33 kV Chikiti S/S
	March’18

	25
	132/33 kV Athagarh S/S
	February’18

	26
	132/33 kV Tirtol S/S
	January’18 (Bus charged)


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. 

[Action: CESU / NESCO / WESCO / SOUTHCO] 
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC

SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators, the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the last meeting, O&M stated that IB TPS has placed requisition for 6 Nos of Apex meters. SLDC stated that for replacement of all meters including generators, 10 nos of meters will be required. IBTPS may place their requisition for 10 Nos. of meters.

In the 113th PSOC meeting O&M has agreed to install 4 Nos meters as check meter in 220 kV Ib-Budhipadar line.

In the 114th PSOC meeting O & M stated that the energy meters have already been released. IbTPS was advised to co-ordinate with Budhipadar sub-station for installation of meters.
In the 115th PSOC meeting, it was deliberated that the energy meters are yet to be installed. O&M was requested to explore the installation process.
Deliberations in the meeting

It was decided that CGM (O&M), OPTCL may direct the E & MR Division, Burla to take up the work.
[Action: OPTCL / IB TPS]    
E.3: Declaration of stand-by Energy Meter 
OPTCL should declare a meter as “Standby Meter” for Generators & EHT consumers for the purpose of energy accounting in case of failure of main & check meter. As per Section 2 (v) of Central Electricity Authority (Installation and Operation of Meters) Regulations, 2006, ‘Standby Meter’ means a meter connected to CT and VT, other than those used for main meter and check meter and shall be used for accounting and billing of electricity in case of failure of both main meter and check meter. The standby meter must be a ABT compliance meter.
Further, due to frequent problems noticed in the CVTs, it is suggested to replace the CVT by IVT for metering purpose. In the 114th PSOC meeting it was suggested that OPTCL may notify the stand by meters.

In the 115th PSOC meeting, it was decided that a separate meeting will be convened by GRIDCO with OPTCL (O&M) and SLDC to finalize the issue.

Deliberations in the meeting

It was decided that a separate meeting is to be convened by GRIDCO with OPTCL (O&M) and SLDC to finalise the issue.

[Action: GRIDCO/ O&M/SLDC]

E.4: Replacement of defective meters  at Renewable sources.
It is noticed that the energy meter installed at the following renewable sources are showing “power off” mostly during night time resulting non-recording of energy imported by the renewable projects.

1. Jay Iron & Steel, Bamra

2. MGM Green Energy Ltd., Chandpur

3. Molisati Vinimay Pvt. Ltd., Barkot

4. Rajratan Energy Holding Pvt. Ltd., Bolangir

5. Abacus Holdings Pvt. Ltd., Sonepur

6. Alex Green Energy Pvt. Ltd., Patnagarh
In the 114th PSOC meeting it was suggested to investigate the issue by GRIDCO & DISCOMs 

Deliberations in the meeting

GRIDCO stated that letter has been issued to the solar power producers in this regard. Discoms are requested to intimate the status in the next meeting.
[Action: GRIDCO / WESCO/CESU]

E.5: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same. Another meeting was proposed to be convened in the month of August’17 to finalize the mechanism of data communication. In the 113th PSOC meeting, it was decided that GRIDCO will take follow up action with all the RE generators to provide real time generation data to SLDC. ERLDC has reminded again to intimate the status.   

A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.

Deliberations in the meeting

CGM (Telecom) stated that the solar projects need to pay the SCADA integration charges for display of the data through SCADA.

[Action: GRIDCO/ Telecom / SLDC]

E.6: Major Events in the month of November’17
1) 400kV Jhasuguda-Vedanta (Sterlite) DC charged for the first time as follows:

a. Ckt 1: 18:27Hrs of 06/11/17

b. Ckt 2: 18:53Hrs of 06/11/17
2) 500MVA ICT II at Pandiabili charged for the first time at 15:46Hrs of 17/11/17. Earlier it was charged on 12/07/16 but failed on 21/09/16 due to internal fault. It was replaced and first time charged at 15:46Hrs of 17/11/17
3) 132/33kV, 40 MVA transformer commissioned at Choudwar by replacing the 20MVA transformer.

E.7: Important Grid Incidences during the month of November’17.
On 21.11.17 at 22:20 Hrs, 220/132kV, 160MVA AT-2 at Budhipadar sub-station tripped on differential protection due to bursting of 220kV B phase CT. All feeders emanating from 220kV Bus-I (Vedanta ckt-I, AAL ckt.-II, IbTPS ckt.- I & III, Korba ckt.-III) & AT-I tripped on bus-bar protection along with bus coupler breaker.  

E.8: Outage of major transmission Elements during the month of November’17. (above 10 hrs).
Deliberations in the meeting
Outage of major transmission elements above 10 hours during the month was reviewed. 
[Action: C.G.M. (O&M)]

E.9:  Review of Outage Program of State Generators / Transmission elements for the month of Jan’18:
Tentative Outage programme for State Generators for the month of January’2018 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 3

# 5

# 6
	01.01.18 to 31.01.18

25.10.16 to continue

16.10.15 to continue
	Annual Maintenance

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 2

# 3
	01.01.18 to 25.01.18

15.10.15 to continue
	Annual Maintenance

Under R,M & U

	3
	Balimela
	# 1
# 2

# 7
	05.08.16 to continue
01.11.17 to continue

12.10.17 to 31.01.18
	Under R,M & U
Programming for R&M

Governor problem 

	4
	Rengali
	# 5
# 4
	21.03.17 to 15.01.18

16.01.18 to 15.02.18
	Hoist gate problem
Annual Maintenance

	5
	Upper Kolab
	# 2
	28.05.17 to 30.04.18
	Upstream leakage & intake gate Problem

	6
	Upper Indravati
	# 3
	01.01.18 to 31.01.18
	Annual Maintenance


E.10: Generation Program for the month of January’18.
Generation schedule for the month of January’18 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.12.16
	Reservoir Level as on 01.12.17
	MDDL
	High Flood    Reservoir Level

	
	Jan’18
(1st fortnight)
	Jan’18
(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	30
	30
	629.23 ft 
	 628.04 ft
	590 ft.
	630 ft.

	HPS-II, Chiplima
	20
	20
	-
	-
	-
	-

	Balimela
	80
	80
	1506.70 ft 
	1483.80 ft
	1440 ft.
	1516 ft.

	Rengali
	20
	20
	122.90 mt

1.78mt mtr mt
	122.99 mt mt
	109.72mtr 
	123.5 mtr.

	U.Kolab
	50
	50
	856.34 mt mt
	853.97 mt
	844 mtr 
	858 mtr.

	U. Indravati
	150
	150
	638.90 mt
	636.11 mt mt
	625mtr 
	642 mtr

	MKD (O/D)
	20
	20
	2744.80 ft 
	2748.80 ft
	2685 ft.
	2750 ft.

	TOTAL
	370
	370
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

E.11: Anticipated power generation and demand for the month of January’2018.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	800
	1000

	2
	WESCO
	800
	1050

	3
	NESCO
	550
	750

	4
	SOUTHCO
	400
	500

	6
	Total Discom
	2550
	3300

	
	System Loss & others
	150
	250

	
	Total Demand
	2700
	3550

	Availability
	
	

	1
	Hydro
	370
	1050

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	350
	350

	4
	ISGS share (including OA)
	1050
	1200

	5
	CGP support (OA)
	200
	200

	6
	Total availability
	2720
	3550

	7
	Surplus / Deficit
	20
	0


ANNEXURE

[image: image2.png]116th Power System Operational Co-ordination Committee Meeting
[ At 11:00 A.M. on 27.12.2017]
[At PTC, Chandaka, Bhubaneswar]

SL‘. Name Designation | Organisation Mobile No. VE-mail Address Siﬁ_r\lature

1 | Bt e B i (0 | oprcl. | AU 8900730 |diepestn@opilin (o, —

2 B3P Mishea com(RTi)| 0pTCL | 9438907019 ele-me/é/‘;g% > inl e

3| 0N Mithoe com(rp) | Guidee N2850999 Y /gff’"'W@'?}W(“’“"”’ 4

4 | pK. Lahe comlosm)| opTes | Q43090791 9 | egm-ormogpfd- s hae

5 | NeC. Suaro Com(Cons)|  0PTCL | 9A38707q¢) Urn'wn@oﬂi-fwiuﬁ‘

6 | H-K. Somoderey (GM['/:(#«) spreL | 43890722 ffhygﬂ*ﬂ@offduj” %

7| Pos. Sahow Com(lnpd| 0PTEL | GY43BUOTTTE | efe pambueapbenin | (L

8 | PK.Mithse | LD SepC | 9988907400 's'gm‘,umza{;g?\'jf‘ /E/

9 | 5P Pada [T oupe | 73255020 Sqel klepe ot peif Ed—

10 | P Mt RO 1 6npC 73298 Gals | hom ttpe@gei] v, >

1| A K-Das Dyp-maneye o HPC q861089qyL ""'—‘awl’“g“zﬁjmy‘[ L

12 é’*’“‘m"?g“m N\alofam A m ORPC THAYEY O Q0K Mg,mﬂlﬂmm@?ﬁ:m &““)}‘ﬁiﬂiﬁ—
B lvamed ke Jod DaM | T [ag3g250074 ﬂ"fﬁ/ 5%@{2 @1&/7
14 ?my/dmgaﬂ Gh. | heece |o48390co s [M/éé;:fzi%L (ﬂ/ﬁ}"”‘

15 Ao Coprerp | e NEC o |qunEsotosg T;‘”w”bt@@';?;f ”W%&%z
15 |Poh Vg [hvter | ops ee [quant Soma [ S o
17 | Samih aner | Da(D) | oPTen | Q42890 7art |WSebhene it | Qoo

8 s Sebov | hem G| oprer | gyssweses ! |seshm@erklel gy

19 | .n- CHANDRA | GGy | TSPLANG AFFHHHZSSE| Bunoe - asee com (02|
VSN Padee. |6 @reolopTeoL. 9428 0guaL ele S8 RAS @

n [Pofef qhepsftarisal prer fyssrerazo ek bk gt
2 | S Padhy | 857 | 5C | 938500 geceapcr ¢ |
3 5 'P/{/W”“f% Scbhrn vpTL | Avyeats] &9+ orm |- npr C

o AT W e G RN < ol =

5 | K. Aot ]| Qb [ o1t [ voervn 72| Guge st [ J s
% | W © Jero <M"l\\ [dale WQ;

v | Pt-pdy (O | Cenn 7

5 [ G (o OOt [thy s beomaenygs | Gt





[image: image3.png]Scbiest] 1 }

wamkm & Pomm) oprer [qrzeqo par) [ebsumy © | b
s LR MR _ - ' .

0 | C&-R WM oprer [T43R 709308 |elosmthon |y gl

31| Gmacails U] Gy LLpe | 9437907409 v

32 | PRASHANT Kumpr DAS DaM(ep | Sde Ahag00F40g | prasmrdseyanrwn | () '

33 S. KD AF Congu Qe <ipc 92437000 26) <_camhneshd @ nedofin St

M| Supus oy Dy Mawergel SLbe Q428407423 ﬁ

35 |Co Mahen=ra, | AGMED | GoADo | 94385911 &w)‘nmg\gm;?:f E‘

36 | MadhwScuan Sakdp AcraCEI) GRIDGW | AE5LU27 277 e

37 Rmrﬂ,,m Poy B AEP (1) tRI9C0 | D 73F)]S 750 *’“**/’;:; e | =

38 Mol A Lomur Aam( ) SWDCT TASLIEPET w@*}#&!&gﬂ ﬁ%

9 SURRATIT BEhetsy Dy (E) | SLdc |9428909669 N L \\Mﬁ





