[image: image1.emf]
Distribution list

1. The Director (Commercial), Gridco, Bhubaneswar

2. The Director (Operation), OPTCL, Bhubaneswar

3. The Director (Projects), OPTCL, Bhubaneswar

4. The Director (Operation), OHPC, Bhubaneswar

5. The CGM (O&M), OPTCL, Bhubaneswar.

6. The CGM (Const.), OPTCL Bhubaneswar.

7. The CGM (RT&C), OPTCL, Bhubaneswar.

8. The CGM (PP), GRIDCO, Bhubaneswar.

9. The CGM (IT), OPTCL, Bhubaneswar.

10. The CGM (Telecom), OPTCL, Bhubaneswar.

11. The Sr. G.M (Const)-I, OPTCL, Bhubaneswar.

12. The Sr. G.M (Const)-II, OPTCL, Sambalpur.

13. The Sr. G.M (CPC), OPTCL, Bhubaneswar.

14. The Sr. G.M (CP), OPTCL, Bhubaneswar.

15. The Sr. G.M. (O&M), Zone-I, Narendrapur 

16. The Sr. G.M.(O&M), Zone-II, Meramundali.

17. The CEO, CESU, Bhubaneswar.

18. The A.O., WESCO, Burla

19. The A.O., NESCO, Balasore

20. The A.O., SOUTHCO, Berhampur.

21. The Member Secretary (GCC), OPTCL.

22. The ED, Power Grid Corporation of India, Bhubaneswar.

23. The Sr. G.M. (El.), BHEP, Balimela

24. The A.G.M. (El.), CHEP, Chiplima

25. The Sr. G.M. (El.), UIHEP, Mukhiguda

26. The Sr. G.M. (El.), RHEP, Rengali

27. The D.G.M. (El.), HHEP, Burla

28. The D.G.M. (El.), UKHEP, Bariniput, Koraput

29. The S.E. (O&M), Machhakund

30. The DGM (Elect.), IbTPS, OPGC, Banharpali.

31. The Vice President (O), IMFA, Choudwar.

32. The D.G.M. (O&M), NTPC (TTPS), Talcher.

33. The AGM (Elect.), JINDAL Stainless Ltd., Duburi

34. The G.M, HINDALCO, Hirakud.

35. The G.M.CPP, NALCO, Angul.

36. The Director, M/s. Jindal Steel & Power Ltd., Angul

37. The AVP-Vedanta Ltd (IPP), Jharsuguda

38. The G.M, Vedanta Ltd (CGP), Jharsuguda.

39. The DGM (Power Distribution), RSP, Rourkela.

40. Joint President, Aditya Aluminium Ltd., Lapanga, Sambalpur

41. The G.M. (Elect.),  Bhusan Steel Limited. Meramundali

42. The G.M. (Elect.), Bhusan Power & Steel Ltd, Budhipadar.
43. The G.M. (Elect.), IFFCO Limited.

44. Director & COO, GMR Kamalanga Energy Limited, Satyanagar, Bhubaneswar.

45. The CEO, Bhubaneswar Power Pvt. Ltd, IRC Village, Nayapalli, Bhubaneswar.

46. M/S Tata Power & Steel Ltd., Kalinganagar

Odisha Power Transmission Corporation Ltd. Bhubaneswar.


Minutes of 116th PSOC meeting held on 27.01.2018 at PTC, Chandaka, BBSR
List of participants is at Annexure.

CGM, SLDC welcomed all the members to the 117th PSOC meeting. In his welcome address, he highlighted the system performance for the month of December’2017 and overall power scenario of the State. He also emphasized on the power drawal, made by all the Discoms during the month. 
D.G.M. (SS), SLDC took the agenda items for discussion.
The review proceeded as follows: 
1: Confirmation of minutes of 116th PSOC meeting held on 27.12.2017
The minutes of meeting was circulated vide letter No. SGM (PS)-PL-15/2016/217(47) dated 11.01.2018 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting:
The minutes of 116th PSOC meeting was confirmed. 
PART B : SYSTEM PERFORMANCE
B1: Review of Grid Performance for the month of December’2017.
(A)  Frequency 

It was noticed that, during the month of December’17, 72.78 % of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 72.83 % during the month of  November’17. The maximum and minimum System frequency during the month was 50.18 Hz & 49.75 Hz respectively.

 (B)  Grid demand 

Grid demand for the month of  December’17 was reviewed. The average consumption during the month was 2919 MW. The maximum System demand of 4230 MW occurred on 27.12.17at 21:00 Hrs and minimum demand of 2057 MW occurred on 09.12.17 at 04:00 Hrs. 
Deliberation in the meeting

It is observed that the average demand during the month of  December’ 17 has been decreased by 19 MW while the peak demand  was increased by 72 MW from that of November’17. The average demand during the month has been increased by 196 MW in comparison to December’16. Due to load growth and import of power by M/s Vedanta Ltd. through Open Access transaction are the reasons for increase of average demand.
 (C)  Voltage Profile of important Sub Stations in OPTCL System during the month of Dec’17.

The Voltage profile at different 220 kV buses in OPTCL system during the month of Dec’17 was reviewed. 
The maximum Voltage of 243.17  kV occurred at Tarkera 220 kV bus. Mendhasal 220 kV bus has experienced the minimum Voltage of 205.82 kV. The 220 kV Voltage profile of Jayanagar & Narendrapur and 400 kV Voltage profile of Meramundali  & New Duburi bus during the month of December 2017 in 15 minute block was reviewed.
Deliberation in the meeting:
It was decided that SLDC shall monitor the VAR injection by JSPL & BSL on real time basis and issue instruction to absorb VAr at high voltage condition failing which one ckt. of the above industries shall be disconnected from both the ends. 







 [Action: JSPL / BSL / SLDC]
(D) Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of December’17.

Auto loading of all 220 kV S/Ss was reviewed. 
(E) DISCOM Drawal during the month of December’17 
The schedule and actual energy drawal by Discoms for the month of December’17 was reviewed. 
Deliberation in the meeting:
It was noticed that the total energy drawal by CESU during the month was 8.507 MU above the schedule, while all other Discom drawal was in line with the scheduled energy. WESCO stated that daily final schedule is not matching with the final schedule of the month. NESCO stated that Bhogarai S/S drawal is not incorporated in their drawal schedule. SLDC assured to take necessary action in these issues.

[Action: SLDC] 
(F) Energy Generation / import during the month of December’17 
Energy generation and exchange during the month of December’17 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2171.41 MU. 
Deliberations in the meeting
The energy demand has been increased due to import of power by M/S Vedanta Ltd. through Open Access transaction. 
 (G) Drawal of Machhakund Power during the month of December’17
The drawal of Machhakund power during the month of December’17 was 18.613 MU, against AP drawal of 17.893 MU. 
Deliberations in the meeting

Due to improve of generation at Machhakund PH, the State’s drawal during the month has been increased.  
(H) Under Frequency relay operation in OPTCL System during the month of December’17.

There is no UF Relay operation during the month of December’17 as the frequency had never gone beyond 48.50 Hz. 
(I) Status of Open Access applications during the month of December’2017
Status of Open Access Applications received and disposed by SLDC during the month was reviewed.

Deliberations in the meeting
Total 198 numbers of Short Term / Medium term and Collective transaction applications have been processed by SLDC for according Approval / Consent / NoC during the month. 
PART C – Issues discussed in the 141th OCC meeting of ERPC on 19.12.2017
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting held on 29.04.16 at New Delhi, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format. 
The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	10.05.15
	10.05.17
	162.5 Cr.


	25.16 Cr. +12.93
	Total contract awarded for

Rs. 51.35 Cr



	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	
	22.35 Cr.
	
	Tendering under process


In the 116th PSOC meeting, OPTCL stated that they are linking another project for funding through PSDF and the target date will be changed. The revised target date for completion will be intimated to ERPC. Further, technical specification for 400 kV bus reactors at Meramundali S/S is yet to be prepared. It was suggested that CPC may expedite the same.

Deliberations in the meeting
OPTCL stated that 400 kV bus Reactor for Meramundali S/S shall be procured after getting sanction by PSDF. 
[Action: CGM (O&M)/OHPC] 
C.2: Persistent over drawl by West Bengal and Odisha
In 140th OCC, over drawl pattern of West Bengal and Odisha was deliberated in detail. Some improvement in West Bengal and Odisha Drawl pattern has been observed during December and up to 7th January-2018. West Bengal average over drawl quantum was reduced to 1 MU during above mentioned period where as for Odisha over drawl quantum is around 2 MU per day.

In view of above, still there is some scope to maintain drawl as per schedule during morning and evening peak hour to avoid such quantum over drawl.
In view of the above, Gridco is requested to explore import of power from any other sources to meet the State’s demand and to avoid appearance before the CERC.
In the 116th PSOC meeting, GRIDCO stated that they are take necessary action for procurement of power from other sources to meet the State’s requirement.
Deliberations in the meeting
CGM (PP) stated that the power scenario of the State have improved due to higher IPP & hydro dispatch schedule.
[Action: GRIDCO] 

C.3: PPA details for the years 2017-18 to 2019-20
CEA vide mail dated 21st November 2017 informed that it has been decided to estimate the demand and availability of power (energy and peak), initially for the year 2017-18 and subsequently for the years 2018-19 and 2019-20. In this regard, PPA details for the years 2017- 18 to 2019-20 are required as per the format available in the ERPC agenda.
All the constituents furnish the data as per the format to CEA by email: rk.jena@gov.in.
In the 116th PSOC meeting, GRIDCO stated that they shall furnish the required data.

Deliberations in the meeting
CGM (PP) stated that GRIDCO is preparing the details of PPA made by them. GMR was requested to forward the required data.

 [Action: GRIDCO/ GMR] 

C.4: Data for preparation Load Generation Balance Report (LGBR) of ER for the year 2018-19
As per the IEGC, RPC Secretariat is responsible for finalization of the Annual Load Generation Balance Report (LGBR) for Peak as well as Off-peak scenarios and the annual outage plan for the respective region. Vedanta / GMR / OPGC are requested to furnish their realistic generation programme for FY 2018-19.

Deliberations in the meeting

It was deliberated that Vedanta / GMR / OPGC shall furnish the required data directly to ERPC under intimation to SLDC.

[Action: Vedanta / GMR / OPGC] 

C.5: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 117th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by June’18. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by Mar’18. 

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Keonjhar S/S (220/33 kV) by March’18.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	March 2018 


Deliberations in the meeting
NESCO intimated that they are ready to draw power from the proposed 220/33 kV S/S Keonjhar S/S.

[Action: CGM (Const) / NESCO]
C.5: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In the 107th PSOC meeting, CGM (IT) informed that “Crisis management plan” work is awarded to M/s Digital Age Strategies Pvt. Ltd. The said firm has completed the study of Servers and Firewalls at SLDC, Bhubaneswar and back-up SLDC at Meramundali. Presently the data centers of SLDC and GRIDCO are being audited for IT security vulnerability assessment.

In the 116th PSOC meeting, IT stated that audit has been completed and recommended for “ISO 270001 certificate”. Certificate will be received by the end of February’2018.
Deliberations in the meeting

CGM (IT) stated that audit has been completed and “ISO 270001 certificate”. Certificate has been issued conditionally for one year. In case OPTCL fails to fulfill the conditions, the period may not be extended. However, the audit report is yet to be received by IT.
[Action: CGM (IT) / Telecom]
C.6: Certification through BIS as per IS 18001:2007 to all generating / transmission units.
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In the 111th PSOC meeting CGM (O&M) stated that 22 nos of officers are nominated from Chandaka, Mendhasal, Atri, Kesura, Bidanasi & Cuttack S/Ss to undergo training. Awareness training shall be started from 1st week of August’17. After receiving the price offer, order will be placed. 

In the 113th PSOC meeting CGM (O&M) stated that certification for 6 Nos of S/Ss will be done by December’2017.
In the 116th PSOC meeting, CGM (O&M) stated that draft modality has been prepared. Order for Mendhasal S/S will be issued as a pilot project.

Deliberations in the meeting
CGM (O&M) stated that draft project report for Mendhasal S/S has been submitted to BIS. The report will be approved in the meeting to be conducted by them.

 [Action: CGM (O&M)]
C.7: Status of Disturbance Recorder, Stand alone Event Logger and Time Synchronization equipment.

The status of DR/EL and GPS as updated in previous OCCs is given below. Constituents are also requested to furnish their list of new DR/EL which are not included in the list.

[image: image2.emf]
[image: image3.emf]
[image: image4.emf]
[image: image5.emf]
In the 116th PSOC meeting, CGM (O&M) stated that EL at Meramundali sub-station for 220kV side has been installed and EL for Mendhasal sub-station has been included in the automation project. OHPC stated that DR of Indravati PH has been rectified.

Deliberations in the meeting

CGM (O&M) stated that order for EL at Mendhasal will be placed during January 2018. It was suggested that OHPC may verify whether the DR for Indravati is included for PSDF funding and intimate ERPC.

[Action: OHPC / O&M]  
C.8: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************

The latest status along with proposed logic as follows:
[image: image6.emf]
[image: image7.emf]
In the 115th PSOC meeting, SLDC stated that EoI document is being prepared by CPC. GM (O&M) stated that the item has not been listed in PSDF. SLDC may investigate and resend the proposal.

In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.

Deliberations in the meeting

It was decided that SLDC shall process for tendering.

[Action: SLDC] 
C.9: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2017-18 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2017
	Conducted on 30th May 2017
	Last week of January 2018
	Conducted on 09.01.18

	3
	Rengali
	2nd week of June 2017
	Conducted on 29.06.17
	Last week of November 2017
	Conducted on 30.11.17

	4
	U. Indravati
	3rd week of June 2017
	2nd week of July-2017
	2nd week of February 2018
	

	6
	Balimela
	3rd week of October  2017
	
	1st week of March 2018
	

	9
	Burla
	Last week of June 2017
	Can be conducted after synchronization of #2
	Last week of February 2018
	To be conducted on 29th Jan’18


The black start exercise of Upper Indravati P.H. which was scheduled to be carried out on 09.01.2018 at 11:00Hrs could not be carried out due to transmission line problem and will be performed later.

 [Action: SLDC]

C.10:Training on “Optimum calculation of transfer capability (ATC, TTC and TRM)” by International Consultant

CEA vide mail dated 21st December 2017 informed that M/S Powertech Labs Inc. (PLI) Canada is providing consultancy services in India. As per the contract 3 days training is arranged at ERPC, Kolkata from 19th to 21st February 2018. The training will be held at the ERPC conference Hall, Kolkata. The training programme covers the following topics:

· Examination and recommendation of methodology for optimum calculation of transfer capability (TTC/ATC/TRM) in the planning and the operational horizons

· Calculation of transfer capability (TTC/ATC/TRM) for entire country

Constituents may nominate members preferably dealing with Transmission Planning and Grid Operation.
Deliberations in the meeting

It was decided that CGM (O&M) shall nominate Sri Alok Kumar Maharana and Sri A.K.Banarjie for the above training

[Action: Sr. G.M. (CP) / CGM (O&M)]

C.11: Less recording by Joda end energy meter of Joda _Ramchandrapur line.
Meter No NP-5937- A installed at Joda end of 220 Ramchandarpur is recording 10 % to 15 % less as compared to Ramchandarpur end since 06.12.2017. Subsequently ERLDC vide mail dated 14.12.17 (with a copy to PGCIL) requested OPTCL to check CT/PT connection to the said meter. However the problem is still persisting and GRIDCO accounting is done with Ramchandarpur end meter.

Deliberations in the meeting

GM (O&M) stated that DGM (O&M) Joda has been advised to apply for shutdown for checking the fault and removing all unwanted meters. 

[Action: O&M]

C.12: Methodology for Submitting the Status of New Transmission Elements / Generating Units to be commissioned within the State

For clear visibility of the Eastern Region networks and better system operation, all the new transmission elements (ISTS & STU links) need to be updated regularly. The commissioning of new transmission elements of ISTS lines has been processed and updated by RLDC whereas commissioning of STU lines has been processed by SLDCs. However, commissioning status of new STU lines of states has not been updated to ERLDC and ERPC regularly. Sometime SLDCs used to submit the status of their new commissioning of elements during OCC meeting. To regularize the process following methodology need to be adopted:

1. Transmission elements/ Generating units expected to be commissioned during next month need to be submitted to ERLDC/ERPC in every OCC.

2. Detail parameters of new transmission element before commissioning need to be shared with RLDC.

3. Detail date and time of synchronization need to be updated on real time to ERLDC after commissioning of any new Transmission element/Generating unit.

4. SLDC SCADA team needs to configure the new element in their SCADA and share the same to ERLDC SCADA for network update.

5. List of the new transmission elements/ generating units commissioned during last month need to inform RLDC/RPC within 7th day of the current month, so that same to be updated in OCC.
It was deliberated in the OCC meeting of ERPC that the information should be sent by email in the following id:

1. erldcam@gmail.com
2. ftcer@posoco.in
3. mserpc-power@nic.in
Deliberations in the meeting
It was decided that Sr. GM (CP) and GRIDCO shall forward the Transmission planning and Generation planning report to ERPC and other concerns as mentioned above. 
C.13: Non-functioning of bus coupler breaker at Indravati PH switchyard – Other observation of Protection audit team
On 04.01.2018 3rd party protection audit party of ERPC visited the switchyard of UIHEP. The following observations were made by the team.

1. 220kV bus coupler breaker is not operating since 2013.
2. ICT tie breaker is not in service.
3. Digital PLCC panel is installed which is yet to be commissioned.
Deliberations in the meeting
It was decided that OHPC may take necessary action for compliance of the protection audit report. OHPC may prepare the DPR if required and seek funding through PSDF.  OHPC may coordinate GM (O&M) in this regard. CGM (Telecom) stated that communication system has been approved by NLDC for PSDF funding.
[Action: OHPC]

PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of Dec’17:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	8.507
	1.530

	2
	WESCO
	0
	3.294
	0.568

	3
	NESCO
	1
	-2.980
	0.716

	4
	SOUTHCO
	0
	-0.489
	0.180

	
	Total
	1
	8.332
	


It is noticed that CESU & WESCO had overdrawn during the month.
Deliberations in the meeting

NESCO stated that energy drawl from Bhogarai S/S is not incorporated in the above resulting indication of under drawl by NESCO. 
[Action: SLDC/ All Discoms]
D.2: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl. No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220/132 kV, 100 MVA, Auto- 1 at Duburi
	Main tank severely damaged
	March-2018

	2
	220/132kV, 100MVA  Auto-2  at Bhadrak
	Fire hazard on 31.05.2017
	March-2018


[Action: CGM (O&M)]
D.3: Communication issues 
The status of data communication from CGPs as deliberated in the last meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s IFFCO, Paradeep
	Completed

	2
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	3
	M/s Rohit Ferrotech
	PLCC established and inspection by Telecom Engineers completed.  Database has already been prepared by OPTCL.    

	4
	VISA
	New RTU installed. Testing to be done.

	5
	Paradeep
	Duburi-Paradeep Line shutdown arranged for drawing OPGW after which data can be displayed. To be completed by January 2018.

	6
	GMR
	GMR on line data is available at SLDC but not available directly to ERLDC. GMR entrusted the work on Powergrid.

	7
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 116th PSOC meeting, GCC stated that they will file a case against NINL & IRE before the OERC soon.
Deliberations in the meeting
Members opined that GCC should file a case soon against NINL & IRE before the OERC.
[Action: CGM (Telecom) / GCC / RT&C]
D.4: Web based drawal / generation scheduling.

In the 111th PSOC meeting it was decided that from 1st August 2017 the schedule submitted through web portal will be considered. The web based schedule will be implemented for TTPS and Ib TPS from 1st September’2017. 
At present all State thermal generating stations including IPPs & CGPs are furnishing their schedule through web portal except IbTPS. Provisions for acceptance of backing down schedule for past block are not kept in the software. IT has already been intimated about this issue. Provision for automatic extraction of Power Exchange schedule for incorporation in the schedule of respective Generator / CGP may be kept in the software.
In the 115th PSOC meeting OPGC stated that IbTPS has started scheduling through web portal. IT may explore to resolve the problems identified by SLDC.
Deliberations in the meeting

IT stated that option for manually change of schedule has been kept. SLDC shall submit the required format, for automatic change the schedule automatically.
[Action: SLDC]

D.5: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

Deliberations in the meeting

IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 
[Action: O&M/ IT/SLDC/GRIDCO]
D.6: Software for Deviation charge billing.

Hon’ble OERC may notify “Intra State Deviation settlement and related matters” Regulation at any time. For implementation of the regulation, required software for Deviation Charge billing need to be developed and tested. CGM (IT) may take necessary steps for development of the software.

As decided a committee has been constituted for development of the software in house. The work is in progress. 

In the 115th PSOC meeting, IT stated that the software is expected to be completed by end of Dec’17.

In the 116th PSOC meeting, IT stated that the software is completed except calculation portion, which will be done as per the draft Regulation of OERC.

Deliberations in the meeting

IT stated that the software will be ready within a week time.

 [Action: CGM (IT) / SLDC]
D.7: Rectification / Replacement of Defective Meters at different interface points.

A list of defective meters indicating the defects has been indicated by SLDC.

Deliberations in the meeting 

O&M stated that a meeting has been convened on 30.01.2018 to discuss the issue.
[Action: O&M / SLDC]

D.8.DISCOM Issues

CESU

1. Connectivity of Ransingpur sub-station with Argul for stand by supply for Ransinghpur (connected to Chandaka S/S) from which AIIMs is availing power supply.
2. Construction of new 132/33 kV S/S at Parajang, Khurda Ind. Estate & Kantilo.
3. Bay extension at Angul S/S.
4. Mismatch of drawal display with actual meter data.
5. Providing main and check meter data to CESU.
Deliberations in the meeting

SLDC stated that, the meter data management and accounting is being done as per the metering code provisions. Providing check meter data to CESU is not required. Display of Discom drawal is for monitoring purpose, which may or may not match with the energy meter data. CESU may use some software for their demand estimation without fully depending on SCADA data. CESU may take up the other issues with O&M. 
[Action: CESU]
SOUTHCO

1. Interruption of power supply to Rambha Traction sub-station during November-2017 occurred 3 times (26minutes) thereby causing serious disruption of passenger trains & loosing reliability surcharge.
2. Installation of Apex meter at 33kV Mukhiguda feeder at Tentuhkhunti Grid by OPTCL for accounting & deduction of WESCO drawal from SOUTHCO Energy account.

Deliberations in the meeting
It was decided that OPTCL shall install energy meter at Tentulikhunti for Mukhiguda feeder, which is dedicated to WESCO consumers. 26 minute interruption to a consumer during a month may not result loosing of reliability surcharge. SOUTH may go through the orders to examine the issue.

[Action: SOUTHCO]  

PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by March’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by March’2018.

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	March’18

	4
	400/220 kV, 2x315 MVA Lapanga S/S
	June’18

	5
	220/33 kV, 2x20 MVA Baliguda S/S
	December’18

	6
	220/33 kV, 2x20 MVA Kalimela S/S
	June’18

	7
	220/33 kV, 2x20 MVA Kasipur S/S
	March’18

	8
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	March’18

	9
	220/33 kV, 2x20 MVA Narasinghpur S/S
	March’18

	10
	220/132 /33 kV, 2x100 MVA Aska S/S
	June’18

	11
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	February’18

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	December’18

	13
	220/132/33 kV Jayapatana S/S(320 MVA)
	December’18

	14
	220/132 kV Pratapsasan S/S(320 MVA)
	March’19

	15
	220/132 kV Kesinga S/S (320 MVA)
	June’18

	16
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	March’18

	17
	132/33 kV Ghense S/S
	March’18

	18
	132/33 kV Dhenkikote S/S 
	January’18

	19
	132/33 kV Betanati S/S
	March’18

	20
	132/33 kV Kantabanji S/S
	February’18 

	21
	132/33 kV Podagada S/S
	February’18 

	22
	132/33 kV Muniguda S/S
	Charged

	23
	132/33 kV R.Udyagiri S/S
	March’18

	24
	132/33 kV Chikiti S/S
	March’18

	25
	132/33 kV Athagarh S/S
	February’18

	26
	132/33 kV Tirtol S/S
	Charged


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. 

[Action: CESU / NESCO / WESCO / SOUTHCO] 
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC

SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators, the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the 116th PSOC meeting, it was decided that CGM (O&M), OPTCL may direct the E & MR Division, Burla to take up the work.
Deliberations in the meeting

CGM (O&M), OPTCL may direct the E & MR Division, Burla to take up the work soon.
[Action: OPTCL / IB TPS]    
E.3: Declaration of stand-by Energy Meter 
OPTCL should declare a meter as “Standby Meter” for Generators & EHT consumers for the purpose of energy accounting in case of failure of main & check meter. As per Section 2 (v) of Central Electricity Authority (Installation and Operation of Meters) Regulations, 2006, ‘Standby Meter’ means a meter connected to CT and VT, other than those used for main meter and check meter and shall be used for accounting and billing of electricity in case of failure of both main meter and check meter. The standby meter must be a ABT compliance meter.
Further, due to frequent problems noticed in the CVTs, it is suggested to replace the CVT by IVT for metering purpose. In the 114th PSOC meeting it was suggested that OPTCL may notify the stand by meters.

In the 116th PSOC meeting, it was decided that a separate meeting is to be convened by GRIDCO with OPTCL (O&M) and SLDC to finalise the issue.

Deliberations in the meeting

It was suggested to convene the meeting is to decide the issue.
[Action: GRIDCO/ O&M/SLDC]

E.4: Replacement of defective meters  at Renewable sources.
It is noticed that the energy meter installed at the following renewable sources are showing “power off” mostly during night time resulting non-recording of energy imported by the renewable projects.

1. Jay Iron & Steel, Bamra

2. MGM Green Energy Ltd., Chandpur

3. Molisati Vinimay Pvt. Ltd., Barkot

4. Rajratan Energy Holding Pvt. Ltd., Bolangir

5. Abacus Holdings Pvt. Ltd., Sonepur

6. Alex Green Energy Pvt. Ltd., Patnagarh
In the 116th PSOC meeting GRIDCO stated that letter has been issued to the solar power producers in this regard. Discoms are requested to intimate the status in the next meeting.

Deliberations in the meeting

WESCO stated that they have visited the solar plants. The plants are using their own source such as DG & Battery for lighting purpose.

 [Action: GRIDCO / WESCO/CESU]

E.5: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same. Another meeting was proposed to be convened in the month of August’17 to finalize the mechanism of data communication. In the 113th PSOC meeting, it was decided that GRIDCO will take follow up action with all the RE generators to provide real time generation data to SLDC. ERLDC has reminded again to intimate the status.   

A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.

In the 116th PSOC meeting, CGM (Telecom) stated that the solar projects need to pay the SCADA integration charges for display of the data through SCADA.

Deliberations in the meeting

CGM (Telecom) stated that for pilot project the integration charges may not be required. The Agencies may be asked to proceed with their project.
[Action: GRIDCO/ Telecom / SLDC]

E.6: Major Events in the month of December’17
19/12/2017: 220 kV Samagara – Atri ckt.- II made LILO at Pandiabili.

27/12/2017: 20MVA, 132/33kV 2nd transformer commissioned at Mania.

E.7: Important Grid Incidences during the month of December’17.
No important grid incidence occurred during the month of December 2018.

E.8: Outage of major transmission Elements during the month of December’17. (above 10 hrs).
Deliberations in the meeting
Outage of major transmission elements above 10 hours during the month was reviewed. 

[Action: C.G.M. (O&M)]

E.9:  Review of Outage Program of State Generators / Transmission elements for the month of Feb’18:
Tentative Outage programme for State Generators for the month of February’2018 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 4

# 5

# 6
	02.02.18 to 28.02.18

25.10.16 to continue

16.10.15 to continue
	Annual Maintenance

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to continue
	Under R,M & U

	3
	Balimela
	# 1
# 2

# 7
	05.08.16 to continue
01.11.17 to continue

12.10.17 to 31.01.18
	Under R,M & U
Programming for R&M

Governor problem 

	4
	Rengali
	# 5
# 4

# 2
	21.03.17 to 31.01.18

01.02.18 to 28.02.18

16.02.18 to 15.06.18
	Hoist gate problem
Annual Maintenance

Programming for Capital Maintenance

	5
	Upper Kolab
	# 2
	28.05.17 to 30.04.18
	Upstream leakage & intake gate Problem

	6
	Upper Indravati
	# 3
	08.02.18 to 07.03.18
	Annual Maintenance


E.10: Generation Program for the month of February’18.
Generation schedule for the month of February’18 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.01.17
	Reservoir Level as on 01.01.18
	MDDL
	High Flood    Reservoir Level

	
	Feb’18
(1st fortnight)
	Feb’18
(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	40
	40
	628.17 ft 
	 626.85 ft
	590 ft.
	630 ft.

	HPS-II, Chiplima
	30
	30
	-
	-
	-
	-

	Balimela
	90
	90
	1503.90 ft 
	1479.00 ft
	1440 ft.
	1516 ft.

	Rengali
	30
	30
	122.52 mt

1.78mt mtr mt
	122.66 mt mt
	109.72mtr 
	123.5 mtr.

	U.Kolab
	60
	60
	856.39 mt mt
	853.78 mt
	844 mtr 
	858 mtr.

	U. Indravati
	200
	200
	639.00 mt
	635.92 mt mt
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2740.50 ft 
	2747.40 ft
	2685 ft.
	2750 ft.

	TOTAL
	480
	480
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

E.11: Anticipated power generation and demand for the month of February’2018.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	900
	1150

	2
	WESCO
	1000
	1100

	3
	NESCO
	700
	800

	4
	SOUTHCO
	400
	550

	6
	Total Discom
	3000
	3600

	
	System Loss & others
	150
	200

	
	Total Demand
	3150
	3800

	Availability
	
	

	1
	Hydro
	480
	1050

	2
	State Thermal
	780
	780

	3
	IPP, small hydro &RE
	600
	600

	4
	ISGS share (including OA)
	1100
	1200

	5
	CGP support (OA)
	200
	200

	6
	Total availability
	3160
	3830

	7
	Surplus / Deficit
	10
	0


PART F: OTHER ISSUES

All members expressed their gratitude to Er. B. P. Mishra, CGM (RT&C) and Er. U.N. Mishra, SCM (SLDC), who are going to retire from service on superannuation by end of this month for their advice and guidance. PSOC will remember their valuable advice and the foot prints they have left for all times with deep regard.  

F.1:  Date and Venue of the next (118th) PSOC meeting.

The date and venue of 118th PSOC meeting will be intimated to all members.

