[image: image1.png]STATE LOAD DESPATCH CENTRE
OFFICE OF THE CHIEF LOAD DESPATCHER
ODISHA POWER TRANSMISSION CORPORATIC AITED

&)
BELALS e GRIDCO Colony, P.O.- Mancheswar Rly. Colony, Bhubaneswar-17, FAX-0674- 2748509
Lifetine of Odlishal CIN — U401020R2004SGC007553

o
No-SGM (PS)-PL-15/2016 / & } Dated:29.03.2018
\

From:
The Chief Load Despatcher
SLDC, OPTCL, Bhubaneswar-17.

To:
As per distribution list

Sub: Minutes of 119" PSOC meeting held on 23.03.2018 at PTC, Chandaka

Sir,
Please find enclosed herewith the minutes of 119" Power System Operational Co-ordination

meeting held on 23.03.2018 at PTC, Chandaka, Bhubaneswar.

This is for your information & necessary action.

Yours faithfully;

Chief Load Despatcher,
SLDC, OPTCL

Encl: As above




Distribution list

1. The Director (Commercial), Gridco, Bhubaneswar

2. The Director (Operation), OPTCL, Bhubaneswar

3. The Director (Projects), OPTCL, Bhubaneswar

4. The Director (Operation), OHPC, Bhubaneswar

5. The CGM (O&M), OPTCL, Bhubaneswar.

6. The CGM (Const.), OPTCL Bhubaneswar.

7. The CGM (RT&C), OPTCL, Bhubaneswar.

8. The CGM (PP), GRIDCO, Bhubaneswar.

9. The CGM (IT), OPTCL, Bhubaneswar.

10. The CGM (Telecom), OPTCL, Bhubaneswar.

11. The Sr. G.M (Const)-I, OPTCL, Bhubaneswar.

12. The Sr. G.M (Const)-II, OPTCL, Sambalpur.

13. The Sr. G.M (CPC), OPTCL, Bhubaneswar.

14. The Sr. G.M (CP), OPTCL, Bhubaneswar.

15. The Sr. G.M. (O&M), Zone-I, Narendrapur 

16. The Sr. G.M.(O&M), Zone-II, Meramundali.

17. The CEO, CESU, Bhubaneswar.

18. The A.O., WESCO, Burla

19. The A.O., NESCO, Balasore

20. The A.O., SOUTHCO, Berhampur.

21. The Member Secretary (GCC), OPTCL.

22. The ED, Power Grid Corporation of India, Bhubaneswar.

23. The Sr. G.M. (El.), BHEP, Balimela

24. The A.G.M. (El.), CHEP, Chiplima

25. The Sr. G.M. (El.), UIHEP, Mukhiguda

26. The Sr. G.M. (El.), RHEP, Rengali

27. The D.G.M. (El.), HHEP, Burla

28. The D.G.M. (El.), UKHEP, Bariniput, Koraput

29. The S.E. (O&M), Machhakund

30. The DGM (Elect.), IbTPS, OPGC, Banharpali.

31. The Vice President (O), IMFA, Choudwar.

32. The D.G.M. (O&M), NTPC (TTPS), Talcher.

33. The AGM (Elect.), JINDAL Stainless Ltd., Duburi

34. The G.M, HINDALCO, Hirakud.

35. The G.M.CPP, NALCO, Angul.

36. The Director, M/s. Jindal Steel & Power Ltd., Angul

37. The AVP-Vedanta Ltd (IPP), Jharsuguda

38. The G.M, Vedanta Ltd (CGP), Jharsuguda.

39. The DGM (Power Distribution), RSP, Rourkela.

40. Joint President, Aditya Aluminium Ltd., Lapanga, Sambalpur

41. The G.M. (Elect.),  Bhusan Steel Limited. Meramundali

42. The G.M. (Elect.), Bhusan Power & Steel Ltd, Budhipadar.
43. The G.M. (Elect.), IFFCO Limited.

44. Director & COO, GMR Kamalanga Energy Limited, Satyanagar, Bhubaneswar.

45. The CEO, Bhubaneswar Power Pvt. Ltd, IRC Village, Nayapalli, Bhubaneswar.

46. M/S Tata Power & Steel Ltd., Kalinganagar
Odisha Power Transmission Corporation Ltd. Bhubaneswar.


Minutes of 119th PSOC meeting held on 23.03.2018 at PTC, Chandaka, BBSR
List of participants is at Annexure.

CGM, SLDC welcomed all the members to the 119th PSOC meeting. In his welcome address, he highlighted the system performance for the month of February’2018 and overall power scenario of the State. He also emphasized on the power drawal, made by all the Discoms during the month. 
G.M. (PP), GRIDCO took the agenda items for discussion.
The review proceeded as follows: 
1: Confirmation of minutes of 118th PSOC meeting held on 26.02.2017
The minutes of meeting was circulated vide letter No. SGM (PS)-PL-15/2017/893(47) dated 17.03.2018 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting:
The minutes of 118th PSOC meeting was confirmed. 
PART B : SYSTEM PERFORMANCE
B1: Review of Grid Performance for the month of February’2017.
(A)  Frequency 

It was noticed that, during the month of February’18, 78.50 % of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 76.51 % during the month of  January’18. The maximum and minimum System frequency during the month was 50.12 Hz & 49.78 Hz respectively.

 (B)  Grid demand 

Grid demand for the month of  February’18 was reviewed. The average consumption during the month was 3265 MW. The maximum System demand of 4211 MW occurred on 12.02.18at 20:00 Hrs and minimum demand of 2241 MW occurred on 16.02.18 at 15:00 Hrs. 
Deliberation in the meeting

It is observed that the average demand during the month of  February’ 18 has been increased by 158 MW while the peak demand  was decreased by 40 MW from that of January’18. The average demand during the month has increased by 333 MW in comparison to February’17. Due to change of weather condition and import of power by M/s Vedanta Ltd. through Open Access transaction the average demand has increased during the month.
 (C)  Voltage Profile of important Sub Stations in OPTCL System during the month of Feb’18.

The Voltage profile at different 220 kV buses in OPTCL system during the month of February’18 was reviewed. 
The maximum Voltage of 238.50 kV occurred at Jayanagar 220 kV bus. Bolangir 220 kV bus has experienced the minimum Voltage of 208.36 kV. The 220 kV Voltage profile of Jayanagar & Narendrapur and 400 kV Voltage profile of Meramundali  & New Duburi bus during the month of February’2018 in 15 minute block was reviewed.
Deliberation in the meeting:
CGM (O&M) stated that installation of bus reactors at New Duburi, Meramundali and Mendhasal (each 125 MVAr) have been proposed through PSDF funding.  







 [Action: CGM (O&M)]
(D) Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of February’18.

Auto loading of all 220 kV S/Ss was reviewed. 
(E) DISCOM Drawal during the month of February’18 
The schedule and actual energy drawal by Discoms for the month of February’18 was reviewed. 
Deliberation in the meeting:
It was noticed that the energy under drawl  by WESCO during the month was 37.858 MU above the schedule, while all other Discom drawal was in line with the scheduled energy. WESCO stated that the under drawl by Vedanta from its Open Access schedule is being reflected as WESCO’s under drawl.

 [Action: SLDC] 
(F) Energy Generation / import during the month of February’18 
Energy generation and exchange during the month of February’18 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2193.76 MU. 
Deliberations in the meeting
The energy demand has been increased due to import of power by M/S Vedanta Ltd. through Open Access transaction. 
 (G) Drawal of Machhakund Power during the month of February’18
The drawal of Machhakund power during the month of February’18 was 17.431 MU, against AP drawal of 15.467 MU. 
Deliberations in the meeting

Sr. G.M SLDC stated that there is no matching load available, in case more Nos of Machhakund units synchronized. Southco may explore their takeoff arrangement from newly commissioned Podagada 132/33 kV S/S to increase Machhakund drawal of the State. 
 [Action: Southco]

(H) Under Frequency relay operation in OPTCL System during the month of February’18.

There is no UF Relay operation during the month of February’18 as the frequency had never gone beyond 48.50 Hz. 
(I) Status of Open Access applications during the month of February’2018
Status of Open Access Applications received and disposed by SLDC during the month was reviewed.

Deliberations in the meeting
Total 140 numbers of Short Term / Medium term and Collective transaction applications have been processed by SLDC for according Approval / Consent / NoC during the month. 
PART C – Issues to be discussed in the 143rd OCC meeting of ERPC on 26.03.2018
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	10.05.15
	30.11.18
	162.5 Cr.


	25.16 Cr.
	Total contract awarded for

Rs. 51.35 Cr



	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-

Jan 19

Burla-Nov

2018,

Chiplima

Dec 2018
	22.35 Cr.
	
	Tendering under process


In the 116th PSOC meeting, OPTCL stated that they are linking another project for funding through PSDF and the target date will be changed. The revised target date for completion will be intimated to ERPC. Further, technical specification for 400 kV bus reactors at Meramundali S/S is yet to be prepared. It was suggested that CPC may expedite the same.

In the 117th PSOC meeting, O&M deliberated that 400 kV bus Reactor for Meramundali S/S shall be procured after getting sanction by PSDF. 

In the 118th PSOC meeting, SLDC stated that ADMS for SLDC is to be incorporated as PSDF funding item. O&M shall intimate ERPC the revised target date.
Deliberations in the meeting
O&M stated that the target date has been revised to 30.11.2018. OHPC stated that the status remained same.
[Action: O&M / OHPC]
C.2: PPA details for the years 2017-18 to 2019-20
CEA vide mail dated 21st November 2017 informed that it has been decided to estimate the demand and availability of power (energy and peak), initially for the year 2017-18 and subsequently for the years 2018-19 and 2019-20. In this regard, PPA details for the years 2017- 18 to 2019-20 are required as per the format available in the ERPC agenda.
All the constituents furnish the data as per the format to CEA by email: rk.jena@gov.in.
In the 117th PSOC meeting, CGM (PP) stated that GRIDCO is preparing the details of PPA made by them. GMR was requested to forward the required data.

In the 118th PSOC meeting, CGM (PP) stated that GRIDCO will forward the required information to ERPC by the end of February’2018.
       Deliberations in the meeting

Gridco stated that the PPA details are under process. GMR was requested to forward their PPA details in the format to ERPC.
 [Action: GRIDCO / GMR] 
C.3: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 119th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by June’18. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by June’18. 

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Keonjhar S/S (220/33 kV) by April’18.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	December 2018 


[Action: CGM (Const.)]
C.4: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In the 107th PSOC meeting, CGM (IT) informed that “Crisis management plan” work is awarded to M/s Digital Age Strategies Pvt. Ltd. The said firm has completed the study of Servers and Firewalls at SLDC, Bhubaneswar and back-up SLDC at Meramundali. Presently the data centers of SLDC and GRIDCO are being audited for IT security vulnerability assessment.

In the 117th PSOC meeting, CGM (IT) stated that audit has been completed and “ISO 270001 certificate”. Certificate has been issued conditionally for one year. In case OPTCL fails to fulfill the conditions, the period may not be extended. However, the audit report is yet to be received by IT.

In the 118th PSOC meeting, CGM (IT) stated that certificate is expected by end of February’2018.
Deliberations in the meeting

CGM (IT) stated that the Aduit report and Certificate is yet to be received.
[Action: CGM (IT) / Telecom]
C.5: Certification through BIS as per IS 18001:2007 to all generating / transmission units.
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In the 111th PSOC meeting CGM (O&M) stated that 22 nos of officers are nominated from Chandaka, Mendhasal, Atri, Kesura, Bidanasi & Cuttack S/Ss to undergo training. Awareness training shall be started from 1st week of August’17. After receiving the price offer, order will be placed. 

In the 113th PSOC meeting CGM (O&M) stated that certification for 6 Nos of S/Ss will be done by December’2017.
In the 116th PSOC meeting, CGM (O&M) stated that draft modality has been prepared. Order for Mendhasal S/S will be issued as a pilot project.

In the 117th PSOC meeting CGM (O&M) stated that draft project report for Mendhasal S/S has been submitted to BIS. The report will be approved in the meeting to be conducted by them.

In the 118th PSOC meeting, O&M stated that the report has already been submitted. Approval is yet to be received.
Deliberations in the meeting
O&M stated that approval is yet to be received.
[Action: CGM (O&M)]
C.6: Status of Disturbance Recorder, Stand alone Event Logger and Time Synchronization equipment.

The status of DR/EL and GPS as updated in previous OCCs is given below. Constituents are also requested to furnish their list of new DR/EL which are not included in the list.

[image: image2.emf]
[image: image3.emf]
[image: image4.emf]
[image: image5.emf]
In the 118th PSOC meeting O&M stated that 400 kV side EL at Mendhasal shall be replaced. Further, Order has been placed for automation of Mendhasal S/S, which is expected to be completed by end of May’2018. Proposal for including DR for Indravati is yet to be sent.
Deliberations in the meeting
OHPC stated that EL & DR at Indravati is functioning. PSOC advised OHPC to revise the status in the OCC meeting. 
[Action: CGM (O&M) / OHPC]
C.7: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************

The latest status along with proposed logic as follows:
[image: image6.emf]
[image: image7.emf]
In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 117th PSOC meeting it was decided that SLDC shall process for tendering.

In the 118th PSOC meeting, SLDC stated that the tender specification is expected to be received from CPC by 1st week of April’2018. After receiving the same SLDC will process for tendering
Deliberations in the meeting
It was decided that SLDC may prepare the financial specification and get approved from Finance wing of OPTCL without depending on CPC, as the matter is very much delayed. 
[Action: SLDC]
C.8: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2017-18 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2017
	Conducted on 30th May 2017
	Last week of January 2018
	Conducted on 09.01.18

	3
	Rengali
	2nd week of June 2017
	Conducted on 29.06.17
	Last week of November 2017
	Conducted on 30.11.17

	4
	U. Indravati
	3rd week of June 2017
	2nd week of July-2017
	2nd week of February 2018
	Conducted on
09.03.2018

	6
	Balimela
	3rd week of October  2017
	Conducted on 09.01.18
	1st week of March 2018
	Conducted on
09.03.2018

	9
	Burla
	Last week of June 2017
	Can be conducted after synchronization of #2
	Last week of February 2018
	Conducted on 29th Jan’18


[OHPC / SLDC may update in OCC meeting]
C.9: Non-functioning of bus coupler breaker at Indravati PH switchyard – Other observation of Protection audit team
On 04.01.2018 3rd party protection audit party of ERPC visited the switchyard of UIHEP. The following observations were made by the team.

1. 220kV bus coupler breaker is not operating since 2013.
2. ICT tie breaker is not in service.
3. Digital PLCC panel is installed which is yet to be commissioned.
In the 117th PSOC meeting it was decided that OHPC may take necessary action for compliance of the protection audit report. OHPC may prepare the DPR if required and seek funding through PSDF.  OHPC may coordinate GM (O&M) in this regard. CGM (Telecom) stated that communication system has been approved by NLDC for PSDF funding.

In the 118th PSOC meeting, OHPC stated that rectifications of equipments at Indravati switchyard been included for PSDF funding. Work will be completed by January’2019.
Deliberations in the meeting

OHPC stated that the work will be completed by January’2019.
[Action: OHPC]
C.10: Status of UFRs healthiness installed in Eastern Region

UFR Healthiness Certification for the month of January, 2018 has been received from CESC, WBSETCL, DVC, JUSNL, OPTCL and BSPTCL.

OCC advised OPTCL to change 33kV Laxmipur feeder with suitable feeder of desired load.

In the 118th PSOC meeting, it was decided that SOUTHCO shall identify other feeders having equivalent quantum of load in place of Laxmipur feeder load and submit to O&M for necessary action.

Deliberations in the meeting

O&M stated that Laxmipur feeder load has already been accommodated in other feeders.
C.11: Approval of outage procedure and Submission of outage request to ERLDC as per procedure.

The procedure for transmission element outage was approved in 87th ERPC meeting. After this some minor modifications in the approved procedure was also done. As per the procedure following need to be adhered by the outage indenting parties while applying OCC approved transmission element outages to ERLDC for approval:

1. Request for outages which are approved by OCC must be sent by the indenting agency of the transmission asset at least 3 days in advance to respective RLDC by 10:00 hours. (For example, if an outage is to be availed on say 10th day of the month, the indenting agency would forward such requests to the concerned RLDC on or before 7th day of the month by 1000 hours.)

2. In case the request for transmission element outage is not received within the timeline prescribed above, it will be assumed that the indenting agency is not availing the outage. However, indenting agency is duty bound to inform ERLDC at least 3 days in advance, if it is not availing the OCC approved outage.

Since last few months it was observed that some of the indenting agencies were deviating from submission dates corresponding to their OCC approval date while submitting their request, which causes a lot of inconvenience to coordinate with multiple agencies and also to carry out system study before approve the outage request. In some cases, indenting agencies were also not intimated ERLDC/ERPC in advance for cancellation of any outage approved in OCC.

Detail outage procedure as on date is updated in ERLDC website.

It was decided that SLDC & O&M shall examine the outage procedure and forward their comments to ERLDC.

[Action: SLDC /(O&M)].

C.12:  Islanding scheme for GMR & IbTPS

In the 118th PSOC meeting CGM (Telecom) stated that Telecom has suggested for laying of optical fibre to implement islanding scheme for IbTPS, which is yet to be done by them. GMR IPP has no islanding scheme at present. Also it was decided that GMR should develop an islanding scheme for their State connected unit.

Deliberations in the meeting

Ib TPS stated that their islanding scheme can be tested in the month of July 2018 while annual maintenance of units. It was decided that O&M will convene a meeting for discussion of the islanding scheme of GMR, Vedanta, NALCO and other major CGPs.
[Action: O&M/ GMR / Vedanta/ NALCO]
C.13: Accounting of Tertiary Loading Arrangement at PGCIL Grid S/Ss in ER

As per the decision in the 35th CCM meeting of ERPC held on 02.08.2017 “Accounting of Tertiary Loading Arrangement at PGCIL Grid S/Ss in ER” and subsequent ratification in 36th TCC & ERPC meeting held on 13th & 14th September 2017, it was decided that the drawal of auxiliary power from tertiary winding of different Powergrid S/Ss would be treated as State drawal for inter-regional accounting. Powergrid and States would make back to back commercial arrangements for this power.

Accordingly from the following Powergrid S/S auxiliary consumption has been added in Gridco’s drawal from 23.10.2017.

1.Angul(PG), 2. Sundargarh (PG), 3. Pandiabili (PG), 4. Bolangir (PG), 5. Baripada (PG), 6. Jaipur (PG), 7. Keonjhar (PG) and 8. Rengali (PG). For Rourkela (PG) the tertiary drawal has been added from 05.02.2018.

Till date no back to back arrangement has been made between Gridco and Powergrid to account the energy consumption ( 2.60146 MU) which has been added the State’s transmission loss. This has also been intimated to Gridco by SLDC vide letter No. 831 (4) dated 08.03.2018. 

Deliberations in the meeting

It was decided that GRIDCO will convene a meeting with Powergrid and all DISCOMs to discuss the issue of accounting the energy drawal by Powergrid.

[Action: GRIDCO / Discoms].

PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of Feb’18:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	-2.497
	0.431

	2
	WESCO
	0
	-37.858
	6.790

	3
	NESCO
	0
	-0.212
	0.052

	4
	SOUTHCO
	0
	0.789
	0.300

	
	Total
	0
	-39.778
	


It is noticed that WESCO had overdrawn substantially due to under drawl of OA scheduled quantum by Vedanta Ltd during the month.
[Action: SLDC/ Discoms]
D.2: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl. No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220/132 kV, 100 MVA, Auto- 1 at Duburi
	Main tank severely damaged
	April-2018

	2
	220/132kV, 100MVA  Auto-2  at Bhadrak
	Fire hazard on 31.05.2017
	April-2018

	3
	220/132 kV, 100 MVA Auto-1 at Chandaka
	Oil filtration since 05.02.2018 
	March-2018


CGM (O&M) may update the progress.

D.3: Communication issues 
The status of data communication from CGPs as deliberated in the last meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	3
	M/s Rohit Ferrotech
	PLCC established and inspection by Telecom Engineers completed.  Database has already been prepared by OPTCL.    

	4
	VISA
	New RTU installed. Testing to be done.

	5
	Paradeep
	Already integrated.

	6
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 118th PSOC meeting, GCC stated that a case will be filed against NINL, IRE & Rohit Ferrotech for non compliance of the data communication provision.

Deliberations in the meeting
It was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. SLDC stated that RLDC is not getting the GMR-Meramundali line flow data. CGM (Telecom) has assured to investigate the issue.
GMR Issue

	GMR on line data is available at SLDC but not available directly to ERLDC. GMR entrusted the work on Powergrid.


[Action: GCC / RT&C/ Telecom]
D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
Deliberations in the meeting

IT stated that Parameters of 16 Nos meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
[Action: O&M / SLDC / IT]
D.5: Software for Deviation charge billing.

Hon’ble OERC may notify “Intra State Deviation settlement and related matters” Regulation at any time. For implementation of the regulation, required software for Deviation Charge billing need to be developed and tested. CGM (IT) may take necessary steps for development of the software.

As decided a committee has been constituted for development of the software in house. The work is in progress. 

In the 117th PSOC meeting IT stated that the software will be ready within a week time.
In the 118th PSOC meeting IT stated that the format is being revised after changing of schedule.

Deliberations in the meeting
IT stated that modification of program is under process.

[Action: IT / SLDC]
D.6.DISCOM Issues

CESU

1. Connectivity of Ransingpur sub-station with Argul for stand by supply for Ransinghpur (connected to Chandaka S/S) from which AIIMs is availing power supply.
2. Wide mismatch of actual drawal and SCADA display data to the tune of +115 MW to -117 MW.
Deliberations in the meeting

It was decided that CESU shall discuss their requirement with O&M.
[Action: CESU / O&M]
WESCO Agenda
Deduction of Station Transformer loss from BSP bill of Discoms.

Deliberations in the meeting

O&M stated that Discoms may install meters in the primary side of Station transformer. Further the Discoms may discuss the issue with Gridco separately.  
[Action: Gridco / Discoms]
D.7: Rectification / Replacement of Defective Meters at different interface points.

A list of defective meters indicating the defects has been placed in the 116th PSOC meeting wherein OPTCL was requested to take necessary action for checking CT / PT and early replacement of these meters wherever required. O&M proposed to convene a meeting to discuss the issue. The meeting is yet to be convened.

Deliberations in the meeting
O&M stated that a meeting will be convened with Secure Meters and SLDC to discuss the issue.

[Action: O&M / SLDC]

PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by June’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by April’2018.

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	March’18

	4
	400/220 kV, 2x315 MVA Lapanga S/S
	June’18

	5
	220/33 kV, 2x20 MVA Baliguda S/S
	December’18

	6
	220/33 kV, 2x20 MVA Kalimela S/S
	December’18

	7
	220/33 kV, 2x20 MVA Kasipur S/S
	April’18

	8
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	May’18

	9
	220/33 kV, 2x20 MVA Narasinghpur S/S
	June’18

	10
	220/132 /33 kV, 2x100 MVA Aska S/S
	December’18

	11
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	Charged during March’18

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	December’18

	13
	220/132/33 kV Jayapatana S/S(320 MVA)
	December’18

	14
	220/132 kV Pratapsasan S/S(320 MVA)
	March’19

	15
	220/132 kV Kesinga S/S (320 MVA)
	June’18

	16
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	June’18

	17
	132/33 kV Ghense S/S
	March’18

	18
	132/33 kV Dhenkikote S/S 
	Charged on 24.02.2018

	19
	132/33 kV Betanati S/S
	March’18

	20
	132/33 kV Kantabanji S/S
	Charged on 28.02.18 

	21
	132/33 kV R.Udyagiri S/S
	July’18

	22
	132/33 kV Chikiti S/S
	August’18

	23
	132/33 kV Athagarh S/S
	April’18


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. WESCO may make necessary takeoff arrangement from the newly commissioned 220/132/33 kV Bargarh S/S.
[Action: CGM (Construction) / DISCOMs]
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC

SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators, the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the 117th PSOC meeting, it was decided that CGM (O&M), OPTCL may direct the E & MR Division, Burla to take up the work.

In the 118th PSOC meeting Sr. G.M, EHT (O&M) Zone-II assured to install the meters soon.

Deliberatons in the meeting
O&M stated that Ib TPS may deposit the required amount to release meters (for check meter).

[Action: OPTCL / IB TPS]    
E.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same. Another meeting was proposed to be convened in the month of August’17 to finalize the mechanism of data communication. In the 113th PSOC meeting, it was decided that GRIDCO will take follow up action with all the RE generators to provide real time generation data to SLDC. ERLDC has reminded again to intimate the status.   

A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.

In the 116th PSOC meeting, CGM (Telecom) stated that the solar projects need to pay the SCADA integration charges for display of the data through SCADA.

In the 117th PSOC meeting CGM (Telecom) stated that for pilot project the integration charges may not be required. The Agencies may be asked to proceed with their project.

In the 118th PSOC meeting GRIDCO state that MoM has already been made for 2 Nos. pilot projects and work will be started soon.
Deliberations in the meeting
It was decided that SLDC shall write a letter to Gridco to intimate the status for deliberations in the OCC. Gridco may explore for early completion of the pilot project.

[Action: SLDC / GRIDCO / Telecom]
E.4: Planned outage of 400 kV transmission elements and Inter-State tie lines.

As decided in the OCC meeting that the consolidated planned outage program for all 400 kV lines and Inter-State tie lines shall have be submitted to ERPC for approval in the monthly OCC meeting. The has also been indicated in the procedure at item No C.11 above. CGM (O&M) may please intimate all the GM in charge of (O&M) Circles to prepare the monthly outage programe if any and forward to SLDC for including in the OCC agenda of the State.

Deliberations in the meeting
CGM (O&M) agreed to instruct the field S/Ss to follow the guide line for planned shutdown. 
[Action: CGM (O&M/ SLDC) 

E.5: Disturbance at Tarkera Grid S/S- Interruption of power supply to RSP-Agenda by RSP
On 12th March, 2018, 22:39 Hrs: Tarkera Grid s/s - Auto Tr-4 'R' Phase new 220kV CT of GE make failed within 5 Hrs of commissioning leading to very heavy voltage dip, Islanding of our Power Plants & their units tripping due to load collapsing.

This was a repetition of new CT failure at Tarkera Grid. On 14-Nov-17 also, Auto Tr-2, R- Ph new CT had failed at 00:07 Hrs. leading to wide spread power failure & related disturbance.

In both the incidences, RSP lost almost 14 Hrs worth of production apart from shock to equipments.

Deliberations in the meeting

O&M stated that they will discuss with GE to ascertain the reasons of CT failure.
[Action: O&M]

E.6: Major Events in the month of February’18
09.02.18: Podagada 132/33 kV, 1x12.5 S/S charged

24.02.18: Dhenkikote 132/33 kV, 1x20 MVA kV S/S charged with radial feeder from Karanjia.

28.02.18: Kantabanji 132/33 kV, 1x40 MVA S/S & Traction feeder idle charged with radial feeder from Kharior S/S.

E.7: Important Grid Incidences during the month of February’18.
Important Grid incidents during the month was reviewed. There was only one incident during the month. 

[Action: O&M]
E.8: Outage of major transmission Elements during the month of February’18. (above 10 hrs).
Outage of major transmission elements above 10 hours during the month was reviewed. There was only one outage during the month. 

[Action: O&M]
E.9:  Review of Outage Program of State Generators / Transmission elements for the month of Apr’18:
Tentative Outage programme for State Generators for the month of April’2018 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 2

# 5

# 6
	09.02.18 to 30.04.18
25.10.16 to continue

16.10.15 to continue
	Shaft seal problem

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to continue
	Under R,M & U

	3
	Balimela
	# 1

# 2

# 7
	05.08.16 to continue

20.11.17 to continue

19.03.18 to 18.04.18
	Under R,M & U

Programming for R&M

Governor problem/Breaker replacement 


Deliberations in the meeting

SLDC stated that shutdown of Rengali and Upper Kolab to be deferred due to power shortage to meet the peak requirement. 

[Action: OHPC / SLDC] 
E.10: Generation Program for the month of April’18.
Generation schedule for the month of April’18 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.03.17
	Reservoir Level as on 01.03.18
	MDDL
	High Flood    Reservoir Level

	
	Apr’18
(1st fortnight)
	Apr’18
(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	45
	45
	622.04 ft 
	 620.97 ft
	590 ft.
	630 ft.

	HPS-II, Chiplima
	35
	35
	-
	-
	-
	-

	Balimela
	240
	240
	1496.40 ft 
	1458.70 ft
	1440 ft.
	1516 ft.

	Rengali
	120
	120
	121.74 mtr
	121.64 mtr
	109.72mtr
	123.5 mtr.

	U.Kolab
	60
	60
	854.88 mtr mt
	852.00 mtr
	844 mtr 
	858 mtr.

	U. Indravati
	250
	250
	636.88 mtr
	634.06 mtr mt
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2729.45 ft 
	2744.20 ft
	2685 ft.
	2750 ft.

	TOTAL
	780
	780
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

OHPC / SLDC may deliberate & Members may discuss. 
E.11: Anticipated power generation and demand for the month of Apr’2018.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1100
	1350

	2
	WESCO
	1100
	1250

	3
	NESCO
	750
	950

	4
	SOUTHCO
	450
	570

	6
	Total Discom
	3400
	4120

	
	System Loss & others
	170
	200

	
	Total Demand
	3570
	4320

	Availability
	
	

	1
	Hydro
	800
	1350

	2
	State Thermal
	770
	770

	3
	IPP, small hydro &RE
	650
	650

	4
	ISGS share (including purchase)
	1100
	1300

	5
	CGP support (OA)
	250
	250

	6
	Total availability
	3570
	4320

	7
	Surplus / Deficit
	0
	0


Members may discuss.

PART F: OTHER ISSUES

Additional Agenda
F.1 Payment of Energy Charges and Deviation charges. - GMR
GMR stated that they are paying Deviation charge to Gridco while drawing power from the grid for startup purpose and Energy charges to CESU for such drawal as a consumer of CESU. 

Deliberations in the meeting

It was decided that GMR may raise the issue before Gridco, which can be sorted out through a discussion with CESU, Gridco and GMR.  

[Action: GMR]

 F.2 Time drifting between main and check meters- JSPL

JSPL stated that there is a time drifting between main and check meters installed in their feeders.

Deliberations in the meeting

O&M stated that GPS synchronization of all meters will be taken up by OPTCL to resolve such issues.

[Action: O&M / JSPL]

 F.3 Isolation of 220 kV Upper Sileru-Balimela line- SLDC

SLDC stated that 220 kV Upper Sileru-Balimela line was idle charged from Upper Sileru end. Due to bursting of LA the line is isolated from Sileru end. If this will continue, the conductor may be stolen by miscreants at any time.
Deliberations in the meeting

It was proposed that till installation of LA at Sileru end, the line shall be kept charged from Balimela end up to the last dead end tower by removing jumpers towards Sileru end.
[ Action: Sr.G.M (O&M), Zone-I]

F.4:  Date and Venue of the next (120th) PSOC meeting.

[image: image8.png]119th Power System Operational Co-ordination Committee Meeting
[ At 11:00 A.M. on 23.03.2018]
[At PTC, Chandaka, Bhubaneswar]

= Name Designation | Organisation|  Mobile No. E-mail Address | Signature
1 |8k, Sohaot comip)| op7el | 942817917 G e
2 | B Cameory ComlTeks) 0PTCL | AYBFAOFIAN ogm A Pt g 4o %
3| Pk Mishes cLp Sioe TUIFGUTYGu2 |elephoismesifmisn, «L,
4 | Cmecity Jho |5 60 | o= | qa38907903 4
’ Dot SO0 opTCL | 9uds909te) |ete shise vp: 'y
6 fdﬁ chevdad T 5 - 25907220 qz,r”w’l«m]akjma . M
o hepevn  [Headon o) hl < et AN
AT T S T 7 T
s L7 M, Bty p s Dam L ern(C |75 Yg hovis - m‘f W «2}(9
9 |80 Pasolar | 5287 | stipe |723550 sow [P E Vo
vl s < Bhl |y owpe |[PEEITS e/l
1 M»K_Bjéu\l;\’ i&"\z)';'g;’ OhpC 722880 0235" %MLLUM&%@;J’@: m
12 [P PG, [Mewge | oMPe ”\HSWIGSWLM»‘"Y‘“’““% N
s Vs paM | Tl [aqss250074 vkzi:'z%ﬁ-gm WA —
AT = chand?
14 —T A CHANDRE | G M TSP [ TIRYY2SS6 iﬁ\%ﬁane';&@ E
i | Skevvboa [§am [ BPR 99%0%4202%%%55% Clage -
2 = S
s [R K shah | paM)| ReP [gRoseemsy S8 77a0E -«
17 | T Tayapey Evesg | Srcttts | qumrs £l a0 Jmmé’m“w R\
18 |S. 18 Poka Meomcter | WESCD | qaz7es7aer [TRTMO o
w | B K Sade | Gm |wESG qf/%»za{ﬁ/i poraths naro 4]
. ffzﬂfa ] -
20 fKMWWFW A OPh e 9338715401 /ﬁ‘ mmf AuaA/T/qu_
a [farsnesmtndit] gy IVESCO Tpussaocorg w»mméf@,“ D ppines
2P Kpad |om  |okSy | 9438(AH ¢h| abt e
5 | RoMichon| A |opTel |guzst07305| GRS | o
u ok Do [HM | 0P [Rassqo 7k e do "y
25 | Madholodensahlo Dam | GRIDG (42428 B e Q&f”c“;,L M-S&
% SabendRIT  [6m @rag 0Pl |943g90809¢. clsdpacoaron | Jolo
7 [T | & Qe | amreaoiho Qickydy,
2 D W Do Gm Grdeo QA8 07D E m





[image: image9.png];L'. Name Designation | Organisation Mobile No. E-mail Address Signature

P Ny ( bm Dam 1l 2692 9#0] }Jgiﬁﬁﬁ%—ﬂqé .
30 |<4c‘/‘\/ar%4 Diro(Fin| coESco 9)737’0_8—7053 K woct 2000 € ko ol @
30| L Lok AamE) pom | M3 TOS] | lesusabn @b DO |
2 (MK Panda hen Velpsde [areracprer Pofie el 16D

3 |farihovtn Lot A | GIMR | asygzcssyo | BEHS KT iy
34 | Connih ©, Dohor= bu(lc) | oftel | U4z8A0725 L [k scberem@orici e s 9»,

P | Boradphh kusotolrooguiens | 1D | agazoeoaet A Srotvsosss@raddneten  Liave
| bufale gony | M ste | qyagqarvas

7 Kby o A1 | Gt o008 bulineilopmp i o S
38

39

40

41

4

43

44

45

46

47

43

49

50 N

51

52

53

54

55





