[image: image1.jpg]QAR QIS QR 6YNEI 697

OFFICE OF THE CHIEF LOAD DESPATCHER,SLDC
ODISHA POWER TRANSMISSION CORPORATION LIMITED

; cL GRIDCO Colony, P.0.-Mancheswar Rly. Colony, Bhubaneswar-751017, FAX-0674- 2748509
I Lifeline of Odi .)l CIN — U401020R20045GC007553

No-SGM (PS)-PL-15/2017/  9U &% Dated:)g.08.2018

From:

The Chief Load Despatcher
SLDC, OPTCL, Bhubaneswar-17.

To:
As per distribution list

Sub: Minutes of 123" PSOC meeting held on 28.07.2018 at PTC, Chandaka

Sir,
Please find enclosed herewith the minutes of 123™ Power System Operational
Co-ordination meeting held on 28.07.2018 at PTC, Chandaka, Bhubaneswar.

This is for your information & necessary action.

Yours faithfully;

Encl: As above

X
Chief Load ]ﬁ%atcher,
SLDC, OPTCL

Copy along with enclosures forwarded to the Executive Assistant to CMD, Gridco / OPTCL
for kind information of CMD.




Distribution list

1. The Director (Commercial), Gridco, Bhubaneswar

2. The Director (Operation), OPTCL, Bhubaneswar

3. The Director (Projects), OPTCL, Bhubaneswar

4. The Director (Operation), OHPC, Bhubaneswar

5. The CGM (O&M), OPTCL, Bhubaneswar.

6. The CGM (Const.), OPTCL, Bhubaneswar.

7. The Sr. G. M. (RT&C), OPTCL, Bhubaneswar.

8. The CGM (PP), GRIDCO, Bhubaneswar.

9. The CGM (IT), OPTCL, Bhubaneswar.

10. The CGM (Telecom), OPTCL, Bhubaneswar.

11. The Sr. G. M. (Const)-I, OPTCL, Bhubaneswar.

12. The C.G.M. (Const), OPTCL, Sambalpur.

13. The Sr. G.M (CPC), OPTCL, Bhubaneswar.

14. The Sr. G.M (CP), OPTCL, Bhubaneswar.

15. The Sr. G.M. (O&M), Zone-I, Narendrapur 

16. The Sr. G.M. (O&M), Zone-II, Meramundali.

17. The CEO, CESU, Bhubaneswar.

18. The A.O., WESCO, Burla

19. The A.O., NESCO, Balasore

20. The A.O., SOUTHCO, Berhampur.

21. The Member Secretary (GCC), OPTCL.

22. The ED, Power Grid Corporation of India, Bhubaneswar.

23. The Sr. G.M. (El.), BHEP, Balimela

24. The A.G.M. (El.), CHEP, Chiplima

25. The Sr. G.M. (El.), UIHEP, Mukhiguda

26. The Sr. G.M. (El.), RHEP, Rengali

27. The D.G.M. (El.), HHEP, Burla

28. The D.G.M. (El.), UKHEP, Bariniput, Koraput

29. The S.E. (O&M), Machhakund

30. The DGM (Elect.), IbTPS, OPGC, Banharpali.

31. The Vice President (O), IMFA, Choudwar.

32. The D.G.M. (O&M), NTPC (TTPS), Talcher.

33. The AGM (Elect.), JINDAL Stainless Ltd., Duburi

34. The G.M, HINDALCO, Hirakud.

35. The G.M.CPP, NALCO, Angul.

36. The Director, M/s. Jindal Steel & Power Ltd., Angul

37. The AVP-Vedanta Ltd (IPP), Jharsuguda

38. The G.M, Vedanta Ltd (CGP), Jharsuguda.

39. The DGM (Power Distribution), RSP, Rourkela.

40. Joint President, Aditya Aluminium Ltd., Lapanga, Sambalpur

41. The G.M. (Elect.),  Bhusan Steel Limited. Meramundali

42. The G.M. (Elect.), Bhusan Power & Steel Ltd, Budhipadar.
43. The G.M. (Elect.), IFFCO Limited.

44. Director & COO, GMR Kamalanga Energy Limited, Satyanagar, Bhubaneswar.

45. The CEO, Bhubaneswar Power Pvt. Ltd, IRC Village, Nayapalli, Bhubaneswar.

46. M/S Tata Power & Steel Ltd., Kalinganagar
Odisha Power Transmission Corporation Ltd. Bhubaneswar.


Minutes of 123rd PSOC meeting held on 28.07.2018 at PTC, Chandaka, BBSR
List of participants is at Annexure.

CLD, SLDC welcomed all the members to the 123rdrd PSOC meeting. In his welcome address, he highlighted the system performance for the month of June’2018 and overall power scenario of the State. He also emphasized on the power drawal, made by all the Discoms during the month. 
G.M. (PP), GRIDCO took the agenda items for discussion.
The review proceeded as follows: 
1: Confirmation of minutes of 122nd PSOC meeting held on 25.06.2018
The minutes of meeting was circulated vide letter No. SGM (PS)-PL-15/2017/1277(47) dated 12.07.2018 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting:
The minutes of 122rd PSOC meeting was confirmed. 
PART B : SYSTEM PERFORMANCE
B1: Review of Grid Performance for the month of June’2018.
(A)  Frequency 

It was noticed that, during the month of June’18, 71.44 % of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 69.25 % during the month of  May’18. The maximum and minimum System frequency during the month was 50.16 Hz & 49.68 Hz respectively.
In the 122nd PSOC meeting SLDC stated that the frequency profile of SLDC is not matching with that of ELDC frequency data. Telecom was requested to enquire the source from which ERLDC is collecting the frequency and do the needful. Sr.GM Telecom stated that adoption of frequency acquisition from ERDL reference point may create problem of resetting at the time of link failure. However adoption of PMU frequency can resolve the problem.

[Action: Telecom / SLDC]  
 (B)  Grid demand 

Grid demand for the month of  June’18 was reviewed. The average consumption during the month was 3455 MW. The maximum System demand of 4729 MW occurred on 01.06.18 at 02:00 Hrs and minimum demand of 2173 MW occurred on 29.06.18 at 14:00 Hrs. 
Deliberation in the meeting

It is observed that the average demand during the month of  June’ 18 has been decreased by 343 MW and peak demand  was increased by 37 MW from that of May’18. The average demand during the month has increased by 304 MW in comparison to May’17. Due to change of weather condition and power import by Vedanta Ltd through Open Access transaction, the average demand has increased during the month.
 (C)  Voltage Profile of important Sub Stations in OPTCL System during the month of June’18.

The Voltage profile at different 220 kV buses in OPTCL system during the month of  June’18 was reviewed. 
The maximum Voltage of 239.13  kV occurred at Bhadrak 220 kV bus, while Paredeep  220 kV bus has experienced the minimum Voltage of 203.91 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Meramundali, Mendhasal  and New Duburi bus during the month of June 2018 has been reviewed. 
Deliberation in the meeting:
SLDC stated that, Maximum Voltage at Bhadrak 220 kV bus may be due to some transient incident. 








 [Action: SLDC]
(D) Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of June’18.

Auto loading of all 220 kV S/Ss during the month of June’18 was reviewed. 
(E) DISCOM Drawal during the month of June’18 
The schedule and actual energy drawal by Discoms for the month of June’18 was reviewed. 
Deliberation in the meeting:
It was noticed that all the Discoms have drawn their respective scheduled energy with marginal deviation.

[Action: DISCOMs] 
(F) Energy Generation / import during the month of June’18 
Energy generation and exchange during the month of  June’18 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2487.390 MU. 
Deliberations in the meeting
The energy demand has been decreased due change in weather condition. 
(G) Drawal of Machhakund Power during the month of June’18
The drawal of Machhakund power during the month of June’18 was 19.692 MU, against AP drawal of 21.635 MU. 
Deliberations in the meeting

It was deliberated that the takeoff arrangement from Podagada S/S is scheduled to be done on 28.06.2018.
  [Action: Southco]

(H) Under Frequency relay operation in OPTCL System during the month of June’18.

There is no UF Relay operation during the month of June’18 as the frequency had never gone beyond 48.50 Hz. 
(I) Status of Open Access applications during the month of June’2018
Status of Open Access Applications received and disposed by SLDC during the month was reviewed.

Deliberations in the meeting
Total 101 numbers of Short Term / Medium term and Collective transaction applications have been processed by SLDC for according Approval / Consent / NoC during the month. 
PART C – Issues discussed in the 146th  OCC meeting of ERPC held on 15.06.2018

C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

 The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
146th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	30.11.18
	162.5 Cr.


	38.09Cr.
	90% equipment installed and commissioned. Stn Tfr and some measuring instruments are under tendering process.



	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.22 Cr
	Request for 10% grant is to be submitted as agreement has signed
	Tender floated

	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov

2018,

Chiplima

Dec 2018
	22.35 Cr.
	
	Tendering under process

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 


	28-08-17
	
	31.94 Cr
Ested. cost
	
	Appraisal committee recommends for project cost of 30.23 Cr and 27.23 Cr grant by monitoring committee. Tender floated.

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost
	
	Recommendation by  Appraisal committee will be sent to CERC for concurrence.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	20.02.2018  Date of submission 
	
	41.1 Cr

Estt cost
	
	Compliance to TSEG observation submitted.


 [Action: O&M / Telecom/SLDC]

C.2: Automatic Under Frequency Load Shedding

NPC vide letter dated 30 May 2018, informed that considering the grid size and assuming Power Number of 7000, the following two options of AUFLS are proposed.

Option-1

AUFLS scheme with 4 stages of frequency viz 49.2, 49.0, 48.8 & 48.6 Hz

	AUFLS
	Frequency (Hz)
	Load relief in MW

	
	
	NR
	WR
	SR
	ER
	NER
	Total

	Stage-I
	49.2
	3920
	3360
	3170
	1380
	170
	12000

	Stage-II
	49.0
	3950
	3380
	3190
	1380
	170
	12070

	Stage-III
	48.8
	3970
	3400
	3210
	1390
	170
	12140

	Stage-IV
	48.6
	4000
	3430
	3230
	1400
	170
	12230

	
	Total (MW)
	15840
	13570
	12800
	5550
	680
	48440


 Option-2

AUFLS scheme with 4 stages of frequency viz 49.4, 49.2, 49.0 & 48.8 Hz

	AUFLS
	Frequency (Hz)
	Load relief in MW

	
	
	NR
	WR
	SR
	ER
	NER
	Total

	Stage-I
	49.4
	3900
	3340
	3150
	1370
	170
	11930

	Stage-II
	49.2
	3920
	3360
	3170
	1380
	170
	12000

	Stage-III
	49.0
	3950
	3380
	3190
	1380
	170
	12070

	Stage-IV
	48.8
	3970
	3400
	3210
	1390
	170
	12140

	
	Total (MW)
	15740
	13480
	12720
	5520
	680
	48140


In the 122nd PSOC it was decided to adopt the 2nd option. OPTCL may forward their views to ERPC accordingly.

Deliberations in the meeting.

SLDC stated that all the constituents of ERPC have agreed for adopting 2nd option except WB. OPTCL has forward its views to ERPC.
[Action: SLDC / O&M)]

C.3: Shutdown clearance of 400 kV IBEUL – Jharsuguda D/C to start construction of OPGC MGR Corridor under crossing locations 

The issue of time limit extension for diversion works of 3 nos. towers of 400 kV IBEUL – Jharsuguda D/C at 4 nos. crossing locations to facilitate construction works of OPGC MGR Corridor had been revised several times since June, 2017 onwards. Finally, ERPC, on the advice of CEA allowed the extension time limit up to 31.05.2018.  

While OPGC was ready to start the construction works of MGR line from June, 2018 IBEUL reported one extension tower collapsed at location no. 45 on 29.04.2018, which would require 2 months’ time for its restoration. In order to take the stock of the present status of ongoing works of the respective organisations, ERPC convened a Special meeting on 01.06.2018, wherein M/s OPGC pleaded to start the construction works of MGR line by opening of the conductor of the spans at the crossing points. Since the restoration of IBEUL line (under S/D) was not going to take place within 2 months and OPGC is ready to start the works in all respect, OPGC requested shutdown clearance of the line vide letter dated 02/07/2018. 

In view of the facts, ERPC informed concerned utilities to attend the 147th OCC Meeting scheduled to be held on 20.07.2018 to discuss and finalise the issue. 

In the meanwhile an email addressed to OPGC with a copy to ERPC has been received from IBEUL wherein it has been intimated that “IBEUL is under financial stress because of which the Company has been referred to NCLT under section 7 of Insolvency and Bankruptcy Code (IBC) by project lenders. The hearing for the same is scheduled for 16th July 2018 before NCLT, Hyderabad. Under these circumstances, the Company is unable to commit itself to make any financial commitments since all its dues to the creditors will be governed by the provisions of the IBC. Thus completion of balance works of the diversion of the 400 KV IBEUL-SNG DC Line at the four Railway Crossings of OPGC has been held up and IBEUL is in a fix and not in position to make any progress and make any commitment to any authority. However considering the urgency of work of OPGC for commissioning of their expansion project, I would request you to kindly convene a meeting in OPGC office at Bhubaneswar involving your site engineers and IBEUL to resolve the issues.” 

Deliberations in the meeting

O&M stated that IBTPS have already agreed to allow the shutdown.
[Action; IBTPS/ O&M]

C.4: FLEXIBILITY IN GENERATION & SCHEDULING OF THERMAL POWER STATIONS TO REDUCE EMISSIONS-MOP, GOI ORDER 

MoP vide letter No. 23/70/2017-R&R dated 05.04.2018 published a detailed mechanism of allowing Flexibility in Generation and Scheduling of Thermal Power Stations to reduce emissions. Subsequently, CEA vide its letter No. 7/X/VIP/GM/2018/923-27 dated 12.06.2018 requested all RPCs to make necessary changes in Energy Accounting to implement the above mentioned mechanism. 

The concept of flexible utilization of coal as introduced by the Central Govt in year 2016, allows the use of coal within its basket in optimal manner. This avoids unnecessary coal transportation and reduces the power generation cost. In a similar manner, it has been decided by MoP that there should be some flexibility in Generation and Scheduling of Thermal Power Stations so that Discoms are able to meet their RPO without facing any additional financial burden. 

Further, due to large scale integration of Grid connected renewable, which is generally infirm in nature, there is a need for balancing power to maintain security & stability of the Grid. Such balancing has to be done by Discoms and Generators both. This flexibility will provide optimum use of RE by Power Generators and help reduce emissions.  

The issue was discussed in 38th TCC/ERPC Meeting wherein, MS, ERPC informed that a workshop would be arranged at ERPC, Kolkata. 

Accordingly, a workshop is scheduled to be held at ERPC Kolkata on 27.07.2018. 

TCC advised all the constituents to nominate concern officers for detailed deliberation. Based on the discussion in the workshop, ERPC Secretariat, if necessary, would write a letter to CEA highlighting the issues needed to be addressed before implementation of the said mechanism. 

 Deliberations in the meeting

SLDC representative has attended the meeting.
C.5: Implementation of Web based PSP report in ERLDC 

ERLDC is currently preparing PSP report on daily basis which contains ISGS/IPP schedule & actual generated energy, inter-regional tie line energy exchange, energy consumption of states and energy generated by state generators (including DVC), voltages of important substations etc. The content in the report is being used by MOP, States and various other agencies for data compilation and preparation of other reports. This report is prepared during night shift hours as per the energy data submitted by all ISGS/IPPs, states, transmission licensees to ERLDC. Generally ERLDC received data from all users by 02:00 Hrs of night in different reporting formats(Ex-cell, Word, Mail, Over phone etc..) and prepared PSP report by 0400 hrswhich is uploaded in ERLDC website and sent to MOP.  However, due to submission of data in different formats by the users, it is very difficult compile and validate such data during night hours before preparation of the PSP report. To improvise the data reporting system, a new web based PSP reporting portal has been developed, wherein generators, transmission licensees& states can log-in to the portal and submit their energy data. Beta version of this software is already installed at ERLDC and parallel testing is going on. The new PSP web based portal will be operationalized with effect from 00:00 hrs of 01st August, 2018. In this regard all generators, transmission licensees& states are requested to nominate one nodal person to ERLDC in erldcso@posoco.in, who will co-ordinate with ERLDC nodal person and their nightshift executives to fill energy data. In the meantime it is requested to all generators, transmission licensees& states to instruct their night shift operators to enter the energy data using their user credential in ERLDC PSP web portal. Individual user id and password will be shared to respective nodal co-coordinators / control room through mail. 

Nodal Persons from ERLDC side: 

 
1. Shri Tushar Ranjan Mohapatra - (9433041873)
2. Shri Chandan Mallick – (9007059660) 
Deliberations in the meeting
SLDC stated that implementation of the above operation will be started from 1st August’2018. It was decided that SLDC shall intimate to the above to OHPC/ OPGC/ TTPS.

[Action: SLDC/OHPC/IbTPS/TTPS] 

C.6: Two days’ Worhshop at Upper Kolab /Balimele, Odisha 

In 37th ERPC Meeting, it was decided to organise a two days’ workshop at   Upper Kolab / Balimela, Odisha covering emerging issues in the Power Sector (1st day) and Black Start & Restoration Procedure (2nd day). OPGC, OHPC, GRIDCO, DISCOMS of Odisha, TSTPS, Powergrid Odisha etc. would be invited as participants for the above workshop. 

 Members may note.  

C.7: Agenda point related to reporting of grid events by users, STU, CTU and SLDC to RLDC 

As per IEGC section 5.9.4 (b) and 5.9.6 (a), all users, STU, CTU and SLDC are to send written report to RLDC for the events notified by IEGC section 5.9.5. in the format of draft written report as per IEGC section 5.9.6 (c). All users, STU, CTU and SLDC are requested to send flash report in given format to erldcprotection@posoco.in/ erldccr@posoco.in/ erpcprotection@gmail.com followed by events mentioned in IEGC section 5.9.5. 
Deliberations in the meeting

It was decided that the events shall be reported to ERLDC on real time basis by STU and SLDC. 
[Action: O&M / SLDC]  

C.8: Agenda point related to load forecasting by SLDC   

For better grid management and shutdown planning, RLDCs needs to do short term load forecasting. Accuracy and effectiveness of load forecasting depend on input data. As per current practice, day ahead load forecasting is being done at ERLDC by analysing trend previous days demand. However, for further tuning and better accuracy of load forecasting result, demand estimation from SLDCs are to be done at their end and same need to be shared with ERLDC for estimation of Eastern Region demand. 
Deliberations in the meeting

SLDC stated that the State demand forecasting is being done as per the drawal forecast by all the DISCOMs. The DISCOMs were requested to share their forecast methodology for intimation to ERLDC.
[Action: SLDC  / All DISCOMs] 

C.9: Status of Implementation of islanding schemes in ER- Islanding scheme at IbTPS- OPGC 

The islanding scheme was discussed in 68th PCC Meeting held on 18-06-2018.  PCC opined that the draft scheme submitted by Odisha was three years old and the draft scheme is needed to be reviewed with existing network configuration.   

PCC decided to discuss the islanding scheme in next PCC Meeting and advised OPTCL to submit all the relevant details to ERPC and ERLDC. 

The islanding scheme has already deliberated in the OCC meeting.
C.10: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************

The latest status along with proposed logic as follows:
[image: image2.emf]
[image: image3.emf]
In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 122nd PSOC SLDC stated that the tendering will be done by end of July’2018.

Deliberations in the meeting
SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval

[Action: SLDC]
C.11: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 123th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by Dec’18. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by Dec’18.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Keonjhar S/S (220/33 kV) by Aug’18.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	December 2018 


C.12: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

The activity of the preparation of Crisis Management Plan for countering the cyber-attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA. 

In 142nd OCC, ERLDC informed that, in line with Enquiry Committee Recommendation, cyber security audit is being conducted on regular basis for SCADA system installed at ERLDC and SLDC as well but cyber security audit for telecom infrastructure installed in Eastern Region is not being carried out.  

OCC advised all the constituents to conduct the cyber security audit on telecom infrastructure installed in Eastern Region. It is further advised that compliance / mitigation of the points observed during the audit should also be completed for improvement of the telecom infrastructure in ER. 

In 37th TCC meeting, it was decided that a workshop would be conducted by CEA at ERPC for further benefit of ER Constituents.  

In 144th OCC, ERLDC informed that they have already conducted a workshop with the help of NPTI, Durgapur on 21st March 2018. 

A workshop on cyber security was conducted by CEA at ERPC, Kolkataon 09-05-2018.  

As suggested by CEA, a format would be circulated among ER constituents for furnishing the information of their respective systems for discussion in OCC Meeting. The format is enclosed at Annexure-E2. 

OCC advised all the constituents to submit the information to ERPC as per Annexure-E2.  

In the 122nd PSOC meeting CGM (IT) stated that Audit report is yet to be received. Audit for the next FY will be commenced from July’18.

Deliberations in the meeting
IT stated that the Audit report has already been received. After depositing the required charges, audit for FY 2018-19 will be started. It was suggested that IT shall furnish the information as sought by ERPC in the required format.  

 [Action: CGM (IT)]
C.13: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.  

As per the information received from the constituents the following generators certified with IS 18001:  

 All NTPC stations in Eastern Region  

 Teesta, NHPC 

 All OHPC generating units  

 All CESC generating units  

 All units of WBPDCL 

 DGPC units 

In the 117th PSOC meeting CGM (O&M) stated that draft project report for Mendhasal S/S has been submitted to BIS. The report will be approved in the meeting to be conducted by them.

In the 122nd PSOC meeting CGM (O&M) stated that Audit team is expected soon.

Deliberations in the meeting

CGM (O&M) stated that the report is yet to be received.
     [Action: CGM (O&M)]
C.14: Status of Disturbance Recorder, Standalone Event Logger and Time Synchronization equipment.   

The status of DR/EL and GPS as updated in previous OCCs is enclosed at Annexure-E.4. 

Constituents are also requested to furnish their list of new DR/EL which are not included in the list. 

Deliberations in the meeting

O&M stated that since the S/Ss will be covered under automation scheme. These equipment are not required. SLDC may deliberate in the OCC.
[Action: SLDC]
C.15: Data for GEOSPATIAL energy portal of Neeti Aayog-CEA
NITI Aayog is developing a user friendly GIS based Energy Map of India, which would provide true locations of all energy resources in India including power plants, coal and oil reserves, transmission lines etc.  

CEA sought the information of name, voltage level, capacity, longitude and latitude of 33kV and 66 kV substations and lines.  

The information may be shared with CEA vide email: cedpd-cea@gov.in.  

All Discoms are requested to submit the above data to CEA with a copy to SLDC for forwarding to ERPC.                                                                                        

In the 122nd PSOC meeting it was deliberated that for submission of line data, detail mapping of the line is required, which involve a lot of expenditure. However, the Discoms may furnish the S/S data in 1st phase. SLDC may write to all Discoms in this regard.

Deliberations in the meeting

DISCOMs stated that they have started the work

[Action: All DISCOMs]
C.16: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2018-19 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2018
	Done on 08.06.2018
	Last week of January 2019
	

	3
	Rengali
	2nd week of June 2018
	August’18
	Last week of November 2018
	

	4
	U. Indravati
	3rd week of June 2018
	August’18
	2nd week of February 2019
	

	6
	Balimela
	3rd week of October  2018
	
	1st week of March 2019
	

	9
	Burla
	Last week of June 2018
	Done on 07.06.2018
	Last week of February 2019
	


Deliberations in the meeting

SLDC stated that mock black start exercise for Balimela will be done at the time of workshop conducted by ERPC at Upper Kolab/ Balimela.

[Action: OHPC / SLDC]
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of June’18:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	-1.98911
	-0.2379

	2
	WESCO
	0
	2.31564
	0.3614

	3
	NESCO
	0
	-3.6404
	-0.7453

	4
	SOUTHCO
	0
	-1.80285
	-0.5692

	
	Total
	0
	-5.11672
	


It is noticed that CESU, NESCO & SOUTHCO have under drawn while WESCO has over drawn during the month. 

Deliberations in the meeting

All the DISCOMs have maintained their energy drawal schedule with marginal deviation.

[Action: SLDC/ Discoms]
D.2: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl. No
	Name of transmission element
	Reason of outage
	Probable date of revival

	2
	220/132kV, 100MVA  Auto-2  at Bhadrak
	Fire hazard on 31.05.2017
	Aug-2018


CGM (O&M) may update the progress.

D.3: Communication issues 
The status of data communication from CGPs as deliberated in the 120th PSOC meeting meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	2
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. 
In the 121st PSOC meeting G.M. (RT&C) stated that they have raised certain queries regarding the provision of providing data communication facilities to SLDC by the CGP / Industries. SLDC stated that the “Procedure on Communication and Data Transmission”  approved by Hon’ble OERC  vide orders, dated 23.09.2011 passed in case Nos. 41, 42 and 51/2011 followed by corrigendum order issued in letter No.2243, dated 01.12.201, published in the Odisha Gazette No. 485 Dated 29th March 2012 was circulated by RT&C wing of OPTCL vide letter No. R&T-REGN-08/2011/198 (8) dated 19.04.2012. RT&C may refer the said letter wherein the provisions have been clearly mentioned.  Also RTC may take necessary initiative for filing Petition before the OERC.

In the 122nd PSOC meeting GCC stated that Telecom have forwarded a list of 8 Nos. of CGP/Industries who have not complied the data communication facilities. It was suggested that RT&C may file a case before the OERC.

Deliberations in the meeting

RT&C have sought some information from Telecom wing which will be intimated. NALCO stated that due to problem in their internal communication system, data communication to SLDC is being interrupted.
[Action: GCC / RT&C/ Telecom]
D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 119th PSOC meeting IT stated that Parameters of 16 Nos meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
In the 120th PSOC meeting IT stated that M/s Secure Meter is not responding to them. It was decided that O&M shall convene a meeting with M/s Secure meters to resolve the issue.  
In the 121st PSOC meeting it was decided that SLDC shall write CPC and OPTCL to convene a meeting with TCS and Secure meters to discuss the issue. 
In the 122nd PSOC meeting IT stated that they will study 2 Nos of sample meters.

Deliberations in the meeting

IT stated that out of 840 Nos interface meters connected with AMI, 750 Nos are reporting at present. The newly replaced meters are not reporting. 2 Nos. of meters has sent to M/s SECURE meters for study.

[Action: IT/ OPTCL/ SLDC]
D.5: Web based drawal / generation scheduling.

In the 111th PSOC meeting it was decided that from 1st August 2017 the schedule submitted through web portal will be considered. The web based schedule will be implemented for TTPS and Ib TPS from 1st September’2017. 
At present all State thermal generating stations including IPPs & CGPs are furnishing their schedule through web portal.

The following fetchers need to be incorporated in the software: 

1. Provisions for acceptance of backing down schedule for past block.

2. Provision for automatic extraction of Power Exchange schedule from the worksheet for incorporation in the schedule of respective Generator / CGP.

3. Navigation between different web pages within the portal

4. Report generation in excel format with down loading provision.
In the 120th PSOC meeting it was decided that SLDC and IT may discuss the issue and resolve.
In the 122nd PSOC meeting SLDC stated that they have discussed the issue with IT and expected to resolve soon.

Deliberations in the meeting

SLDC stated that the work is under progress

[Action: IT/SLDC]
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by Dec’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by Oct’2018.

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	Oct’18

	4
	400/220 kV, 2x315 MVA Lapanga S/S
	Sept’18

	5
	220/33 kV, 2x20 MVA Baliguda S/S
	July’19

	6
	220/33 kV, 2x20 MVA Kalimela S/S
	March’19

	7
	220/33 kV, 2x20 MVA Kasipur S/S
	Oct’18

	8
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	Aug’18

	9
	220/33 kV, 2x20 MVA Narasinghpur S/S
	September’18

	10
	220/132 /33 kV, 2x100 MVA Aska S/S
	March’19

	11
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	Charged during March’18

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’19

	13
	220/132/33 kV Jayapatana S/S(320 MVA)
	March’19

	14
	220/132 kV Pratapsasan S/S(320 MVA)
	Dec’19

	15
	220/132 kV Kesinga S/S (320 MVA)
	December’18

	16
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	September’18

	17
	132/33 kV Ghense S/S
	Charged during April’18

	18
	132/33 kV Dhenkikote S/S 
	Charged on 24.02.2018

	19
	132/33 kV Betanati S/S
	March’19

	20
	132/33 kV Kantabanji S/S
	Charged on 28.02.18 

	21
	132/33 kV R.Udyagiri S/S
	December’18

	22
	132/33 kV Chikiti S/S
	October’18

	23
	132/33 kV Athagarh S/S
	Charged on 31.05.2018


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. 
[Action: CGM (Construction) / DISCOMs]
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC

As per the provision in the Act, SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators will record 15 min block energy injection,   the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the 119th PSOC meeting CGM (O&M) stated that Ib TPS may deposit the required amount to release meters (for check meter).

In the 122nd PSOC meeting Ib TPS stated that this has already been approved by their Authority. The required amount will be deposited soon.

Deliberations in the meeting

O&M stated that the required amount is yet to be deposited by IB TPS. Ib TPS have not sent their representative to the meeting for deliberation.
[Action: O&M / IBTPS]
E.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same.

A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.
M/S Secura Meters Ltd has shown a demo for the pilot project on dated 09.07.2018. However, the data integration with SLDC VPS was not elaborated in the said demo. 
Deliberations in the meeting

Telecom stated that M/S Secure meters could not complete the Demo, as M/S Camptrol requires Rs. 3.5 lacs to allow firewall access to them. M/s Camptrol also interested to take up the work. GRIDCO may allow them for the pilot project. OPTCL may examine for Firewall access to avoid burden to the Solar projects.

[Action: O&M/ GRIDCO/ Telecom]
E.4: Major Events in the month of June’18
24.06.18: 132/33 kV, 12.5 MVA Tfr at Olavar S/S charged. 
E.5: Important Grid Incidences during the month of June’18.
There is no reportable incident occurred during the month.
E.6: Outage of major transmission Elements during the month of June’18. (above 10 hrs).
Outage of major transmission elements above 10 hours was reviewed. The events are due to conductor snapping and CT failure.

[Action: O&M]
E.7:  Review of Outage Program of State Generators / Transmission elements for the month of August’18:

Tentative Outage programme for State Generators for the month of August’2018 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1

# 2

# 5

# 6
	14.03.18 to 31.08.18

25.05.18 to 16.08.18

25.10.16 to continue

16.10.15 to continue
	T&G coupling cover water leakage

Shaft seal problem

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3

# 1

# 2
	15.10.15 to continue

22.07.18 to 30.09.18

22.07.18 to 30.09.18
	Under R,M & U

Flood water inrush to turbine 

Flood water inrush to turbine

	3
	Balimela
	# 1

# 2

# 5
	05.08.16 to continue

20.11.17 to continue

10.08.18 to 25.09.18
	Under R,M & U

Programming for R&M

Annual Maintenance

	4
	Rengali
	# 3
	07.07.18 to 10.08.18
	Fault in 220 kV unit breaker

	5
	Upper Kolab
	# 2
	25.05.17 to continue
	Upstream leakage & intake gate Problem

	6
	U. Indravati
	# 3

# 4
	10.07.18 to 25.08.18

27.06.18 to 25.08.18
	Water leakage in penstock

Annual Maintenance

	5
	TTPS
	# 3
	24.07.18 to 22.08.18
	Annual Maintenance

	6
	Ib TPS
	# 1
	24.07.18 & continuing
	GT bushing oil leakage.


[Action: OHPC / SLDC]
E.8: Generation Program for the month of August’18.
Generation schedule for the month of August’18 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.07.18
	Reservoir Level as on 01.07.17
	MDDL
	High Flood    Reservoir Level

	
	Aug’18
(1st fortnight)
	Aug’18
(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	70
	70
	600.56
	598.52
	590 ft.
	630 ft.

	HPS-II, Chiplima
	0
	0
	-
	-
	-
	-

	Balimela
	250
	250
	1448.00
	1458.30
	1440 ft.
	1516 ft.

	Rengali
	140
	140
	111.11
	110.25
	109.72mtr 
	123.5 mtr.

	U.Kolab
	160
	160
	845.84
	848.47
	844 mtr 
	858 mtr.

	U. Indravati
	250
	250
	627.00
	628.94
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2704.35
	2707.80
	2685 ft.
	2750 ft.

	TOTAL
	900
	900
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

Deliberations in the meeting

SLDC stated that at Chipilima all units are under shutdown and at Burla four nos. of units are under shutdown. OHPC should prepare the implementable generation schedule. Accordingly Burla and Chiplima generation schedules have revised.

[Action: SLDC/OHPC] 
E.9: Anticipated power generation and demand for the month of August’2018.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1050
	1300

	2
	WESCO
	1000
	1150

	3
	NESCO
	750
	950

	4
	SOUTHCO
	350
	450

	6
	Total Discom
	3150
	3850

	
	System Loss & others
	150
	200

	
	Total Demand
	3300
	4050

	Availability
	
	

	1
	Hydro
	900  
	1050

	2
	State Thermal
	700
	700

	3
	IPP, small hydro &RE
	300
	450

	4
	ISGS share (including OA& purchase)
	1100
	1550

	5
	CGP support (OA)
	300
	300

	6
	Total availability
	3300
	4050

	7
	Surplus / Deficit
	0
	0


PART F: OTHER ISSUES

F.1: Commissioning of OPGW between Indravati-Indravati (PG)
Sr. GM (SLDC) stated that in the last OCC meeting ERLDC insisted for commissioning of OPGW between Indravati & Indravati (PG) since the line has been handed over to OPTCL. Telecom may explore for drawal of OPGW between the above two S/Ss. If OPGW is not available with OPTCL the same may be borrowed from PGCIL.

[Action: CGM (Telecom) / O&M]

F.2: Shutdown of 400 kV Meramundali-Vedanta DC line

CGM (Const.) asked shutdown on 400 kV Meramundali- Vedanta DC line on continues basis for making LILO at Lapanga 400 kV bus.   SLDC may examine and allow the shutdown.
[Action: SLDC/ CGM (Const.)] 
F.2:  Date and Venue of the next (124th) PSOC meeting.
Annexure[image: image4.jpg]123rd Power System Operational Co-ordination Committee Meeting
[ At 11:00 A.M. on 28.07.2018]
[At PTC, Chandaka, Bhubaneswar]

j(') Name Designation | Organisation Mobile No. E-mail Address Signature
1|8k Sohe | comlom)| optec | 9438997919 |cm-omod | gy e
2 |N.Co Suas comlt)| opzer | 9438507921 cfywwf—"’?“““"//ﬁiﬂ‘i/
3| Pt Sohi, Comlton)s oprel | FY2890 F77E| e pe o ‘é"
4 | PR Mishea Cub | SLbE | 9u3EUTNID 2l phaishrecridiniin /Z«/
s | Gmaefle, | SGm | scve | gp2s909902 [P e Ty
6 | C Ptregns | Letm | op7e) | aYngnnrter |ae. *?“W:LCW S
T [Pl R T o et | oprel | 342510730 e 5‘"’1@ |
i K |4 /Jé/am [/ / Aaxy T7]2> C\‘”’ U
: M D R52 [Guéw QupG, [massioass o ””’”5‘”»151 ol 35|
B S A PR e o ey £ B
10 S Phee S Bref oI HEP | 73R Lo485|s qB\/C,L(I 75 —
U Ak Pallinodic 6, @ ) 0 Prel [443590 70| bl okpadaalicrt M‘*
2 |AbMbanls | AGM | ol |9 os o | o 670 €t Sl
B AP Mabypates | G SHPC | Fa288hmIs WW@MW i
- Dlwwm@fs* AGM | OhPL | FB2snboorofnpatro obpeg |y BE
% (?r%ﬂ%%fw Mase DGM| SLDC G 4239675490~ sibfvo! Wa
9Pk Nayaw | Dam [T 2uuianis907502 | Tmne 2z
ET e | 1T [AU3890T L [t - SKicghon.
1| A Genapak | Aam | Naleo | qu3rossned | Gsenapatt Qadendo okl
T ) LCO (a5 ) @ :
o | BB P 307 N?ﬁ’ b 507k To0 &E&iﬁx sl pEca
0 | 5. rdm&L\M\ Gmep)| wbsco Ll 3Lre50L0 1Y oernowmdm'ﬂ/ﬂ}iﬂw
2 Dk Rahov | Maaven ) NESOURLE 9Y 26906020 "“w“’mﬂ”ﬂ'“”"@é"yﬁqg G
T
2 ML Bl | D-MEOD | WESD | Sigazssy | ducauessoditned, @
5 |Sk Do ko | 0Pl [943ego72it [eloeiptd o] g,
T ofere  dxpuinlior
5 | R Mishon [ DGy |epTer [PASSSCTRRIET o] Cumtive
ele sl amt |
5 |g A Padee Grfpazo| opter 9433903096 e }L
15K Mooty e GRioen [94289070
7 oo, ggﬂh,z’\'ﬂ\)q GM@na £ D¢ |J4aeqozare | Sl A
w |« Aok (1) | S o | 193850783 | el s bt S,




[image: image5.jpg]Sl

Mobile No. E-mail Address Signatur

N Name Dasignation | Organisation
» | Pk padhy Gy din QL3RI | combt G rahh Y

0 | D.PRar | aom oD |94299079144 mﬁ,ﬁbﬁ;‘/}/
M| € Cad o hom |To CamE 943290%0< ) a!e:unkw@ffg_-

2 | MK Parcdn | 4G et |orprucyany il B el [ @)
3| g 2 Wshra i 9589 0257/ Pl Ry 2

# | Pk Doy aM | 4eTpco

3| 8. K Doy I longh-

% | § 8- Sanwp » M

¥ 5.6 NAYAK  [snaM |aRIDco | quyphousy |ATTIEETTOr | gonagh
38 émbwﬂﬂge»‘ncm D (&) T‘i??‘éﬁa'?“”é?cl‘b*kkgﬁ'ﬁém
39 [P.p. BENERA| DM(EL Q4> &5 eF 212 B~
10

41

2

3

44

45

46

47

43

49

50

51

52

53

54

55





