[image: image1.jpg]QARY TQYC QIR 6INE 69F

OFFICE OF THE CHIEF LOAD DESPATCHER,SLDC

ODISHA POWER TRANSMISSION CORPORATION LIMITED
GRIDCO Colony, P.0.-Mancheswar Rly. Colony, Bhubaneswar-751017, FAX-0674- 2748509

CIN - U401020R20045GC007553

47
No-SGM (PS)-PL-152017/ 59 Dated: 05.01.2019

From:

The Chief Load Despatcher
SLDC, OPTCL, Bhubaneswar-17.

To:

As per distribution list

Sub: Minutes of 128" PSOC meeting held on 18.12.2018 at PTC, Chandaka,
Bhubaneswar.

Sir,

Please find enclosed herewith the minutes of 128" Power System Operational

Co-ordination meeting held on 18.12.2018 at PTC, Chandaka, Bhubaneswar.

This is for your information & necessary action.

Yours faithfully;

Encl: As above
“\1 \

Chief Load De?patcher,
SLDC, OPTCL

Copy along with enclosures forwarded to the Executive Assistant to CMD, Gridco / OPTCL
for kind information of CMD.




Distribution list

1. The Director (Commercial), Gridco, Bhubaneswar

2. The Director (Operation), OPTCL, Bhubaneswar

3. The Director (Projects), OPTCL, Bhubaneswar

4. The Director (Operation), OHPC, Bhubaneswar

5. The CGM (O&M), OPTCL, Bhubaneswar.

6. The CGM (Const.), OPTCL, Bhubaneswar.

7. The Sr. G. M. (RT&C), OPTCL, Bhubaneswar.

8. The CGM (PP), GRIDCO, Bhubaneswar.

9. The CGM (IT), OPTCL, Bhubaneswar.

10. The CGM (Telecom), OPTCL, Bhubaneswar.

11. The Sr. G. M. (Const)-I, OPTCL, Bhubaneswar.

12. The C.G.M. (Const), OPTCL, Sambalpur.

13. The Sr. G.M (CPC), OPTCL, Bhubaneswar.

14. The Sr. G.M (CP), OPTCL, Bhubaneswar.

15. The Sr. G.M. (O&M), Zone-I, Narendrapur 

16. The Sr. G.M. (O&M), Zone-II, Meramundali.

17. The CEO, CESU, Bhubaneswar.

18. The A.O., WESCO, Burla

19. The A.O., NESCO, Balasore

20. The A.O., SOUTHCO, Berhampur.

21. The Member Secretary (GCC), OPTCL.

22. The ED, Power Grid Corporation of India, Bhubaneswar.

23. The Sr. G.M. (El.), BHEP, Balimela

24. The A.G.M. (El.), CHEP, Chiplima

25. The Sr. G.M. (El.), UIHEP, Mukhiguda

26. The Sr. G.M. (El.), RHEP, Rengali

27. The D.G.M. (El.), HHEP, Burla

28. The D.G.M. (El.), UKHEP, Bariniput, Koraput

29. The S.E. (O&M), Machhakund

30. The DGM (Elect.), IbTPS, OPGC, Banharpali.

31. The Vice President (O), IMFA, Choudwar.

32. The D.G.M. (O&M), NTPC (TTPS), Talcher.

33. The AGM (Elect.), JINDAL Stainless Ltd., Duburi

34. The G.M, HINDALCO, Hirakud.

35. The G.M.CPP, NALCO, Angul.

36. The Director, M/s. Jindal Steel & Power Ltd., Angul

37. The AVP-Vedanta Ltd (IPP), Jharsuguda

38. The G.M, Vedanta Ltd (CGP), Jharsuguda.

39. The DGM (Power Distribution), RSP, Rourkela.

40. Joint President, Aditya Aluminium Ltd., Lapanga, Sambalpur

41. The G.M. (Elect.),  Bhusan Steel Limited. Meramundali

42. The G.M. (Elect.), Bhusan Power & Steel Ltd, Budhipadar.
43. The G.M. (Elect.), IFFCO Limited.

44. Director & COO, GMR Kamalanga Energy Limited, Satyanagar, Bhubaneswar.

45. The CEO, Bhubaneswar Power Pvt. Ltd, IRC Village, Nayapalli, Bhubaneswar.

46. M/S Tata Power & Steel Ltd., Kalinganagar
Odisha Power Transmission Corporation Ltd. Bhubaneswar.


Minutes of 128th PSOC meeting held on 18.12.2018 at PTC, Chandaka, BBSR
List of participants is at Annexure.

Chief Load Despatcher, SLDC, OPTCL welcomed all the participants to the 128th Power System Operational Coordination meeting and highlighted the system performance during the month of November’2018 and overall power scenario of the State. He also emphasized on the drawal by all the Discoms during the month. 

Dy.Manager, SLDC took the agenda items for discussion. 

The review proceeded as follows: 
1: Confirmation of minutes of 127th PSOC meeting held on 24.11.2018
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2017/3815(47) dated 10.12.2018 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting:
Since no comments have been received from the members, the minutes of 127th PSOC meeting was confirmed. 
PART B : SYSTEM PERFORMANCE
B1: Review of Grid Performance for the month of November’2018.
(A)  Frequency 

It was noticed that, during the month of November’18, 79.04 % of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 74.06 % during the month of  October’18. The maximum and minimum System frequency during the month was 50.12 Hz & 49.79 Hz respectively.
 (B)  Grid demand 

Grid demand for the month of  November’18 was reviewed. The average consumption during the month was 3632 MW. The maximum System demand of 4522 MW occurred on 08.11.18 at 19:00 Hrs and minimum demand of 2959 MW occurred on 26.11.18 at 03:00 Hrs. 
Deliberation in the meeting

It is observed that the average demand during the month of  November’ 18 has decreased by 598 MW and maximum demand  has decreased by 748 MW in comparison to October’18. The demand has decreased during the month due to change in power import by Vedanta Ltd through Open Access transaction.
 (C) Voltage Profile of important Sub Stations in OPTCL System during the month of Nov’18.
The Voltage profile at different 220 kV buses in OPTCL system during the month of  November’18 was reviewed. 
The maximum Voltage of 237.69  kV occurred at Bhadrak 220 kV bus, while Narendrapur  220 kV bus has experienced the minimum Voltage of 209.75 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Meramundali, Mendhasal  and New Duburi bus during the month of November 2018 was reviewed. 
(D) Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of Nov’18.

Auto loading of all 220 kV S/Ss during the month of Novemberr’18 was reviewed. 
(E) DISCOM Drawal during the month of November’18 
The schedule and actual energy drawal by Discoms for the month of November’18 was reviewed. 
Deliberation in the meeting:
It was noticed that all the DISCOMs have over drawn during the month of November’18. CESU has over drawn 43.769 MU followed by WESCO 66.424 MU, NESCO 32.012 MU & SOUTHCO 43.983 MU. The DISCOMs were requested to predict their drawal in a realistic manner. WESCO stated that due to shut down of RSP CGP unit, their drawal was increased. RSP stated that NSPCL unit of 1x250 MW is expected to be synchronized by end of June’2019.
[Action: DISCOMs] 
(F) Energy Generation / import during the month of November’18 
Energy generation and exchange during the month of November’18 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2615 MU. 
Deliberations in the meeting
The energy demand has been decreased due to reduced power import by Vedanta CGP through Open Access transaction.

(G) Drawal of Machhakund Power during the month of November’18
The drawal of Machhakund power during the month of November’18 was 21.964 MU, against AP drawal of 25.621 MU. 
Deliberations in the meeting

It was noticed that the State’s drawl from Machhakund has reduced since last seven months. Southco may explore for adding of Koraput, Dasmantpur & Kakariguma feeders to Podagada S/S. Representative from SOUTHCO stated that since the contractor is not turning up, the work is getting delayed.
[Action: Southco]

(H) Under Frequency relay operation in OPTCL System during the month of Nov’18.

There is no UF Relay operation during the month of November’18 as the frequency had never gone beyond 48.50 Hz. 
(I) Status of Open Access applications during the month of November’2018
Status of Open Access Applications received and disposed by SLDC during the month was reviewed.

Deliberations in the meeting
Total 169 numbers of Short Term / Medium term and Collective transaction applications have been processed by SLDC for according Approval / Consent / NoC during the month. 
PART C – Issues discussed in the 152th  OCC meeting of ERPC held on 17.12.2018

C.1: Over drawal/under injection by ER Entities 

Odisha over drawl was in the range of 1 to 3MUwhile maximum over drawl touched 3.51MU on 05-12-18 and 395MW maximum on 05-12-18.
There is little improvement of load generation management observed in west Bengal and DVC but Odisha is still overdrawing in to the tune of 2 to 3 mu on daily basis. However, this reduction in quantum of over drawl occurred may be due to natural reduction of demand during winter season.
Deliberations in the meeting
SLDC stated that GRIDCO may explore for arranging power from external sources through procurement/ banking to meet the State’s demand.

[Action: GRIDCO] 

C.2: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
149th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	30.11.18
	162.5 Cr.


	38.09Cr. Requisition for 11.00 Cr placed.
	90% equipment installed and commissioned. Stn Tfr and some measuring instruments are under tendering process.



	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.22 Cr
	Request for 10% grant already submitted. Agreement  signed
	Tender floated

	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov18
Chiplima

Dec 2018
	22.35 Cr.
	2.235 Cr
	Placed work order for Balimele

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 


	27-07-18
	
	31.94 Cr
Ested. Cost. Approved amount 30.26 Cr. Grant amount 27.23 Cr.
	27.23 Cr.
	Agreement signed and sent to NLDC for signature. Tender floated.

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost. 2.93 Cr recommended by Appraisal committee.
	
	Approved by Appraisal committee. Forwarded to CERC for concurrence.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	12.03.2018  Date of submission 
	
	41.1 Cr

Estt cost
	
	Compliance to TSEG observation submitted. Audit observation has been sent to NLDC. 


[Action: CGM (O&M)]

C.3: Requirement of 132kV bay at 400/220/132kV Baripada S/s---OPTCL 

OPTCL informed that at present two no. of 132 kV Bays are available at Kuchei. The Kuchei­ Rairangpur 132 kV S/C line is LILO at Bangiripushi. The loads of connected substation are as follows:  Bangiriposi-8 MW, Rairangpur-28 MW, Karanjia-21 MW, Dhenkikote-10 MW. Thus the 132 kV S/C line is loaded 67 MW. In case of outage at Joda the Polasponga load which is around 40 MW is catered through this line breaching the thermal limit of the line. 

OPTCL requested for a new 132 kV Bay at Kuchei for 132KV Kuchei­ Bangiripushi line to limit the line loading as well as to meet the n-1 contingency. 

In 151st OCC, OPTCL was advised to give a presentation in next OCC Meeting for detailed discussion.  

OCC advised Powergrid to check the feasibility of providing 132kV bay at 400/220/132kV Baripada S/s.  
Deliberations in the meeting

OPTCL made a presentation in the OCC meeting. POWERGRID stated that two Nos. of bays are available at Baripada (PG), out of which one can be spared to OPTCL. ERPC advised that OPTCL & POWERGRID may have a joint field study for takeoff arrangement.

[CGM (Const) / CGM (O&M)]

C.4: Use of Polymer Insulators in the transmission lines--CEA 

CEA vide letter dated 28th November 2018 informed that many representations have been received in CEA as well as VIP references from Ministry of Power from various manufacturers and associations highlighting the issue of use indiscriminate use of polymer insulators which are mostly imported from China leading to closure of indigenous porcelain manufacturing industry. To resolve the issue, a meeting was held in CEA on 25.5.2018 with various stakeholders to deliberate on the issue. 

PGCIL vide letter no. C/CTU/E/02/TBCB dated 24.10.2018, indicated that on the directions of RPC's, only polymer type insulators are being used in the new transmission lines of PGCIL traversing through states in Northern and eastern Regions. Moreover, PGCIL is replacing the porcelain insulators with polymer insulators in the existing transmission lines of the region. PGCIL has categorically mentioned that the same has been done in accordance with the decision taken in the meetings with Regional Power Committees. 

It is to mention that CEA has issued the Regulations and there are specific provisions regarding use of porcelain (disc type I long rod) and polymer insulators. Regulation Clause No. 89(1)(f)(i) of CEA (Technical Standards for Construction of Electrical Plants and Electric Lines) Regulations 2010, may be referred in this regard. 

It may be clarified whether decision of use of polymer insulation in place of porcelain insulator was taken for some particular lines or locations. Considering the sensitiveness of issue, the same may also be discussed in respective RPC meetings and a balanced approach may be adopted for all future lines. 

Deliberations in the meeting
OPTCL suggested that polymer insulators may be used in saline effected areas.

[Action: O&M]

C.5: Review of Cyber Security Works/Activities- CEA 

CEA vide letter informed that Secretary (Power) is going to review the cyber security related works /activities being carried out in Power Sector. In this regard, it is requested to provide the State wise status on following action points pertaining to cyber security at the earliest: 

1. Appointment of organization-wise Chief Information Security Officers and its status

2. Identification of organization-wise Critical Infrastructure and its status 

3. Preparation of organization-wise Crisis Management Plan and its status 

4. Status of Cyber Security Mock Drill activity in coordination with CERT-In 

5. Status of Training / Workshops on Cyber Security organized / participated by power sector entities 

6. Status of action taken on CERT-In / NCIIPC advisories 

In 148th OCC, all the constituents were advised to send the latest status to mserpc-power@nic.in within a week.   

The same has been received from WBSETCL and OPTCL only.
In the 127th PSOC meeting POWERGRID made a presentation on Cyber Security

Deliberations in the meeting

IT stated that audit will be started from January’2019.

[SR. GM (IT)]

C.6: Submission of static data for preparation of a report on coal fired stations in the country--ERLDC 

One internal committee has been formed by POSOCO to prepare a report on coal fired stations in the country, which will be submitted to the FOLD &FOR, at a later stage. Similar reports have already been prepared by POSOCO for hydro, gas and RES plants, which has been widely appreciated in different forums like FOLD & FOR.  

To prepare this report, some static data (commercial, technical, environmental & general) in proper format for all coal fired stations (ISGS, IPP and State Generators) of capacity >= 200 MW need to be submitted to ERLDC so that the compilation and subsequent analysis of data of thermal generators on an all India basis could be made within stipulated time period. 

The format for data submission was intimated to all generators and state SLDCs via email. Till date only GMR, Adhunik, MPL and Sagardighi have submitted their static data. 

ISGS (NTPC), IPP and State Generators of Eastern Region are requested to kindly accord high priority for submitting the static data to ERLDC in erldcso@posoco.in for preparation of the report within stipulated period. 

Nodal coordinators for this Process from ERLDC are: 

 1. Shri Biswajit Mondal, Sr. Engineer, Mob No: 9903329271 2. Shri Chandan Mallick, Sr. Engineer, Mob No: 9007059660 

Deliberations in the meeting

TTPS, IB TPS, GMR & Vedanta were advised to comply. 
[Action: TTPS, IB TPS, GMR & Vedanta]
C.7: Status of UFRs healthiness installed in Eastern Region 

UFR Healthiness Certification for the month of November, 2018 has been received from CESC, WBSETCL, DVC, BSPTCL and JUSNL. 

OPTCL informed that all UFRs healthy except Sadepalli feeder which would be replaced by 15th November 2018.  

Deliberations in the meeting

O&M stated that 33 kV Sadeipali feeder was wrongly mentioned in place of 33 kV Sargipali feeder from Brajrajnagar S/s. UFR of the said feeder has already replaced on 12.11.2018.
C.8: Implementation of Automatic Demand Management Scheme

The latest status along with proposed logic as follows: 
	Sl. No
	State /Utility
	Logic for ADMS operation
	Implementation status/target
	Proposed logic (if different from under implementation logic

	1
	Odisha
	1. System Frequency < 49.9 Hz 
2. Odisha over-drawl > 150 MW
3. DISCOM over-drawl > (40 MW) 
	10 Months

Sent for PSDF approval
	Logic 2 and 3 is AND or OR, in case it is AND then ADMS may not operate when DISCOMs are in schedule but GRIDCO is over drawing due to less generation at State embedded generators.


In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 123rd PSOc meeting SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval

In the 124th PSOC meeting SLDC stated that the revised estimate has been approved in the BoD.

In the 126th PSOC meeting SLDC stated that CERC approval is awaited for tendering.

Deliberations in the meeting

SLDC stated that CERC approval is awaited for tendering.

[Action: SLDC]
C.9: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 128th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by Dec’18. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by March’19.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Keonjhar S/S (220/33 kV) by December’18. All work completed.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	March’2019 


C.10: Update on status of telemetry  

CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed  NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action.

In the 149th OCC, ERLDC stated that status of Breaker & isolator of NALCO & JITPL are not available.

In the 126th PSOC meeting Telecom stated that Service engineer of the company provided NALCO internal SCADA has arrived but could not rectified the data communication of NALCO to SLDC. Telecom suggested that NALCO may go for optical fibre for uninterrupted data communication instead of PLCC.

In the 127th PSOC meeting Telecom stated that the data communication is not consistent. NALCO stated that they are agreeing to go for optical fiber. Telecom may forward their suggestion and offer for taking necessary action by NALCO. It was suggested that NALCO may coordinate with Telecom in this regard.
Deliberations in the meeting

SLDC stated that data communication from Narsingpur S/s is not in place. Telecom stated that provision for leying of optical fibre in Bhanjanagar-Meramundali line has been kept in PSDF scheme. However, if wave trap foundation will be done at Narsingpur S/S, the data communication can be established. It was suggested that construction wing may intimate the installation of new projects to the Sr. G.M (Telecom) as well as SCADA group of Telecom in advance. NALCO representative was not present to deliberate their communication status.
[Action: CGM (Const) / NALCO/Sr.G.M (Telecom)]

C.11: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2018-19 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2018
	Done on 28.06.2018
	Last week of January 2019
	

	3
	Rengali
	2nd week of June 2018
	Done on 18.08.2018
	Last week of November 2018
	January’2019

	4
	U. Indravati
	3rd week of June 2018
	December’18
	2nd week of February 2019
	

	6
	Balimela
	3rd week of October  2018
	December’18
	1st week of March 2019
	

	9
	Burla
	Last week of June 2018
	Done on 07.06.2018
	Last week of February 2019
	


Schedule for demonstration of black start exercise as follows: 

Balimela HEP of OHPC:21st December 2018 in presence of ERPC and ERLDC engineers

Deliberations in the meeting
SLDC stated that OHPC may make necessary arrangements for conducting mock Black start exercise at Balimele HEP in presence of ERPC and ERLDC on 21st December’2018

[Action: OHPC / SLDC]
C.12: Irregularity of data punching to web based PSP portal--ERLDC 

ERLDC has successfully migrated to web based PSP reporting system since 9th September 2018 in which constituents have access to furnish their respective daily energy consumption/generation through web based portal using their own user ids. The report generated based on such punched data, is used by MOP, CEA, NLDC and other various organizations. The success of preparation and publication of error free Web PSP report in time is totally dependent on the active cooperation ofall the constituents filling the data during night hours. As per the recent practice for report preparation, data filled within 04:00 Hrs are considered for report preparation. In case data is not filled by the user for a particular field within 04:00 Hrs during night then SCADA data for that field is used for report preparation. 

Some observations regarding submission of data in Web PSP are follows: 

1. Users viz: Adhunik (APNRL), KBUNL. DMTCL, BRBCL, Tashiding, Barh and FSTPP are not filling data in Web PSP regularly. 2. Regular mismatch of 4 to 6 mu in 765kV Dharamjaigarh-Jharsuguda-Q/D energy data as declared by RTAMC ER – II and SCADA data of same link is observed. Same also verified from SEM data. 

In this regard all the users are requested to kindly attach due seriousness to fill their own data in Web PSP portal by 04:00 Hrs. Powergrid RTAMC ER – II is requested to check the data of 765kV Dharamajaigarh-Jharsuguda-Q/Dbefore publishing during night hour. 

In 151st OCC, Powergrid RTAMC ER – II agreed to look into the matter of 765 kV DharamjaigarhJharsuguda-Q/D energy data; however till date energy data submitted by ER-II RTAMC during night hour differ from SCADA and SEM energy data. 

Odisha and West Bengal are requested to elaborate the mythology followed for submission of CPP net energy data. 
Deliberations in the meeting
SLDC stated that OHPC stations are nor furnishing their daily generation data at 00:00 hrs. OHPC agreed to instruct all the hydro stations to furnish the data.

[Action: OHPC / SLDC] 

C.13: Submission of Thermal Loading of Transmission line and associated terminal equipment by ISTS licensee  

In line with the MoM of 4th NRCE Meeting dt.03-11-14 and “Operational Guidelines for determination Of TTC, ATC and TRM for the Short-Term Horizon (0-3 Months)” published by NRCE dt.20-02-15, thermal limit for transmission line has to be used for calculation of ATC/TTC. However, the thermal loading of transmission line depend on the Maximum Conductor Temperature, End equipment thermal rating. This has to be submitted by the Owner of the equipment. Further, the equipment owner also has to confirm that relay setting has been aligned so that the line can be operated up to its thermal limit. In the absence of complete details, ERLDC is utilising the data from the CEA Planning Criteria  for thermal rating as given below : 

	Conductor Type 


	Ampacity per 

conductor(A)* 


	Thermal loading 

limit of line (MVA) 



	765 kV Quad ACSR_Bersimis
	732
	3880

	765 kV HexaACSR_Zebra
	560
	4452

	400 kV Twin ACSR_Moose
	631
	874

	400 kV Quad ACSR_Moose 
	631
	1749

	400 kV Quad ACSR_Bersimis 
	732
	2029

	400 kV Triple Snowbird
	630
	1309

	400 kV Twin ACSR_Lapwing
	773
	1071

	220 kV Single AAAC_Zebra
	557
	212

	220 kV Single ACSR_Zebra 
	560
	213

	220 kV Twin ACSR_Moose 
	631
	481

	132 kV Single ACSR_Zebra 
	560
	128

	132 kV Single ACSR_Panther 
	366
	84

	
	
	


*Ambient and Maximum conductor temperature are taken as 45°C and 75°C respectively. Apart from above specifically mentioned in CEA transmission planning criteria following loading limit is considered for HTLS line while calculating ATC/TTC 

	Conductor Type 


	Ampacity per 

conductor(A)* 


	Thermal loading 

limit of line (MVA) 



	400 kV Twin HTLS
	1262 
	1750

	220 kV Single HTLS 
	1020 
	390

	132 kV Single HTLS
	732
	168


In view of this, it is desired that all ISTS Licensee and STU (for 400 kV and important 220 kV lines) may kindly submit the following details to ERLDC for utilization in ATC/TTC calculation: 
a) Transmission line wise Ampacity and Thermal loading along with Maximum Conductor Temperature and conductor type.
b) End Equipment Rating and 
c) Confirmation whether the relay setting has been adopted in line with the thermal rating of the line 

d) Any constraint during thermal loading of line  

OCC advised all the ISTS licensees and STUs to submit the relevant data to ERLDC and ERPC. 
Deliberations in the meeting

It was suggested that Corporate Planning wing may intimate the required data to ERPC/ERLDC.

[Action: Sr. G.M (CP]

C.14: Flexibility in generation & scheduling of thermal Power Stations to reduce emission-MOP, GOI Order

CEA vide letter dated 18th July 2018 informed that a committee has been constituted in CEA under Chief Engineer (TPRM) to develop a road map to enable flexible operation of thermal power stations for smooth integration of intermittent RES generation. 

CEA requested for plant performance data as per the format enclosed at Annexure-C18. CEA requested to submit the hard copy and softcopy (in excel) to cetrmcea@yahoo.com.  

OCC advised all the Generators to submit the plant performance data as per the format to CEA.  

Deliberations in the meeting

All the State thermal generators and IPPs  may note and comply

[Action: TTPS / IbTPS / IPPs]

C.15: Prolonged outage of Power System elements in Eastern Region
Thermal Generating units

	Sl. No
	Station
	Location
	Owner
	Unit No
	Capacity (MW)
	Reason
	Outage date

	1
	Vedanta
	Odisha
	GRIDCO
	2
	600
	Turbine bearing vibration
	23.11.18

	2
	Burla
	Odisha
	OHPC
	1
	37.5
	R&M
	25.10.16

	3
	Burla
	Odisha
	OHPC
	2
	37.5
	R&M
	16.10.15

	4
	Burla
	Odisha
	OHPC
	4
	37.5
	Annual Maintenance
	25.10.18

	5
	Burla
	Odisha
	OHPC
	6
	37.5
	R&M
	16.10.15

	6
	Balimela
	Odisha
	OHPC
	1
	60
	R&M
	05.08.16

	7
	Balimela
	Odisha
	OHPC
	2
	60
	R&M
	20.11.17

	8
	Balimela
	Odisha
	OHPC
	5
	60
	Annual Maintenance
	12.10.17

	9
	U. Kolab
	Odisha
	OHPC
	2
	80
	Repair of MIV & DT gate
	25.08.17

	10
	U. Kolab
	Odisha
	OHPC
	3
	80
	Problem in bypass valve
	

	11
	Chipilima
	Odisha
	OHPC
	1
	24
	Flood water in rush
	21.07.18

	12
	Rengali
	Odisha
	OHPC
	1
	50
	Annual Maintenance
	31.10.18

	13
	Indravati
	Odisha
	OHPC
	4
	150
	Sheer pin failure
	


Deliberations in the meeting

OHPC stated that # 5 of Balemela and # 2 of Upper Kolab is expected to be synchronized by end of December’2018 & January’2019 respectively, while # 4 of Upper Indravati by end of December’2018

[Action: OHPC / Vedanta Ltd]

C.16: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.  

· As per the information received from the constituents the following generators certified with IS 18001:  

· All NTPC stations in Eastern Region  

· Teesta, NHPC 

· All OHPC generating units  

· All CESC generating units  

· All units of WBPDCL 

· DGPC units 

In the 117th PSOC meeting CGM (O&M) stated that draft project report for Mendhasal S/S has been submitted to BIS. The report will be approved in the meeting to be conducted by them.

In the 122nd PSOC meeting CGM (O&M) stated that Audit team is expected soon.

In the 123rd PSOC meeting CGM (O&M) stated that the report is yet to be received.

In the 126th PSOC meeting O&M stated that training has been completed. After compliance of the observations, certificate will be issued. 
In the 127th PSOC meeting O&M stated that internal Audit will be started in the month of December.

Deliberations in the meeting

O&M strated that 1st stage of audit has been completed for 6 Nos. of S/Ss.

[Action: O&M)]
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of November’18:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	43.769
	7.198

	2
	WESCO
	0
	66.424
	12.121

	3
	NESCO
	0
	32.012
	7.934

	4
	SOUTHCO
	0
	43.983
	17.688

	
	Total
	0
	186.188
	


It is noticed that all the DISCOMs were over drawn during the month. SOUTHCO has deviated 17.688% followed by WESCO 12.121 % from the scheduled energy while NESCO and CESU have deviated 7.934 % & 7.198 % respectively. DISCOMs may forecast their drawal in realistic approach to minimise deviation.

Deliberations in the meeting

SLDC stated that that the DISCOMs should forecast their drawal in a realistic manner and adhere to their respective drawal schedule.

[Action: Discoms]

D.2: Communication issues 
The status of data communication from CGPs as deliberated in the 124rd PSOC meeting meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	2
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. 
In the 123rd PSOC meeting it was deliberated that RT&C have sought some information from Telecom wing which will be intimated. NALCO stated that due to problem in their internal communication system, data communication to SLDC is being interrupted.
In the 124th PSOC meeting Telecom stated that communication system for Paradeep area industries will be completed by September’2018. Telecom was advised to give a reply to the information sought by RT&C. 

In the 125th PSOC meeting Telecom stated that the information sought by RT&C will be forwarded soon.
In the 126th PSOC meeting it was decided that SLDC shall convene a meeting with Telecom, GCC & RT&C and discuss the issue for filing case before the OERC.

Deliberations in the meeting
SLDC stated that the meeting will be convened during the month of January’19
[Action: SLDC/ Telecom/GCC / RT&C] 
D.3: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 119th PSOC meeting IT stated that Parameters of 16 Nos meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
In the 123rd PSOC meeting IT stated that out of 840 Nos interface meters connected with AMI, 750 Nos are reporting at present. The newly replaced meters are not reporting. 2 Nos. of meters has sent to M/s SECURE meters for study.

In the 124th PSOC meeting O&M stated that SLDC may intimate the list of defective energy meters to O&M on monthly basis for necessary action. IT may ask TCS to co-ordinate with Secure meters and develop a driver data extraction  
In the 127th PSOC meeting IT stated that TCS is demanding Rs. 6.5 lacs for developing the required software. The proposal is placed before the management for approval

Deliberations in the meeting

IT stated that the memorandum has been placed before the PSC

[Action: IT]
D.4: DISCOM Agenda

CESU 

1. Installation of 2x20 MVA Transformer at Hind Metal S/W stn. for feeding to 33/11 kV S/S already commissioned under ODSSP scheme.

2. Installation of 2x20 MVA Transformer at Grid Steel S/W St. for diversion of load from Athagarh feeder. 

3. Earlier 15minute actual drawl data was provided by SLDC, which was very much vital for giving the day ahead schedule forecast. But after stopping the DSM bill by SLDC as per order of APTEL dated 7.5.2018 passed in Appeal No.55/2015, the 15minute actual drawl data are not provided by SLDC. So, it is requested to provide the month wise actual drawl data in 15minutes block basis for giving more accurate day ahead schedule forecast by CESU.

Deliberations in the meeting
O&M stated that 1x20 MVA Tfr at Hind Metal S/W station is scheduled to be charged by end of April’2019It was suggested that CESU may draw power from the newly charged Athagarh S/S instead of asking for installation of 2x20 MVA Tfr at Grid Steel S/W Stn. CESU may ask their officer deployed at SLDC for collection of 15 minute drawal data as, other DISCOMs are doing. 

 [Action: CESU]

PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Expected to be completed by Dec’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	January’2019

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	December’18

	4
	220/33 kV, 2x20 MVA Baliguda S/S
	July’19

	5
	220/33 kV, 2x20 MVA Kalimela S/S
	July’19

	6
	220/33 kV, 2x20 MVA Kasipur S/S
	January’2019

	7
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	December’18

	8
	220/132 /33 kV, 2x100 MVA Aska S/S
	March’19

	9
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’19

	10
	220/132/33 kV Jayapatana S/S(320 MVA)
	July’19

	11
	220/132 kV Pratapsasan S/S(320 MVA)
	Dec’19

	12
	220/132 kV Kesinga S/S (320 MVA)
	March’19

	13
	132/33 kV Betanati S/S
	March’19

	14
	132/33 kV R.Udyagiri S/S
	March’19

	15
	132/33 kV Chikiti S/S
	(Bus test charged on 11.09.18)


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement.
[Action: CGM (Construction) / DISCOMs]

E.2: Major Events in the month of November’18
31.10.18:  At 13:24 Hrs, 220/132 kV, 160 MVA Auto-3 at Theruvali S/s charged.

03.11.18: 400 kV IbTPS-Lapanga DC line charged.

05.11.18: 400 kV Meramundali-Vedanta DC line made LILO at Lapanga.

23.11.18: At 14:25 Hrs 132/33 kV, 40 MVA Tfr test charged at Bolangir (New) S/S and loaded on 27.11.2018 at 21:25 hrs.

Members may note

E.3: Important Grid Incidences during the month of November’18.
There was only one Grid incident occurred during the month occurred on 29.11.18 at 07:22 hrs, during hand tripping of 220 kV Meramundali ckt-1 for availing shut down. One limb of breaker struck up which lead to LBB relay operation at TTPS end. All feeders connected to main bus –II tripped. Main bus was isolated condition at that time. O&M may analyse the incident for deliberation in the OCC meeting
[Action: O&M]

E.4: Outage of major transmission Elements during the month of November’18. (above 10 hrs).
Outage of major transmission elements during the month was reviewed. The outages are due to conductor / jumper snapping, Buchholtz relay operation etc.
[Action: O&M / SLDC]

E.5:  Review of Outage Program of State Generators / Transmission elements for the month of January’19:

Tentative Outage programme for State Generators for the month of January’2019 
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 4
# 5

# 6
	14.03.18 to 30.11.18

01.01.19 to 31.01.19

25.10.16 to continue

16.10.15 to continue
	T&G coupling cover water leakage

Annual Maintenance

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 2

# 3
	01.01.19 to 31.01.19

15.10.15 to continue
	Annual Maintenance

Under R,M & U

	3
	Balimela
	# 1

# 2
# 8
	05.08.16 to continue

20.11.17 to continue

21.12.18 to 20.01.19
	Under R,M & U

Programming for R&M
Annual Maintenance

	4
	Rengali
	# 2

# 4
	12.12.18 to continue

17.12.18 to 15.01.19
	Replacement of Runner disc.

A.M & DVR replacement

	5
	Upper Kolab
	# 1

# 2
# 4
	02.01.19 to 31.01.19

28.05.17 to 11.01.19

15.01.19 to 15.07.19
	Annual Maintenance

Upstream leakage and intake gate problem
Capital maintenance work


E.6: Generation Program for the month of January’19.
Generation schedule for the month of January’19 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.12.18
	Reservoir Level as on 01.12.17
	MDDL
	High Flood    Reservoir Level

	
	Jan’19
(1st fortnight)
	Jan’19
 (2nd fortnight)
	
	
	
	

	HPS-I, Burla
	20
	20
	625.56 ft.
	628.04 ft.
	590 ft.
	630 ft.

	HPS-II, Chiplima
	10
	10
	-
	-
	-
	-

	Balimela
	200
	200
	1510.00 ft.
	1483.80 ft.
	1440 ft.
	1516 ft.

	Rengali
	40
	40
	118.15 mtr.
	122.99 mtr.
	109.72mtr 
	123.5 mtr.

	U.Kolab
	100
	100
	855.49 mts.
	853.97 mtr.
	844 mtr 
	858 mtr.

	U. Indravati
	200
	200
	638.42 mtr.
	636.11 mtr.
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2744.40 ft.
	2748.80 ft.
	2685 ft.
	2750 ft.

	TOTAL
	600
	600
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

[Action: SLDC / OHPC]

E.7: Anticipated power generation and demand for the month of January’2019.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1050
	1200

	2
	WESCO
	1000
	1150

	3
	NESCO
	700
	800

	4
	SOUTHCO
	300
	350

	6
	Total Discom
	3050
	3500

	
	System Loss & others 
	150
	200

	
	Total Demand
	3200
	3700

	Availability
	
	

	1
	Hydro
	600  
	1050

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	400
	400

	4
	ISGS share (including OA& purchase)
	1100
	1200

	5
	CGP support (OA)
	350
	300

	6
	Total availability
	3200
	3700

	7
	Surplus / Deficit
	0
	0


[Action: DISCOMS / SLDC]
PART F: OTHER ISSUES

F.1: Members not present in the meeting.

It is noticed that following organizations / wings have not deputed their members to represent in the 128th PSOC meeting. Some of the agenda items could not be discussed in absence of representatives of those utility/ wings of OPTCL.

Representatives not presented in the meeting.
	Sl. No
	Name of Organization/Wing
	Sl. No
	Name of Organization/Wing

	1
	EHT(O&M), Zone-II
	8
	Tata Power & Steel,

	2
	RT&C
	9
	HINDALCO 

	3
	BPSL
	10
	TTPS

	4
	BSL
	11
	GMR

	5
	IMFA
	12
	OPGC

	6
	BPPL
	13
	NALCO

	7
	JSPL
	
	


Members are requested to depute their officers to represent in the PSOC meeting in future, since the forum is discussing important operational issues of the State Transmission system.     
F.2:  Date and Venue of the next (129th) PSOC meeting.
Date and venue of 129th PSOC meeting will be intimated to all members.

ANNUXURE

[image: image2.jpg]128th Power System Operational Co-ordination Committee Meeting

[ At 11:00 A.M. on 18.12.2018]

[At PTC, Chandaka, Bhubaneswar]

"il)'. Name Designation | Organisation Mobile No. E-mail Address Signnature

1| P K. MisHR () SLDe 1289079 2 cle(.:/c/c%;ﬁ’tﬁnhq, /w,/

2 | S NAYAR BrUM, tt JaRi10Co L] 9H3HY 045y fagm jp @i co,in et

3| 8, Bamons | S b29| o1l  |9Ussa0385)  |gpm.9om) - apitirpiet %L . 35
I S A L T T A e
3 P. Pp\ﬁ‘_ﬁ L GMOTD| 6P T el |a422909240 Cgm-i4@ ophe)-wi in Nﬁ,{,qw
§ Ak okt (S am(D) | prrer |qussgoryys egm - tel@eplel ol %X
7| 3P Pacda S 4 (ed) B”gﬁ;‘;‘f”“‘wmnugm bhep. beliuhe@puesi)| =

8 Pk PRa | AGMeySe, AT fgup [probebpimnsso| Jox,
O | Arpen Rerar Gl | Mangef®y -0 -o4pd F3a3647v287 et ahec522LC fgrmead)

olo s phec FNT TRk TR, fOre R | Yo
1| yeoom “/”51&% DélM TSL  |a933250074 jr“i%‘;ﬁ’?ﬁi 4%/
2 |PRMee o) Stoe |q4estorsag Prostg e, | Pl

B P Nayan  |bam(re)|opTCL ausgqozcogteledivibsae | fyr o
" Josa duy E.e Serbhio | 94125 01294 |pbd « Ssiin A Gnsniy M\\w/

P LA sh,, A MGl NESEO |qy2ea0626 1 | arkshnorse@le 1
P le W Cora |Mendser | wEsco | 943795729 gmé\f;’ig@tmﬁ 8
7|k pedhy | G cLsv | 9y 3es | A G cesw | A

18 | £, faldan Aam(ex) OPTcL  [943890%0s| |ele cesaboo@oph| fw/x\/

P Ska Do tm@p] ofTer | Glssgn 73/ &@%Ap?ﬁ% 2] oy

0 | Py, L padhel GM L pe |MM28909916 Z’Amf :2& Dy
"D .P.kae [4qu | eine JuagsoruelBil’s S Moo

2 |G RSekw | by | cdaunpad 7138907355 ebabp cle.chip, o rone
% | 3 beshra Gu__|Hottsdny) G, 28905Y) | ele - shonshia Qpidered edl)
* | Mares Rrodk | AH \/eezgfzf\, Y222 stjﬁw@ﬂ ) lb"'l\W%fy
5 | RIK SHAH DEV RoF femoccein iR, hedel . aho)
B | Soaikh Kiman Svldfsatant | 2Lde Srch e X—,@nﬂ%ﬁ%’, el g

2 5u/'0(4l¢f %’ DM $we | 99889034253 %—

B Gt bt latgn M) 8LDC | 9920902)6 0 ele-sscalon € gpill. 10.n Wl





[image: image3.jpg]No.

Name

Designation | Organisation Mobile No. E-mail Address

29

(Lhoraw

A SLD ¢ WB3RI0FU19 %2 g

30

?Mkeq wi S

3070421 3| it Ponwme Denierih e,

31

brv) (5 2y & 209689

ole- /glyelxin.go/j{d.

32

CorF Bakon

33

34

35

36

37

38

39

40

41

42

43

44

45

46

47

48

49

50

51

52

53

54

55

N





