[image: image1.jpg]QAURY FFYIS AU 6YNE 689G

OFFICE OF THE CHIEF LOAD DESPATCHER, SLDC

ODISHA POWER TRANSMISSION CORPORATION LIMITED
GRIDCO Colony, P.0.-Mancheswar Rly. Colony, Bhubaneswar-751017, FAX-0674- 2748509

CIN — U401020R20045GC007553

ug
No-SGM (PS)-PL-15/2019 / 1\85Q ) Dated: 13.06.2019

From:

The Chief Load Despatcher
SLDC, OPTCL, Bhubaneswar-17.

To:

As per distribution list

Sub: Minutes of 133" PSOC meeting held on 29.05.2019 at PTC, Chandaka,
Bhubaneswar.

Sir,
Please find enclosed herewith the minutes of 133" Power System Operational Co-
ordination meeting held on 29.05.2019 at PTC, Chandaka, Bhubaneswar.

This is for your information & necessary action.

Yours faithfully;

Encl: As above
Chief Load Despatcher,

SLDC, OPTCL

Copy along with enclosures forwarded to the Executive Assistant to CMD, Gridco / OPTCL
for kind information of CMD.




Distribution list

1. The Director (Commercial), Gridco, Bhubaneswar

2. The Director (Operation), OPTCL, Bhubaneswar

3. The Director (Projects), OPTCL, Bhubaneswar

4. The Director (Operation), OHPC, Bhubaneswar

5. The CGM (O&M), OPTCL, Bhubaneswar.

6. The CGM (Const.), OPTCL, Bhubaneswar.

7. The Sr. G. M. (RT&C), OPTCL, Bhubaneswar.

8. The CGM (PP), GRIDCO, Bhubaneswar.

9. The CGM (IT), OPTCL, Bhubaneswar.

10. The CGM (Telecom), OPTCL, Bhubaneswar.

11. The Sr. G. M. (Const)-I, OPTCL, Bhubaneswar.

12. The C.G.M. (Const), OPTCL, Sambalpur.

13. The Sr. G.M (CPC), OPTCL, Bhubaneswar.

14. The Sr. G.M (CP), OPTCL, Bhubaneswar.

15. The Sr. G.M. (O&M), Zone-I, Narendrapur 

16. The Sr. G.M. (O&M), Zone-II, Meramundali.

17. The CEO, CESU, Bhubaneswar.

18. The A.O., WESCO, Burla

19. The A.O., NESCO, Balasore

20. The A.O., SOUTHCO, Berhampur.

21. The Member Secretary (GCC), OPTCL.

22. The ED, Power Grid Corporation of India, Bhubaneswar.

23. The Sr. G.M. (El.), BHEP, Balimela

24. The A.G.M. (El.), CHEP, Chiplima

25. The Sr. G.M. (El.), UIHEP, Mukhiguda

26. The Sr. G.M. (El.), RHEP, Rengali

27. The D.G.M. (El.), HHEP, Burla

28. The D.G.M. (El.), UKHEP, Bariniput, Koraput

29. The S.E. (O&M), Machhakund

30. The DGM (Elect.), IbTPS, OPGC, Banharpali.

31. The Vice President (O), IMFA, Choudwar.

32. The D.G.M. (O&M), NTPC (TTPS), Talcher.

33. The AGM (Elect.), JINDAL Stainless Ltd., Duburi

34. The G.M, HINDALCO, Hirakud.

35. The G.M.CPP, NALCO, Angul.

36. The Director, M/s. Jindal Steel & Power Ltd., Angul

37. The AVP-Vedanta Ltd (IPP), Jharsuguda

38. The G.M, Vedanta Ltd (CGP), Jharsuguda.

39. The DGM (Power Distribution), RSP, Rourkela.

40. Joint President, Aditya Aluminium Ltd., Lapanga, Sambalpur

41. The G.M. (Elect.),  Bhusan Steel Limited. Meramundali

42. The G.M. (Elect.), Bhusan Power & Steel Ltd, Budhipadar.
43. The G.M. (Elect.), IFFCO Limited.

44. Director & COO, GMR Kamalanga Energy Limited, Satyanagar, Bhubaneswar.

45. The CEO, Bhubaneswar Power Pvt. Ltd, IRC Village, Nayapalli, Bhubaneswar.

46. M/S Tata Power & Steel Ltd., Kalinganagar
47. Power Grid Corporation of India, Bhubaneswar.  

Odisha Power Transmission Corporation Ltd. Bhubaneswar.


Minutes of 133rd PSOC meeting held on 29.05.2019 at PTC, Chandaka, BBSR
List of participants is at Annexure.

Chief Load Despatcher, SLDC, OPTCL welcomed all the participants to the 133rd Power System Operational Coordination meeting and highlighted the system performance during the month of April’2019 and overall power scenario of the State. He also emphasized on the drawal by all the Discoms during the month. 

Dy. Manager, SLDC took the agenda items for discussion. 

The review proceeded as follows: 
1: Confirmation of minutes of 132nd PSOC meeting held on 19.04.2019
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2019/1322 (48) dated 15.05.2019 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.
Deliberation in the meeting:
Since no comments have been received from the members, the minutes of 132nd PSOC meeting was confirmed. 
PART B : SYSTEM PERFORMANCE
B1: Review of Grid Performance for the month of April’2019.
(A)  Frequency 

It was noticed that, during the month of April’19, 68.13 % of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 70.28 % during the month of  March’19. The maximum and minimum System frequency during the month was 50.25 Hz & 49.72 Hz respectively.
Deliberations in the meeting

SLDC stated that the percentage of times of frequency in the IEGC band has been decreased. However, “above 50.05 Hz” range has been increased from 21.39 %  to 25.37 % in comparison with the previous month. . 
 (B)  Grid demand 

Grid demand for the month of  Apil’19 was reviewed. The average consumption during the month was 3869 MW. The maximum System demand of 5151 MW occurred on 04.04.19 at 20:00 Hrs and minimum demand of 2689 MW occurred on 20.04.19 at 05:00 Hrs. 
Deliberation in the meeting

It is observed that the average demand during the month of  April’ 19 has increased by 343 MW and maximum demand  by 508 MW in comparison to March’19. The demand has increased substantially during the month due to change in weather condition and power import by Vedanta Ltd. through short term open access.
 (C) Voltage Profile of important Sub Stations in OPTCL System during the month of Apr’19.
The Voltage profile at different 220 kV buses in OPTCL system during the month of  April’19 was reviewed. 
The maximum Voltage of 235.67 kV occurred at Jayanagar 220 kV bus, while Paradeep  220 kV bus has experienced the minimum Voltage of 202.70 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV  Voltage profile of Meramundali, Mendhasal  and New Duburi bus during the month of April’ 2019 was reviewed. 
Deliberations in the meeting

It is noticed that the Voltage profile of those S/Ss are mormal.
(D) Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of Apr’19.

Auto loading of all 220 kV S/Ss during the month of April’19 was reviewed. 
(E) DISCOM Drawal during the month of April’19 
The schedule and actual energy drawal by Discoms for the month of April’19 was reviewed. 
Deliberation in the meeting:
It is noticed that all the DISCOMs have over drawn during the month. CESU has over drawn 78.517 MU followed by WESCO 57.187 MU, while SOUTHCO & NESCO have over drawn 30.785 MU & 22.179 MU respectively. The deviation of SOUTHCO, CESU, NESCO & WESCO are 10.14, 10.323, 4.631 & 8.809 % respectively from the scheduled energy. The net over drawal of Discoms during the month was 188.668 MU. 

DISCOMs stated that their day ahead drawal schedule has been curtailed by SLDC for which they have been forced to over draw since area load shedding was not possible. SLDC stated that the drawal schedule of DISCOMS has been approved as per the availability of scheduled power. It was decided that the DISCOMs shall furnish their month ahead drawal to SLDC one week before commencement of the month. Accordingly the LGBR will be prepared and forwarded to GRIDCO for purchasing / selling of power for the month in case of deficit / surplus as the case may be

[Action: DISCOMs] 
(F) Energy Generation / import during the month of April’19 
Energy generation and exchange during the month of April’19 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2785.54 MU. 
Deliberations in the meeting
The energy demand has increased by 161.29 MU in comparison with previous month.

(G) Drawal of Machhakund Power during the month of April’19
The drawal of Machhakund power during the month of April’19 was 24.896 MU, against AP drawal of 26.401 MU. 
Deliberations in the meeting

It was noticed that the State’s drawl from Machhakund during the month was less by 1.5 MU. Southco may explore for adding of Koraput, Dasmantpur & Kakariguma feeders to Podagada S/S. OPTCL may take initiative for adding of more feeders at Podagada S/S. Representative of SOUTHCO stated that 33 kV takeoff lines are under ODSSP scheme.
[Action: Southco]
(H) Under Frequency relay operation in OPTCL System during the month of April’19.

There is no UF Relay operation during the month of April’19 as the frequency had never gone beyond 48.50 Hz. 
(I) Status of Open Access applications during the month of April’2019
SLDC has processed 172 numbers of Short Term / Medium term and Collective transaction applications have been processed by SLDC for according Approval / Consent / NoC during the month. 
PART C – Issues likely to be discussed in the 156th  OCC meeting of ERPC held on 25.04.2019
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	11.05.15
	31.03.19
	162.5 Cr.
Total expenditure may not exceed Rs. 68 Crs.
	38.09Cr. Received Rs. 8.00 Cr on 28.03.19 
	90% equipment installed and commissioned. Tender for measuring instruments under evaluation. Stn. Tfr will reach by 15th June’19

	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	51.22 Cr

	2.56 Cr received as 10 % DPR. Claimed for 20 %.
	Order placed. Expected by July’19


	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov18
Chiplima

Dec 2018
	22.35 Cr.
	2.235 Cr
	Placed work order for Balimela. PO for other units amounting Rs. 2 Crs placed. Order under process.( 7 Cr.)

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal,           Meramundali & New Duburi for VAR control & stabilisation of system voltage 
	27-07-18
	
	31.94 Cr
Ested. Cost. Approved amount 30.26 Cr. Grant amount 27.23 Cr.
	Rs.2.72 Cr received as 10% of DPR. Retendering under process.
	Agreement signed and sent to NLDC for signature. Retendering will be done.

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17    Date of submission
	
	3.26 Cr Estt cost. 2.93 Cr recommended by Appraisal committee.
	
	Approved by Appraisal committee. CERC approval awaited.

	
	OPTCL 

.
	Protection up gradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	12.03.2018  Date of submission 
	
	41.1 Cr

Estt cost
	10% of DPR to be asked.
	Project approved.  Tender to be floated after revision of specification.. 


      [Action:CGM (O&M) / OHPC/ SLDC]
C.2: Erroneous Energy data of 220kV Balangir-Katapalli line at Bolangir ---SLDC, Odisha 

The agenda received from SLDC, Odisha is enclosed at Annexure-B10. 

In 156th OCC, GRIDCO informed that they had incurred huge commercial loss in DSM charges because of the erroneous SEM reading at Bolangir and requested for modification of DSM accounts for the affected period.  

OCC noted that the issue has been raised after a lapse of more than two years. OCC advised GRIDCO to establish the fact that the meter reading of SEM of Bolangir is erroneous and the other end readings are o.k. OCC advised to submit the relevant documents to ERPC Secretariat for scrutiny. After receiving the documents from GRIDCO, ERPC Secretariat would study the case and place the details in next OCC and Commercial Meeting.   
SLDC shall furnish the details to ERPC and ERLDC for study and taking a decision.

Deliberations in the meeting

SLDC stated that the information sought by ERPC has already furnished. ERPC will examine the issue.
[Action: SLDC]
C.3: Guidelines for rationalized use of high performance conductors—CEA 

CEA vide letter dated 9th April 2109 informed that use of high performance conductors is on rise to address issues of growing congestion in the existing network and to utilize ROW more effectively.  

CEA has released a document titled “Guidelines for rationalized use of high performance conductors” to create awareness on use of the conductors. Softcopy of the document is available at: http://cea.nic.in/reports/others/ps/psetd/guidelines_conductors.pdf 

O&M may note.  
C.4: Review of the PSS Tuning of Generators in Eastern Region  

On 31st January 2019, PSS Tuning Meeting was held at ERPC. All generating utilities were advised to complete the PSS tuning of their plant at earliest for improvement of damping in the grid during transients. In addition, the tuning reports have also to be submitted to ERLDC/ERPC for their validation. 
In the 131st PSOC meeting OPGC stated that they have already furnished the data to ERPC. GMR and Vedanta were requested to furnish the data soon to ERPC.
In the 132nd PSOC meeting Vedanta stated that they have already furnished the data. 
Deliberations in the meeting
GMR was requested to furnish the data, if not done.

[Action: GMR]
C.5: Ratification of Demand and Generation for calculation of POC of Q-2 2019-20--ERLDC 

The projected Demand and Generation of ER constituents to be considered in the base case for POC transmission charge and loss calculations for Q2 (July 19-Sep 19)  was circulated to all the concerned via email dated 8th May 2019 for comments and verification.

GRIDCO deliberated to consider the State’s demand excluding Vedanta import through Open Access.

Deliberations in the meeting

GRIDCO stated that they have already taken action.

[Action: GRIDCO]   

C.6: Implementation of Automatic Demand Management Scheme

The latest status along with proposed logic as follows: 
	Sl. No
	State /Utility
	Logic for ADMS operation
	Implementation status/target
	Proposed logic (if different from under implementation logic

	1
	Odisha
	1. System Frequency < 49.9 Hz 
2. Odisha over-drawl > 150 MW
3. DISCOM over-drawl > (40 MW) 
	10 Months

Sent for PSDF approval
	Logic 2 and 3 is AND or OR, in case it is AND then ADMS may not operate when DISCOMs are in schedule but GRIDCO is over drawing due to less generation at State embedded generators.


In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 123rd PSOc meeting SLDC stated that since the estimated cost has increased due to inclusive of SCADA integration, the revised estimate is placed in the BoD for approval

In the 124th PSOC meeting SLDC stated that the revised estimate has been approved in the BoD.

In the 129th PSOC meeting SLDC stated that CERC approval is awaited for tendering.

CERC has approved the revised estimate. SLDC shall process for tendering.
In the 132nd PSOC meeting it was decided that a committee will be constituted with representatives from SLDC, Telecom, IT and DISCOMs to finalize the implementation of the scheme.

Deliberations in the meeting

A committee was constituted with the following members

1. Sri B.D.Panda, AGM, SLDC, Convener

2. Sri Manoj Kumar Das, G.M.(Operation),SLDC

3. Sri Pranab Kumar Nayak, DGM (Telecom)
4. Sri Subrat Kumar Mishra, DGM (IT)

5. Sri P.K.Padhy, GM, CESU

6. Sri. Anil Kumar Patra, Manager, WESCO

7. Sri S.C.Mahalik, G.M, NESCO

8. Sri Sanjeeb Mohanty, A.M, SOUTHCO

[Action: SLDC]

C.7: 220 kV Inter-connecting lines of OPTCL with 400/220 kV Bolangir(PG), Keonjhar & Pandiabil S/s

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 132nd PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by March’19. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by July’19.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	220 kV S.C line and Keonjhar S/S (220/33 kV) , 2x20 MVA charged on 31.12.2018. 2nd ckt; June’’2019

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019. Order placed.

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	July’2019 


In the 132nd PSOC meeting NESCO stated that they have already taken action for downstream takeoff arrangements from Keonjhar S/S. Telecom stated that for charging of Keonjhar-Keonjhar (PG) 2nd ckt, CARD has already been received and ABB engineers has reached the spot. Expected by June’ 2019.

[Action: CGM (Cont) / CGM (Telecom)]
C.8: Bypassing arrangement of LILO of 400kV Lines at Angul 

LILO of Meramundali-Bolangir/Jeypore 400 kV S/C line and LILO of one Ckt of Talcher-Meramundali 400 kV D/C line has been done at Angul 765/400kV Sub-station. The bypass arrangement for these circuits is under implementation at Angul by Powergrid.  

In 157th OCC, Powergrid informed that bypass arrangement would be completed by June 2019.   

OPTCL may please inform the commissioning schedule of the 2nd circuit of 400kV Meramundali-Mendhasal line. 

Deliberations in the meeting

O&M stated that 3rd ICT at Mendhasal will be charged after completing DGA test, after which 400 kV Meramundali-Mendhasal 2nd circuit will be charged.
Powergrid and OPTCL may update.

C.9: Update on status of telemetry  

CERC vide order dated 28.02.2016 on Petition No. 007/SN/2014 directed  NLDC and respective RLDCs to update the status of telemetry every month at their respective websites and take up 

the issue of persistent non-availability of data from Generating Stations/substations at RPC meetings for appropriate action.  

Major issues are given below: 

xxxxxxxxx.

In the 132nd PSOC meeting CGM (Telecom) stated that survey work for Meramundali-Bhanjanagar line is under process. OPGW will be reached at site after completion of survey and preparation of drum schedule. DGM (Telecom) stated that the vendor list and rate will be provided to NALCO for placement of order by them.

Deliberations in the meeting

DGM (Telecom) stated that the vendor list has been provided to NALCO. NALCO stated that the tower schedule has been prepared. 

[Action: Telecom / NALCO]

C.10: Transfer capability determination by the states  

In order to ensure, safe and secure operation of the grid, the states should carry out the power system study for operational planning and power transfer capability through their respective transmission links with the rest of the grid. 

It was decided in the NPC meeting that to begin with, power system study for assessment of operational limits / power transfer capability for each state will be done by the concerned RLDC in association with concerned SLDC. Monthly TTC /ATC will be uploaded by the SLDCs at their respective websites and also communicated to concerned RLDC & NLDC subsequently.

SLDC deliberated that Odisha have furnished the data up to September’2019

[Action: SLDC]
C.11: Mock Black start exercises in Eastern Region – ERLDC 

	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2019
	
	Last week of January 2020
	1st week of June’19

	3
	Rengali
	2nd week of June 2019
	
	Last week of November 2020
	2nd week of June 2019

	4
	U.Indravati
	3rd week of June 2019
	
	2nd week of February 2020
	4th week of June 2019

	6
	Balimela
	3rd week of October  2019
	
	1st week of March 2020
	

	9
	Burla
	Last week of June 2019
	
	Last week of February 2020
	4th week of June 2019


Format for Reporting of Mock Black Start Activity: 

Mock drill on Black start is a continuous activity ongoing in the power system. In addition to black start mock drill, it is essential to monitor each black start to check the performance. ERLDC is in receipt of reports from various black start stations performing these activities from their respective SLDC however, many a times essential information pertaining to performance monitoring of the activities are missing. In view of this it is proposed that, for any mock drill on black start, SLDC must share the following details to access the performance and  the same need to be intimated one week before to ERLDC along with black start process. This will help in finding out any challenges and sharing of experiences with other utilities. 

1. Name and Contact of Personnel available at SLDC: 
2. Name and Contact of Personnel available at Generating Plant: 
3. Name and Contact of Personnel available at Load Substation: 
4. Single Line diagram of the mock drill: 
5. Details of Steps taken for Mock Drill 

Table 1: Performance monitoring of Mock Drill 
	Activity
	Time (Minutes)

	Time taken to start DG set after black out of Island 


	

	Time taken to charge dead bus at Black start station 
	

	Time taken to charge dead bus at Remote end by line charging
	

	Time taken to connect first load post a black out in the island
	

	Duration of stable island operation after successful black start and building up the of the island till synchronization with grid
	

	Time taken to synchronize the island with Grid
	


6. Issues Observed: 
7. Remedial Action Taken if Any for the challenges: 
8. Any other details:  

[Action: SLDC / OHPC]
C.12: Submission of Thermal Loading of Transmission line and associated terminal equipment by ISTS licensee  

In line with the MoM of 4th NRCE Meeting dt.03-11-14 and “Operational Guidelines for determination of TTC, ATC and TRM for the Short-Term Horizon (0-3 Months)” published by NRCE dt.20-02-15, thermal limit for transmission line has to be used for calculation of ATC/TTC. However, the thermal loading of transmission line depend on the Maximum Conductor Temperature, End equipment thermal rating. This has to be submitted by the Owner of the equipment. Further, the equipment owner also has to confirm that relay setting has been aligned so that the line can be operated up to its thermal limit. In the absence of complete details, ERLDC is utilising the data from the CEA Planning Criteria for thermal rating.

OCC advised all the other ISTS licensees and STUs to submit the relevant data to ERLDC and ERPC. 
In the 129th PSOC meeting Sr. G.M (CP) stated that thermal loading data has been submitted by them. O&M shall submit the terminal equipment data

In the 131st PSOC meeting O&M was requested to expedite for furnishing the data.

In the 132nd PSOC meeting O&M stated that they will submit the data by 15th May 2019.
Deliberations in the meeting
O&M stated that the data has already been furnished to ERPC. OHPC may furnish Indravati (PH)-Indravati (PG) end data.
[Action: OHPC]
C.13: Collection of modeling data from Renewable as well as conventional energy generators: ERLDC 

As a National Grid operator, POSOCO is continuously working for ensuring reliability and security of the Grid. With penetration of more and more renewable energy source the task is becoming complicated day by day.  An accurate dynamic modeling of the National Grid needs modeling of conventional as well as renewable / distributed generation sources. World Bank has engaged Digsilent as consultant for assisting POSOCO for building dynamic model of the Grid. A guideline for dynamic data collection has been developed in consultation with Digsilent Pacific team.   All the utilities are requested to collect data from the grid scale renewable power plants as well as from conventional power plants under their jurisdiction and submit the same to ERLDC/ERPC as early as possible. 

In the 132nd PSOC meeting, all generators as well as RE sources were requested to furnish data to SLDC for onward transmission to ERPC.
SLDC requested ERPC to forward the format for preparing the data. The format will be circulated to all RE & conventional generators in the State 
Deliberations in the meeting
SLDC stated that the format will be circulated after receiving from ERPC.
[Action: SLDC]
C.14: Implementation of Automatic Generation Control (AGC) in India (at Inter-State level) 

The issue was discussed in 8th NPC Meeting held on 30th November 2018, it was decided that each RPC would submit the status of implementation of AGC to NPC.  

In 40th TCC, NTPC informed that AGC at Barh STPS will be implemented by May, 2019. 

DVC confirmed that unit#8 of Mejia TPS has been identified for AGC implementation as a pilot project. 

The followings were decided in the TCC Meeting: 

1. Status of implementation of AGC shall be regularly monitored in OCC meetings. 

2. A workshop shall be organized in ERPC wherein NLDC and NTPC will be invited to interact with the ER constituents regarding the experience they have gained in implementing the AGC in other regions. 

In 155th OCC, NTPC informed that implementation of AGC at Unit#4 & 5 of Barh STPS are in progress and was expected to complete by May 2019.  

Odisha informed that unit#3 of OPGC had been selected for implementation of AGC.  

WBPDCL informed that unit#5 of Bakreswar had been selected for implementation of AGC.  

In 156th OCC, OCC decided to organize the workshop at ERPC in May 2019 wherein NLDC, NTPC and Siemens will be invited to interact with the ER constituents.  

The workshop on AGC would be held on 31st May 2019 at ERPC, Kolkata.  

Deliberations in the meeting
Generators may furnish their feedback after attending the workshop.

[Action: OHPC / OPGC / GMR/ Vedanta] 

C.15: Maintenance and support (AMC) renewal of PSSE software.  

Siemens vide letter dated 20th March 2019 informed that the AMC for PSSE software has ended on 30th November 2018.  

Siemens requested ERPC Secretariat to renew the maintenance and support period for all the existing supplied licenses of states for next five years.  

In 156th OCC, All the SLDCs in the meeting agreed for renewal of the AMC of PSSE software for next five years and requested to take up the AMC contract jointly for all the states with the Siemens as it was done during the procurement of software.   

OCC advised ERLDC to take up the issue with NLDC and CTU.  

Deliberations in the meeting

SLDC stated that ERLDC will take necessary action for renewal of the AMC

SLDC / O&M / GRIDCO may note
C.16: Updated Black Start and Restoration procedure of State—ERLDC As per clause IEGC 5.8(b)  

“Detailed plans and procedures for restoration after partial/total blackout of each User’s/STU/CTU system within a Region, will be finalized by the concerned User’s/STU/CTU in coordination with the RLDC. The procedure will be reviewed, confirmed and/or revised once every subsequent year.” 

In 154th OCC all the SLDCs to were advised to submit the updated restoration procedure of their respective state. 


SLDC has developed a draft Black start Restoration procedure and circulated to OHPC /&O&M for comments. Since no comments have been received till date, the draft procedure is finalized and will be submitted to ERLDC / ERPC.

Deliberations in the meeting

OHPC stated that Upper Kolab has furnished their views on the draft procedure. The procedure will be finalized considering the views of Upper Kolab.

[Action: SLDC]

C.17: Shutdown proposal of transmission lines and generating units 

In 151st OCC, it was observed that constituents had not submitting the shutdown requisition within stipulated time as a result ERLDC had been facing difficulty in properly analyzing the shutdown. 

OCC decided the following procedure for submission of transmission elements outage requisition:  

1. Shutdown of Intra Regional Lines- Transmission licensee/SLDCs/Transmission Asset owners shall apply shutdown of their respective Intra Regional Lines for the next month to ERLDC strictly by 8th of every Month. Based on this, ERLDC shall prepare the list which would be placed in OCC Agenda. Any shutdown requisition received after 8th of the month would not be normally considered for discussion in the OCC meeting unless it is considered to be an emergency requirement.   
2. Shutdown of Inter Regional Lines - Transmission licensee/ SLDCs/Transmission Asset owners shall send their shutdown requisition of Inter Regional Lines for the next month directly to NLDC strictly by 5th of every month with a copy to respective RLDCs.
O&M may circulate the above guide lines to all field units to follow while submitting shutdown proposal. 
Deliberations in the meeting

O&M has assured to circulate the guide lines to field units. SLDC requested O&M to return the shutdown of 220 kV, Meramundali-Bhanjanagar, ckt-II taken for conductor replacement, as there in no operational redundancy for in case of shutdown of 400 kV lines by POWERGRID. O&M stated that 220 kV Atri-Narendrapur line will be charged soon.

[Action: O&M / SLDC]

C.18: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN. 

The activity of the preparation of Crisis Management Plan for countering the cyber-attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA. 

In 142nd OCC, ERLDC informed that, in line with Enquiry Committee Recommendation, cyber security audit is being conducted on regular basis for SCADA system installed at ERLDC and SLDC as well but cyber security audit for telecom infrastructure installed in Eastern Region is not being carried out.  

OCC advised all the constituents to conduct the cyber security audit on telecom infrastructure installed in Eastern Region. It is further advised that compliance / mitigation of the points observed during the audit should also be completed for improvement of the telecom infrastructure in ER. 

As suggested by CEA, a format has been circulated among ER constituents for furnishing the information of the respective systems for discussion in OCC Meeting. The format is enclosed at Annexure-E1. 

OCC advised all the constituents to submit the information to ERPC as per Annexure-E1.
Deliberations in the meeting

SLDC stated that the information received from IT has been forwarded to ERPC.

[Action: Sr. G.M (IT)]

C.19: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.    

 
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.  

As per the information received from the constituents the following generators certified with IS 18001:  • All NTPC stations in Eastern Region • Teesta, NHPC • All OHPC generating units  • All CESC generating units  • All units of WBPDCL • DGPC units 

In the 129th PSOC meeting O&M stated that 2nd stage internal audit has been done. Report is yet to be received. Process has been initiated for deposit of application money for external audit. On compliance of the observations Certificate may be issued.    

In the 131st PSOC meeting O&M stated that Audit has been completed but the report is yet to be received.
In the 132nd PSOC meeting O&M stated that external audit stage-I completed. On completion Stage-II external audit certificate may be received.

Deliberations in the meeting

O&M stated that the activity has been postponed due to cyclone “FANI”

[Action: CGM (O&M)]

C.20: Commissioning of new transmission elements in Eastern Region 

The details of new units/transmission elements commissioned in the month of April-2019 based on the inputs received from beneficiaries 

Monthly commissioning List of Transmission element and generators: April 2019 

	Sl No
	Element Name
	Owner
	Charging Date
	Charging Time
	Remarks

	1
	800 MW Darlipali unit 1 (G.T. 1)
	NTPC
	04-04-2019
	09:02
	

	2
	765 KV Jharsuguda- Raipur I
	OGPTL
	04-04-2019
	21:12
	

	3
	765 KV Jharsuguda- Raipur II
	OGPTL
	05-04-2019
	23:32
	

	4
	LILO  132 KV Udala-Baripada SC line at Betanoti S/S 
	OPTCL
	19-04-2019
	14:02
	 (3.104 Kms) in existing line


 [Members may note]
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to Discoms during the month of April’19:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	78.517
	10.323

	2
	WESCO
	0
	57.187
	8.809

	3
	NESCO
	0
	22.179
	4.631

	4
	SOUTHCO
	0
	30.785
	10.140

	
	Total
	0
	188.668
	


It is noticed that all the DISCOMs were over drawn during the month CESU has deviated 10.323% followed by SOUTHCO 10.140% from the scheduled energy while WESCO and NESCO have deviated 8.809 % & 4.631 % respectively. DISCOMs may forecast their drawal in realistic approach to minimise deviation.

SLDC/ Discoms may please deliberate.
D.2: Communication issues 
The status of data communication from CGPs as deliberated in the 124rd PSOC meeting meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	2
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. 
In the 123rd PSOC meeting it was deliberated that RT&C have sought some information from Telecom wing which will be intimated. NALCO stated that due to problem in their internal communication system, data communication to SLDC is being interrupted.
In the 124th PSOC meeting Telecom stated that communication system for Paradeep area industries will be completed by September’2018. Telecom was advised to give a reply to the information sought by RT&C. 

In the 125th PSOC meeting Telecom stated that the information sought by RT&C will be forwarded soon.
In the 126th PSOC meeting it was decided that SLDC shall convene a meeting with Telecom, GCC & RT&C and discuss the issue for filing case before the OERC.

A meeting was convened between SLDC, Telecom, GCC, RT&C, NINL & IRE Ltd on dt.15.01.2019 at SLDC conference hall to discuss the communication issue. Representative of IRE, SLDC, GCC and Telecom were attended the meeting. IRE deliberated that presently CB, CT & CVT are not installed at their end. Tendering for procurement of CB, CT & CVT have already been done, which will be expected by end of April’2019. Due to space constraint at IRE Switch yard, installation of the equipment may not be possible, unless the Switchyard is modified. For modification they may need the help of OPTCL. It was suggested by SLDC that IRE may approach Sr. G.M (O&M), Zone-1, OPTCL in this regard. Simultaneously, they also to write Sr. G.M (Telecom), OPTCL for preparing estimate for extending data communication from their end.

NINL was not present in the meeting.  

In the 130th PSOC meeting it was decided that RT&C shall file a case before the OERC against the defaulting CGP / Industries and Telecom will provide the required information to them. RT&C vide their letter No. 104(4) dated 01.03.2019 asked Telecom wing to prepare the draft Petition along with the required information to them.  
In the 131st PSOC meeting it was decided that T&C and Telecom shall discuss and prepare the Petition to file before the OERC.

In the 132nd PSOC meeting RT&C stated that the draft Petition has been prepared.
Deliberations in the meeting

It was decided that RT&C will provide the draft Petition to Telecom wing within a week for their views.
Action: RT&C and Telecom 

D.3: Data communication from newly commissioned RE sources connected at 132 kV- SLDC

There are as many 8 Nos. of Solar projects with installed capacity of 272.5 MW have connected with OPTCL network through 132 kV lines. The real time data of these plants are yet to be received at SLDC control room. Since the generation quantum is quite substantial (to the tune of 0.6 MU during a day), this has an impact on real time generation monitoring. 

In the 132nd PSOC meeting it was decided that SLDC shall convene a meeting with the defaulting Solar units and Telecom to discuss the issue. 

Deliberations in the meeting

CGM (Telecom) stated that Vinto Solar data can be integrated only after laying of optical fiber, which has been proposed for PSDF funding

[Action:  SLDC/Telecom]

D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos. of meters integrated, around data from 750 nos. of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos. of meters integrated, data from 717 nos. of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos. of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 119th PSOC meeting IT stated that Parameters of 16 Nos. meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
In the 123rd PSOC meeting IT stated that out of 840 Nos. interface meters connected with AMI, 750 Nos. are reporting at present. The newly replaced meters are not reporting. 2 Nos. of meters has sent to M/s SECURE meters for study.

In the 127th PSOC meeting IT stated that TCS is demanding Rs. 6.5 lacs for developing the required software. The proposal is placed before the management for approval

In the 128th PSOC meeting IT stated that the memorandum has been placed before the PSC

In the 130th PSOC meeting IT stated that approved letter was yet to be received by them.

In the 131st meeting IT stated that TCS has already developed the driver for Paralakhemundi and Balasore S/S meters. Data fetching is under testing stage.

In the 132nd PSOC meeting IT stated that EMD has already been shared. Report is expected by end of April19.

Deliberations in the meeting

DGM (IT) stated that Paralakhemundi and Balasore S/S meter data has been tested. The software fetching data for other S/Ss will be tested.

[Action: IT / SLDC]

D.5: Colony consumption of POWERGRID S/Ss

In the 131st PSOC meeting SLDC stated that POWERGRID is consuming power for their colony, which is not reflected in the DISCOM bill. POWERGRID stated that they have applied to DISCOMs to make them consumer. 

It was decided that SLDC shall convene a meeting between GRIDCO, POWERGRID & DISCOMs to discuss the issue.

In the 132nd PSOC meeting CESU stated that POWERGRID has already made consumer of CESU. Other DISCOMs may insist to POWERGRID to become their consumer.  

Deliberations in the meeting

It was decided that all Discoms may submit the details of their problems regarding making POWERGRID their consumer, to GRIDCO. The issue may be raised in the Commercial Committee meeting of ERPC.
[Action: GRIDCO /DISCOMs]

D.6: Collection of modelling data for new Transmission elements as well as Generators  for system study.

SLDC is conducting system study for real time operation and determination of ATC & TTC for the State system. For the said study modelling of all transmission elements as well as generators are required. O&M is requested to furnish the parameters of newly inducted transmission lines / Transformers such as conductor type, line length and resistance, reactance and susceptance etc. and percentage impedance for transformers. Generators are requested to furnish the similar parameters in respect of the generator. 

Deliberations in the meeting

It was decided that SLDC will forward the format by 1st week of June’19 to all Generators and O&M for preparing the data in respect of their units and transmission lines.
[Action: SLDC]

PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Expected to be completed by June’19. (idle charged from Jnagar)

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	July’2019

	3
	220/33 kV, 2x20 MVA Baliguda S/S
	July’19

	4
	220/33 kV, 2x20 MVA Kalimela S/S
	July’19

	5
	220/33 kV, 2x20 MVA Kasipur S/S
	June’2019. Line charged.

	6
	220/132 /33 kV, 2x100 MVA Aska S/S (132/33 kV side)
	132/33 kV Side charged

	7
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’19

	8
	220/132/33 kV Jayapatana S/S(320 MVA)
	July’19

	9
	220/132 kV Pratapsasan S/S(320 MVA)
	Dec’19

	10
	220/132 kV Kesinga S/S (320 MVA)
	July’19

	11
	132/33 kV Betanati S/S
	Charged on 19.04.2019

	12
	132/33 kV R.Udyagiri S/S
	July’2019


The Discoms are requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement.
CGM (Construction) / DISCOMs may deliberate

E.2: Major Events in the month of April’19

1. On dt. 01.04.2019 at 18:46 Hrs - 40 MVA, 132/33 KV Power Transformer charged at GIS S/S, Unit -8, Bhubaneswar.

2. On dt.19.04.2019 at 14:02 Hrs - 132/33 KV Grid S/S, Betanoti S/S Charged by  LILO Arrangement (3.104 Kms) in existing 132 KV Udala-Baripada SC line. At 14:21 Hrs dt.19.04.19 - 1x20 MVA 132/33 KV Power Transformer idle charged from 132 KV side. At 14:53 Hrs dt. 19.04.19 - 33 KV side of kV Power Transformer charged along with 33 KV bus. At 15:52 Hrs dt. 19.04.19 - 132 KV Udala - Betanoti feeder charged.
Members may note

E.3: Important Grid Incidences during the month of April/ May’19.
On dt. 03.05.19  around at 08:30 Hrs, extremely severe cyclonic storm "FANI" hit the coast of Odisha near Puri which caused disturbance in OPTCL System hence leading to load loss of  1800MW along with outages of following transmission elements. Major transmission lines and Distribution network in the Districts of Puri, Khurda and part of Cuttack have been damaged.
[Action: O&M / CESU]
E.4: Outage of major transmission Elements during the month of April’19 and May’19. (above 10 hrs).

Outage of major transmission elements during the month of April as well as due to the impact of “FANI” in the month of May’2019 has been reviewed.
[Action: O&M]

E.5:  Review of Outage Program of State Generators for the month of June’19:

Tentative Outage programme for State Generators for the month of June’2019 
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1

# 4

# 5

# 6
	14.03.18 to continue

25.10.18 to 31.07.19

25.10.16 to continue

16.10.15 to continue
	T&G coupling cover water leakage

Intake gate problem
Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to 30.06.19
	Under R,M work

	3
	Balimela
	# 1

# 2
	05.08.16 to continue

20.11.17 to continue
	Under R,M work

Under R,M work

	4
	Rengali
	# 2
	12.12.18 to 30.06.19
	Replacement of Runner disc.

	5
	Upper Kolab
	# 3

# 4
	28.03.19 to 15.06.19

01.02.19 to continue
	Generator stator inter turn / Earth fault

Capital maintenance work


Deliberations in the meeting

CGM, OHPC, Balimela has requested for shutdown of # 4. SLDC stated that the shutdown will be allowed only after arrival of monsoon.
[Action: OHPC]  


E.6: Generation Program for the month of June’19.
Generation schedule for the month of June’19 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.05.19
	Reservoir Level as on 01.05.18
	MDDL
	High Flood    Reservoir Level

	
	June’19
(1st fortnight)
	June’19
 (2nd fortnight)
	
	
	
	

	HPS-I, Burla
	50
	50
	611.43 ft.
	611.10 ft.
	590 ft.
	630 ft.

	HPS-II, Chiplima
	35
	35
	-
	-
	-
	-

	Balimela
	360
	360
	1478.40 ft.
	1453.30 ft.
	1440 ft.
	1516 ft.

	Rengali
	30
	30
	113.96 mtr.
	117.87 mtr.
	109.72mtr 
	123.5 mtr.

	U.Kolab
	100
	100
	849.58 mts.
	849.48 mtr.
	844 mtr 
	858 mtr.

	U. Indravati
	80
	80
	631.40 mtr.
	631.15 mtr.
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2725.15 ft.
	2724.75 ft.
	2685 ft.
	2750 ft.

	TOTAL
	685
	685
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

[Action: SLDC / OHPC]

E.7: Anticipated power generation and demand for the month of June’2019.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1130
	1450

	2
	WESCO
	1100
	1300

	3
	NESCO
	920
	1000

	4
	SOUTHCO
	470
	600

	5
	Total Discom
	3620
	4350

	
	System Loss & others 
	150
	200

	
	Total Demand
	3770
	4550

	Availability
	
	

	1
	Hydro
	685  
	1200

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	450
	400

	4
	ISGS share (including OA& purchase)
	1545
	1850

	5
	CGP support (OA)
	340
	350

	6
	Total availability
	3770
	4550

	7
	Surplus / Deficit
	0
	0


Members may discuss.

PART F: OTHER ISSUES
All members expressed their gratitude to Er. Purnendu Sekhar Sahoo, C.GM (Const), OPTCL, who is going to retire from service on superannuation by end of this month for his advice and guidance. PSOC will remember his valuable advice and the foot prints he has left for all times with deep regard.  

F.1: Time synchronization of energy meters-GKEL

Time synchronization of Main and check energy meters at both ends of 400 kV Meramundali-GKEL feeder has not been done since a long period. OPTCL may take up the work. 
Deliberations in the meeting
It was decided that GMR will take up the time synchronisation work with Secure Meter in presence of OPTCL.

[Action: GMR/ OPTCL]

F.1:  Date and Venue of the next (134th) PSOC meeting.

The date and venue of 134th PSOC meeting will be intimated
ANNEXURE

[image: image2.jpg]133rd Power System Operational Co-ordination Committee Meeting
[ At 11:00 A.M. on dt. 29.05.2019]
[At PTC, Chandaka, Bhubaneswar]

:‘l) Name Designation | Organisation Mobile No. E-mail Address Signature
1P K Michye eLn SEhc | 9438907402 |ele.ploi shoeg tidionde, &lﬁ/
2 Ak Pattnie Cqm | Tedeow | 9438907YY40 tzt-mkeauwkum a3l
P GR.Dad (S GM@ofPC  aumsnans ¢ b liecais b 1ace)G
4| ¢ P P | G OHPC |7328%99 FM(E;M\,& @ Yo | P Y/
> |5 Klodeteaden [ Sogutn | Vel NAYTA 0042 en 1 ades V.g > <an
© W0 Makepehs |5 Gu_| Bt1re | 7558240015 hom/m o, Mo
7| Bk Womsy P penmeger’| e0BSed | QuzpiSe 1u9, Wé‘:‘ﬁ’;’;}gﬁm el
8 | Prachent Kuma Do | GM(Pewy | Grince | q4se90 7468 Qoﬁj’ff‘;""'d‘”@"‘*m‘“' Oz/
9 |Mansphutmedo| §.mave| CLDe | gusiqores) el ucdostop <%>W1,;p\%
10 [Poacastds. @/tt; o, SEh et pe |aq38703Y10 [l PREMPRG E T .y ‘
1| S k. poopk| 9 CBY) SLRC |FITTE [FEolb R ek ] o Spit
2| RK Cobir | anfecp) optel | aYoe80 |ole vee sohun W ol
13| D N. Petorer D‘akn Oktbc %zssa,og%o Anpabya C:b\zzwaa;:mLJg/? -
14 (A 0w M»L«»ff Do m | oo | Z32889c00y |adum cgfgw_ )qi[é,”
15 ‘Pb’w(ceP Medapern| Ky | DPGL 33891540 1 %’“07; = M AU%WW
s (LK Gewin |gar | WAtco |9hareatsil kot siwin@rells, G
17 1 5 4. Mesbme | D T | £pTee ?‘13%797%5 Mol Mw%@&pfu Ja.
S PR MeKkap [DAMTY] = LDC Q435907549 tof, Wmmq bunoy, 4
19 [P K- Nawan ' [DomTe [Tl 9439907 50p tele v bilsa | p T
2 K TR, Aenppy STOMz) s |9Y 389080294l e lpps [T hgotPe |-
21 | Cipoel, Mobard) MO(€kl] S0 Tico |9UD7959% oglobt sohwegmmihah  Fort
2 MME&N%Q““@@D WEND | Qipgaga, | Mecewemden, | @by
# {bousir Ku. Wy, i (L) orrel 9y3890701) @PQ-%%% /@m
2“ AhkMoAamm AGNCED| oPTeL (AU38I0724 4 Jele: akmﬂ'ﬂa'smfm S
25 [Sovjeygafiu Mkl ey > | o by 39y g syl || >
26 |Gl oot VAo | SHI [ quseapmye A S )
7 | S PRadby | As(A)| SCC | 99598y Jeceapre/aly o
B Pty | GM CESV QU 3%67€¥ 1| ablG cescaonpy )

7 : e



[image: image3.jpg]’il," Name Designation | Organisation Mobile No. E-mail Address Signatui
. N 9 Malaly

» |6 € tahaton | byin(op) NEgEp, TIPS e,%qucg&f* o, el
> Dv P. KOJf %7%@907(4%%@/{&&{@ 0'0‘1 S D Kewr
|, funch velondn [TF457222 [ forah @fmﬁa
28K B mmed I T89Y47108 L |Su, bunmad @ g 5 W
B | M- eanjelH { 01e€ CNOR61IR] fouwren 02 gt Mol
P s cobw  |coutg | OPrel. | Q432904715 ete pwwc,q;m éwﬂw

P Evedbond pomal) 80TeL [ A3ERIDRY cle byssdeagdd « o

Sadogh Kueer Dl fogystert | CLDC |9 A% 30pn14) | £~ Sontosrdis neddffos)ov [0

37

ool sth

428909428 s ssolydopletcos

7 / '
# | ol g Galond %L{gm?um@@wm@ (M
39 W%/’ﬂ\ lodedt 492907160 | ¢fe- (SQ;U;;O@ 0iin Lkl

40

Priacep hut nthanf]

(— [342890590) |2

Lle. ;)»MO M/)\!L 0{'1(1. Wﬁj

41

7(42890%/;?

R AR

2

43

44

45

46

47

48

49

50

51

52

53

54

35





