[image: image1.png]STATE LOAD DESPATCH CENTRE

OFFICE OF THE Sr. GENERAL MANAGER (POWER SYSTEM)
ODISHA POWER TRANSMISSION CORPORATION LIMITED
GRIDCO Colony, P.O.- Mancheswar Rly. Colony. Bhubaneswar-17. FAX-0674- 2748509

CIN = U401020R2004SGCO07553

No-SGM (PS)-PL-15/2014 / ,": 7 z’j(‘/ @q ) Dated: 12.05.2015

ps

From:

The Sr. G.M. (Power System),
OPTCL, Bhubaneswar-17.

To:

As per distribution list

Sub: Minutes of 85" Power System Operational Co-ordination meeting held on
29.04.2015 at PTC, Chandaka .

Sir,
Please find enclosed herewith the minutes of 85" Power System Operational Co-

ordination meeting held on 29.04.2015 at Power Training Centre, Chandaka.

This is for your information & necessary action.

Yours faithfully;

Encl: As above ) /
(S uF- AR

Sr. G.M (Power System)

Copy along with enclosures forwarded to the Executive Assistant to CMD, Gridco / OPTCL
for kind information of CMD.




Distribution list 

1. The Director (Commercial), Gridco, Bhubaneswar
2. The Director (Operation), OHPC, Bhubaneswar
3. The CGM (O & M), OPTCL, Bhubaneswar
4. The CGM (Const.), OPTCL, Bhubaneswar
5. The CGM, (RT&C), OPTCL, Bhubaneswar
6. The C.G.M. (PP), GRIDCO, Bhubaneswar
7. The CGM (IT), OPTCL, Bhubaneswar
8. The Sr. G.M (C.P), OPTCL, Bhubaneswar
9. The Sr. G.M. (TP&C), OPTCL, Bhubaneswar
10. The Sr. G.M. (CPC), OPTCL, Bhubaneswar
11. The Sr. G.M.(O&M), Zone-I, Narendrapur

12. The Sr. G.M.(O&M), Zone-II, Meramundali

13. The Member Secy., (GCC), OPTCL, Bhubaneswar

14. The C.E.O., CESU, Bhubaneswar 
15. The A.O.,WESCO Utility, Burla
16. The A.O., NESCO Utility, Balasore
17. The A.O., SOUTHCO Utility, Berhampur
18. The G.M. (Telecom), OPTCL, Bhubaneswar
19. The Vice President (O), IMFA, Choudwar
20. The D.G.M (Electrical), IbTPS, OPGC, Banharpali
21. The G.M. (O &M), CPP, NALCO, Angul
22. The DGM (O & M), NTPC (TTPS), Talcher
23. The G.M., HINDALCO, Hirakud
24. The D.G.M. (Power Distribution), RSP, Rourkela
25. The D.G.M. (Elect.), JINDAL Stainless Ltd, Duburi
26. The G.M., Vedanta Aluminium Ltd., Jharsuguda
27. The G.M.(Elect.), Bhushan Steel & Power Ltd, Budhipadar
28. The Sr. G.M. (Elect.), Bhusan Steel Limited, Meramundali

29. The S.E., Machhakund
Odisha Power Transmission Corporation Ltd. Bhubaneswar.


Minutes of 85th PSOC meeting held on 29.04.2015 at PTC, Chandaka
List of participants is at Annexure.

Sr. G.M (Power System) welcomed all the participants to the 85th Power System Operational Coordination meeting and highlighted the system performance during the month of March’2015 and overall power scenario of the State. He also emphasized on the drawal by all the Discoms during the month. 
The meeting was chaired by CGM (O&M), OPTCL. 

Manager (SS) took the agenda items for discussion. 

The review proceeded as follows: 
PART A: CONFIRMATION OF MINUTES
A.1: Confirmation of minutes of 84th PSOC meeting held on 26.03.2015
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2014/914(30), dated 08.04.2015 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting

Minutes of 84th PSOC meeting was confirmed since no comments were received.
PART B : SYSTEM PERFORMANCE
B1: Review of Grid Performance for the month of March’2015.
(A)  Frequency 

It was noticed that, during the month, 57.20% of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 57.36% during the month of February’15. The maximum and minimum System frequency during the month of March’15 was 50.47 Hz & 49.58 Hz respectively.

 (B)  Grid demand 

Grid demand for the month of March’15 was reviewed. The energy consumption during the month was 2203 MU. The maximum System demand of 3981 MW occurred on 25.03.2015 at 21:00 Hrs and minimum demand of 2219 MW occurred on 06.03.2015 at 15:00 Hrs. 
Deliberation in the meeting

It is observed that energy consumption during the month of March’ 15 was increased by 397 MU, while the peak demand during the month has increased by 368MW from that of February’15. The energy consumption during the month has been increased by 407 MU in comparison to March’14. The substantial increase of energy and peak was due to induction of M/s SSL (SEZ) load in the system. 
(C)  Voltage Profile of important Sub Stations in OPTCL System.

The Voltage profile at different 220 kV buses in OPTCL system during the month of March’15 was reviewed. It is noticed that Jayanagar 220 kV bus have experienced a maximum voltage of 246.93 kV, while minimum Voltage of 192.71 kV was experienced at Paradeep 220 kV bus. 
Deliberation in the meeting

Sr. G.M (PS) stated that high voltage at Jayanagar has been arrested to some extent in comparison to previous months. Powergrid has scheduled for installation of additional reactor at Jeypore by June’2015. O&M shall check the CVT at Meramundali.









      [Action: CGM (O&M)]
   
(D) Energy Generation / import during the month of March’15 
Energy generation and exchange during the month of March’15 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2203 MU. 
Deliberation in the meeting
Sr. GM (OHPC), UIHEP suggested for increasing of UIHEP generation to meet the irrigation requirement as well as to avoid spilling. Sr. GM (PS) stated that SLDC is taking all steps to optimize hydro generation.

[Action: SLDC] 

(E) Drawal of Machhakund Power

The drawal of Machhakund power during the month of March’15 was 31.514 MU against AP drawal of 30.503 MU 
In the last meeting Sr. G.M (O&M), Zone-I stated that bus modification work at Jayanagar S/S will be taken up after commissioning of Auto at Jayanagar. G.M (Telecom) stated that installation of OPGW equipments at Machhakund and Jayanagar by POWERGRID is expected to be completed by June 2015. After which, Remote Subscriber (RS) phone provision can be made from Jayanagar S/S. Southco Utility stated that around 1.5 MW load has been extended to Akusingh Grid by linking 33/11kV Substation Kumbhar Dhamuni.  Other linking lines as suitable are being taken up. 

In the month of March SLDC & GRIDCO officers had been to Machhakund PH to study the present metering arrangement in view of selling of Machhakund share to AP proposed by GRIDCO. It is proposed to divert the metering cubicle from TTPS to Machhakund PH for proper metering.
Deliberation in the meeting
CGM (O&M) stated that Auto at Jayanagar is expected to be charged by 2nd week of May 2015.   Bus modification work at Jayanagar S/S is will be taken up thereafter. G.M (Telecom) stated that installation of OPGW equipments at Machhakund and Jayanagar by POWERGRID is expected to be completed by June 2015, after which, Remote Subscriber (RS) phone provision can be made from Jayanagar S/S. Southco Utility stated that work for linking of 33 kV Gumuda feeder at Akhusing S/S is under progress. Other linking lines as suitable are being taken up. 
Gridco stated that APGENCO shall install their meters at Machhakund PH. As such diversion of metering cubicle from TTPS to Machhakund need not be required.  
[Action:-G.M (Telecom) / Sr.GM (O&M)-I / SOUTHCO Utility]
(F) DISCOM Drawal during the month of March’15 

The schedule and actual energy drawal by Discoms for the month of March’15 was reviewed. 
Deliberation in the meeting

It was noticed that CESU have overdrawn substantially to the tune of 60.946 MU while NESCO and WESCO have over drawn 11.96 and 8.69 MU respectively. SOUTHCO Utility have complied the schedule successfully. SLDC stated that ABT cell of Distribution Utilities are not being manned to take remedial measures for compliance / revision of drawal schedule. CESU stated that the drawal data displayed at SLDC is not correct, which led wrong prediction of day-ahead drawal.  It was decided that SLDC shall monitor the over drawal by DISCOMs and do the needful for compliance of the drawal schedule. The data displayed shall be checked by the Discom representatives and Telecom officers at SLDC. 
 [Action: All Distribution Utilities, SLDC, Telecom]
(G) Under Frequency Relay operation in OPTCL System during the month of March’15.

There is no UF Relay operation occurred during the month of March’15 as the frequency had never gone beyond 48.50 Hz.

PART C – issues of 108th OCC meeting of ERPC
C1: PLCC Status installed in Eastern Region

In 106th OCC, Powergrid agreed to restore and maintain the PLCC system at both ends (its own end as well as the constituent end) of a line wherein the other ends are not being maintained by respective constituents for some reasons or others. It was decided that the cost of restoration and maintenance of PLCC system at such (constituent) ends of the line will be borne by the respective constituents. In addition to this the constituents also agreed to extend all possible support to Powergrid in carrying out the above work. 

It was decided in the OCC that the list of such PLCC equipments shall be forwarded to PGCIL. POWERGRID have written a letter to CGM (O&M) for execution of an agreement in this regard. 

EL Status

In the last meeting, CGM (O&M) stated that commissioning of EL at Bidanasi has been done. Commissioning of EL at 11 Nos. of S/Ss shall be completed by April 2015. It was also decided that OHPC may take action for installation of EL at their Balimela, Rengali and Upper Kolab PHs and synchronization of Indravati EL with GPS.  

Deliberations in the meeting.

It was decided that G.M (Telecom) shall prepare the estimate only for those PLCC required to be maintained and forward to Powergrid. GM, O&M stated that 10 Nos. of EL have been commissioned. EL at Theruvali and Jayanagar are to be commissioned. OHPC stated that procurement of EL for Balimela, Rengali and Upper Kolab is under process. Synchronization of Indravati EL with GPS is expected to be completed within two months.  

[Action: CGM (O&M) / GM (Telecom.) / OHPC]

C2: Status of UFRs healthiness installed in Eastern Region.

It was decided in the 105th OCC meeting of ERPC that constituents should check the UFR enunciation & PT fuse and thereby certify on monthly basis that UFRs are in service.
Further, it was decided to monitor the quantum of load connected to the UFR and constituents are to submit, on quarterly basis, maximum and average load quantum of each feeder with UFRs connected. OCC advised all constituents to submit the certificate on regular basis.

Deliberations in the meeting.

GM (O&M) stated that certificate for healthiness status of UFR is being forwarded to ERPC regularly. 
C3: Status of “Third Party Protection Audit”

List of observations in 1st third Party Protection Audit along with updated compliances received from the constituents are available in ERP website 

The format for data collection to initiate 2nd Third Party Protection Audit is circulated to the constituents and also made available in ERPC website. All constituents requested to send requisite information by 16th March 2015. On site inspection of 2nd Third Party Protection Audit will commence after receiving the data.

In 107th OCC, members agreed to start 2nd Third Party Protection Audit from the month of May, 2015 with the check lists already designed and modified by ERPC in line with recommendation of the Task Force Committee. It was decided that relevant information as per data format already circulated may be collected during actual visit of Audit team. Finally it was decided in the 108th OCC meeting to conduct 3rd Party Protection Audit from the month of June, 2015.

Deliberations in the meeting.

CGM (O&M) stated that data for all S/Ss have been furnished to CPRI. Inclusion of Balasore sub-station in place of Joda shall be proposed. 
[Action: C.G.M. (O&M)]
C4: Status of 80 MVAr line reactor of 400 kV Meramundali-Angul at Meramundali.

The line reactor of 400 kV Meramundali-Angul at Meramundali was taken out of service without getting clearance from ERLDC, for which OCC expressed its concern. It was decided in the OCC that OPTCL shall investigate and furnish a report to ERPC for taking out the reactor from service without obtaining clearance from ERLDC.

Deliberations in the meeting.

GM (O&M) stated that the reactor at Meramundali had hand tripped as the WTI temperature reached more than 900 C. Alarms had come before one hour at 850 C. It was advised to intimate ERLDC / SLDC before doing any switching operation in future. O&M agreed to take care.
[Action: SLDC / O&M]

C5: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG) S/s 

400/220 kV, 2 X 315 MVA S/S at Bolangir has been established by Powergrid as part of  ISTS system & the following 220 kV interconnecting lines were envisaged to be established by OPTCL:
(i) LILO of OPTCL’s Katapali-Bolangir line (One ckt) at Bolangir (PG): 
(ii) Bolangir (PG)–Bolangir S/C line.

(iii) Bolangir (PG)-Kesinga S/C line. 
Deliberations in the meeting

The statuses of the lines are as follows: 

(i) LILO of OPTCL’s Burla-Bolangir line (One ckt) at Bolangir (PG): June, 2015
(ii) Bolangir –Bolangir (PG) S/C line, which is a part of proposed Bolangir- Kesinga D/C line with one ckt LILO at Bolangir(PG): Excavation work started.

(iii) Bolangir PG-Kesinga S/C line (Part of Bolangir-Kesinga D/C line): Work started
[Action: CGM (O&M) / CGM (Const)]
C6: Future requirement of Special Energy Meters and DCDs 

The requirement of frequency based ABT Special type meters up to 2014 has been procured by Powergrid and likely to be exhausted shortly. Beneficiary Constituents of ER are requested for assessment of their requirement of Special Type Energy Meters and DCDs for the period from 2015 to 2017 and intimate the same in the next OCC meeting so that the advance action for procurement can be taken.

SLDC has furnished the list of defective DCDs to ERPC. It was decided in the 108th OCC meeting that the list shall be forwarded to Powergrid for taking necessary action.

Deliberations in the meeting

SLDC stated that DCDs may not be required as Powergrid is going to adopt AMR for all the metering points soon. However, the existing DCDs may be replaced by Powergiid. SLDC shall intimate Powergid accordingly.
[Action: SLDC]

C7: Certification through BIS as per IS 18001:2007 to all generating / transmission units. 

In the last meeting CGM (O&M) stated that BIS has not responded yet. However, BIS will be reminded again.  

Deliberations in the meeting.

CGM (O&M) stated that BIS is not responding in spite of reminders by OPTCL. 
[Action: CGM (O&M)]
C8: Pollution mapping for Eastern Region 

In 107th OCC meeting, Powergrid informed that the Pollution measurement would start from 1st April, 2015. Constituents were requested to complete the “First set of Pollution Measurement” by 15th April, 2015 and communicate the measurement results to the ERPC, Powergrid and CPRI in the prescribed format (available in the ERPC website). 

In the last meeting, Southco Utility stated that out of 26 Nos of locations hanging of insulators for 5 Nos have been completed. The remaining locations shall be completed soon. Other Distribution utilities shall take necessary action for hanging of insulators at their specified locations.

Deliberations in the meeting.

Southco Utility stated that Southco Utility have completed all their 26 Nos locations. CGM (O&M) stated that measuring kits are being issued. Measurement will be completed by the end of June’2015. 
[Action: CGM (O&M)]

C9: Mock Black start exercises in Eastern Region–ERLDC

The mock black start exercise for OHPC stations for the FY 2015-16 has been scheduled by ERPC.  The test-1 schedule is as detailed.

1. Upper Kolab HEP

Last week of May, 2015
2. Rengali HEP


2nd week of June, 2015
3. U. Indravati HEP

3rd week of June 2015
4. Balimela HEP


1st week of November, 2015

Deliberations in the meeting.

OHPC and SLDC agreed to conduct the black start exercise as per schedule.

 [Action: OHPC / SLDC]

C10: Proposal for review of Power Demand Order (PDO) condition for HVDC Gazuwaka poles, in view of repeated tripping in South Odisha.

ERLDC had made a presentation on the existing and proposed PDOs at HVDC Gazuwaka poles and sought views of OPTCL for implementation in the 106th OCC meeting of ERPC. In 29th PCC, OPTCL agreed to the proposal. 

In the OCC meeting it was decided that, OPTCL shall study and forward their comments to ERPC / ERLDC.

Deliberations in the meeting.

It was decided that OPTCL shall write ERLDC to intimate the basis of determining the quantum of power export after which views can be forwarded.

[Action: CGM (O&M)]

C11: Overloading of 400 kV Meramundali-Mendhasal line

The loading of 400 kV Meramundali-Mendhasal line as observed was 504 MW towards Mendhasal, out of which 56 MW power was flowing towards Baripada PG from Mendhasal through Mendhasal-Baripada 400 kV D/C line. Normally power flow is from Baripada to Mendhasal. This reverse power flow might be due to drawal by WB system. Moreover reactive power flow from Baripada was 120 MVAr. The reactive flow could have been reduced by isolating one of the 400 kV ckts. ERLDC may take appropriate action to reduce the reactive flow.

Deliberations in the meeting
CGM (O&M) stated that the problem can be resolved after charging of 2nd ckt 400 kV Meramundali-Mendhasal line. SLDC may suggest ERLDC for isolating one of the 400 kV Baripada-Mendhasal line for VAR management on real time basis. In the OCC, ERLDC intimated that OPTCL is not paying reactive charges pertaining to this line. ERPC advised OPTCL to check whether reactive charges are paid pertaining to the line or not.  
[Action: SLDC / Gridco/ OPTCL]
C12. Commissioning of new Transmission elements.

1. NTPC Barh Unit-V (660 MW) was synchronized at 15:00 Hrs on 01.03.2015 but tripped. Subsequently synchronized at 19:55 Hrs on 04.03.2015 but tripped at 21:20 Hrs of same day. 
2. 400 kV GMR-Meramundali S/C line was idle charged at 14:40 hrs of 18.03.2015. Subsequently GMR Unit-III was shifted to Meramundali at 21:11 hrs of 18.03.2015.
3. 3 X 500 MVA, 765/400 kV ICT-IV at Angul was charged at 16:15 hrs of 24.03.2015. Subsequently 3 X 80 MVAR L/R of 765 kV Angul-Jharsuguda line was charged at Angul at 19:02 hrs of 24.03.2015.

4. 765 kV Angul-Jharsuguda ckt-II was finally charged at 15:41hrs of 30.03.2015.

5. 765 kV, 330 MVAR B/R –II at Angul was charged at 16:53 hrs of 28.03.2015.

PART-D – Operational Issues

D1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of March’15 was reviewed. Maximum 47 numbers of such messages were issued to WESCO Utility followed by 39 Nos. each to NESCO Utility and 37 Nos. to CESU while 22 Nos to Southco Utility. Total over drawal by all DISCOM utility were 82.85 MU during the month. 
Deliberations in the meeting.

SLDC stated that the Distribution utility officers deployed at SLDC are being coordinated before issue of non compliance messages. Since the officers of distribution utilities are not available in the night shift at SLDC or at their respective DSOCCs, it was not possible to make contact with them.  All the Discoms were requested to predict their drawal in a realistic manner to avoid over drawal / under drawal. Frequent revision of drawal schedule may be avoided as far as possible.

[Action: All Distribution Utility]
 D2: Availability of data of real time power flow of feeders covered under Under-frequency Load shedding scheme (UFLS) and lower relief expected to obtained in real time system operation

In the last meeting DGM (Telcom.) stated that the delivery date was 06.04.2015. The firm has requested to accept DD in place of CBG. However the firm is yet to submit offer for inspection.

Deliberations in the meeting.

Sr. G.M. (Telecom) stated that inspection of MFM is in progress. Work will be completed soon after receipt.
[Action: Sr.GM (Telecom)]
D3: Reporting of major incidents.

In the last meeting, GM (O&M) stated that, E&MR wing of respective circles are requested to create awareness between the Shift Engineers for study of the relay indications for proper reporting. 
The Electromagnetic Relays at Narendrapur and Bhanjanagar shall be replaced by 15th April’2015.

Deliberations in the meeting.

The Electromagnetic Relays at Narendrapur and Bhanjanagar has been replaced.
[Action: CGM (O&M)]
D4: Levy of Reactive Energy Charges due to injection of VAR to the grid.


It is noticed that GRIDCO is the only constituent in ER, liable to pay Reactive Energy charges due to injection of reactive power to the pool at the following inter connection point for the period from 23.02.2015 to 01.03.2015.

(1) 400kV Indravati-Indravati PG
(2) 400kV Meramundali- Angul PG D/C
(3) 220kV Rengali – Rengali PG D/C
(4) 132 kV Baripada PG – Rairangpur
In the last meeting, GM (O&M) stated that, the reactive power flow at both the ends of transmission line need to be compared to ascertain the VAr injection.  OPTCL / SLDC shall compare such VAr flow and confirm whether the line itself is generating VAr and do the needful.

Further, long transmission lines with less loading are responsible for reactive power injection to the grid. It may be examined to keep minimum number of circuits in service to evacuate power from Generating Stations during low generation e.g. Balimela-Jaynagar, Indravati-Theruvali, JSPL-Meramundali.

Deliberations in the meeting.

It was decided that SLDC shall monitor the VAr injection of IPP / CGP on real time basis. Minimum number of ckts shall kept in service in case of low hydro generation. Sr. G.M (PS) stated that Balimela HEP is keeping two Units in synchronization with minimum generation (10 MW each) to meet its auxiliary requirement in contingency conditions, even though DG set is available. OHPC stated that Balimela units cannot sustain till DG set operation. However, the problem can be sorted out after renovation of units.

[Action: OHPC / SLDC]   
D5: Prolonged outage of transmission elements and tentative revival dates

Deliberations in the meeting

The updated revival / tentative revival of prolonged outage of transmission elements are as detailed.
	Sl.No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220 kV Jayanagar-Theruvali ckt-III Breaker
	Breaker defunct
	May 2015

	2
	220/132 kV, 100 MVA Auto-II at Duburi  
	After inspection by repairer, date can be ascertained
	Can be ascertained after inspection.


[Action: CGM (O&M)]

D6: Communication issues 
(i) Installation of communication equipment by CGPs / Industries.

The status of data communication from CGPs as deliberated is as follows

	Sl. No
	Name of CGP
	Present status

	1
	M/s Sri Ganesh Metalicks Ltd.
	M/S Sri Ganesh proposed for communication through wireless communication mode. They have been permitted for testing. 

	2
	M/s IFFCO, Paradeep
	Outdoor commissioning work is completed. Testing of DPLC is in progress.RTU not commissioned.

	3
	M/s MSP Mettalicks
	PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited.

	4
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far.

	5
	M/s Adhunik Metallics
	PLCC & RTU installed. Database has prepared by OPTCL. Commissioning of RTU is yet to be done.

	6
	M/s Rohit Ferrotech
	PLCC established and inspection by Telecom Engineers completed.  Data base has already been prepared by OPTCL.    

	7
	M/s VAL, Jharsuguda
	No isolator status is available. MW/ MVAR not available for Sterlite 1/2 line, station transformer / Smelter. CBs of Bus coupler data, Bus-1 kV/Hz are not available. As per MOM between OPTCL & Sesa Sterlite, Jharsuguda dtd 22.09.2014, provision for telemetry data will be extended within 6 months.(March,2015). The CGP is not responding.


Sr. G.M (CP) / Member Secretary, GCC stated that after receiving the updated information from Telecom, a meeting at zonal level shall be convened to discuss the issue.
[Action: Sr. G.M. (Telecom) / Sr. G.M (CP)]
(ii) Availability of Tap position of 400kV ICTs at Mendhasal.

Tap position data for Meramundali and Mendhasal ICTs are not available for display through SCADA. 

G.M. (Telecom) stated that PCB for ICT –II has already been installed and working. PCB for ICT-I will be installed after availing of line shutdown.

Deliberations in the meeting
Sr. GM (Telecom) stated that Tap position data for Meramundali shall be made available by May 2015.
[Action: Sr.G.M. (Telecom)]

(iii) Availability of data at SLDC.

The data for the following elements are not available for SCADA display.

(a)  Power flow through 132 kV Paradeep- Jagatsinghpur ckt.
(b) Power flow through 132 kV Jajpur Road- Anandpur ckt.
(c)  Machhakund generation data
(d) JSPL (Angul) generation data
Deliberations in the meeting

Sr. G.M. (Telecom) stated that, for item (a) and (b), transducers have been installed and cabling completed. Integration of Transducer with RTU shall be done shortly. Item (c) has already completed. (d) M/s JSPL has been asked to restore its generation data at SLDC, but not responding.

 [Action: Sr. G.M. (Telecom)]

(iv) Integration of new element.

M/s SSL-SEZ became a consumer of WESCO Utility with effect from 20.03.2015 and importing power through intra State open access from its CGP at Jharsuguda as well as from other utility. The drawal of SSL-SEZ needs to be integrated to SCADA to ascertain WESCO Utility drawal and State demand on real time basis. Telecom may explore for integration of SSL-SEZ drawal and display in the VPS of SLDC control room.

Deliberations in the meeting

Sr. G.M. (Telecom) stated that, this issue has been raised in the SCADA meeting of ERPC.

    [Action: Sr. G.M. (Telecom)]

D7: Display of dashboard data.

On 24.02.2015, IT representative presented a demo to all Discoms after the PSOC meeting regarding display of Dash board data in the new format and invited feedback from all Discoms, which is yet to be received. G.M. (Telecom) shall nominate a nodal officer to receive the complaint of Discoms on real time basis for taking necessary action.

Deliberations in the meeting

The Discoms have furnished their feedback. It was decided that IT shall present a demo before SLDC and Telecom to examine the working of the Dashboard. 
    [Action: CGM (IT) / Sr. G.M. (Telecom)/SLDC]

D8:  Communication to Balimela HEP.
Very often it is noticed that the land line / PLCC telephone of Balimela HEP is remaining out of service. Due to failure of communication the Black Start exercise could not be conducted. Also important instructions could not be communicated. It is suggested to strengthen the communication system by providing additional Mobile phone to Balimela HEP as well as to other HEPs also
Deliberations in the meeting.
OHPC has agreed to provide additional mobile phone at Balimela control room. 
    [Action: OHPC]

D9:  Non compliance of OGC provision by UI HEP.
Unit 1 of UI HEP was under shutdown for Annual Maintenance. On 17.04.2015 UIHEP requested SLDC to allow shutdown of Unit-2 for Annual Maintenance for the period from 24.04 to 19.05.2015. Since one unit was already under shutdown, SLDC did not issue shutdown of permission for Unit-2. UI HEP was taken shutdown of their Unit-2 on sou-motu, without waiting the consent of SLDC, which is a violation of OGC provision.

Deliberations in the meeting.
Sr. G.M, UIHEP stated that SLDC has permitted for shutdown of Unit-2. OHPC has intimated the same before availing the shutdown. As such there is no violation of OGC provision.

D10: DISCOM Issues 
SOUTHCO:

ABT issue

1. The data in the new format for ABT Dash Board is not functioning properly except only the current Drawl. 

2. Feedback on the Data display system has been submitted.

3. BSNL has been requested for providing the leased line with necessary application and is under process.

4. Request for taking remedial measures for providing all 57 nos interception point data to Southco with Auto transformer Data as well as Energy reading at 00.00hrs of all points each day. 

5. Low voltage problem in Gunupur, Akhusingi &Parlakhemundi area during BTH power in peak hours.

6. After charging of Dabugaon  Grid S/s South is drawing power. At present one No. of 12.5 MVA has been commissioned at Dabugaon, which is inadequate to meet the load requirement of the area. 2nd 12.5 MVA Tfr may be installed. 

Deliberations in the meeting;

After receiving the feedback IT shall examine the dashboard function. Installation of 220/33 kV S/S at Gunupur has already been proposed. Installation of 2nd 12.5 MVA Tfr at Dabugaon is being examined.
NESCO

1) Display of Dashboard Data of NESCO as per the proposed format submitted in the 79th PSOC meeting.

2) Long time server error problem to be sorted out, which had been occurred from 22.04.15.

Deliberations in the meeting;

Dashboard issue has been deliberated above.

[Action:  Sr.G.M. (Telecom)/ CGM (IT)/ SLDC] 
PART E: OPERATIONAL PLANNING

E1:  Commissioning status of New Transmission elements. 

The status of commissioning of new transmission elements is as follows:

	   Sl. No
	    Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by June 2015.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal, which is under progress.

	3
	Commissioning of 400 kV Ib-Meramundali D/C line.
	400kV SSEL-Meramundali line has been idle charged from SSEL end. Due to theft of conductor line could not be charged. Expected to be charged by end of June’2015. 

	4
	Commissioning of 400 kV Duburi-Meramundali D/C line.
	Work is in progress after disposal of Case. Expected by the end of May 2015. 

	5
	Commissioning of 220 kV Bidanasi-Cuttack line
	Work in progress and expected to be completed by June 2015.

	6
	Commissioning of 220/132 kV Cuttack S/S
	Work in progress and expected to be completed by June 2015.

	7
	Commissioning of 132 kV Baripada (PG)-Jaleswar line
	Work has already been started, which will be completed by December 2015.

	8
	Commissioning of 220/132 kV Kesinga S/S
	Work under progress. Expected by September 2016.

	9
	Connectivity to Keonjhar PG
	Proposal is mooted to be placed in the BoD meeting for connecting the proposed 220 / 33 kV Keonjhar S/S and with Turumunga S/S through 2 Nos. 220 kV ckts each. 

	10
	LILO of 220 kV Burla - Bolangir line (one ckt) at Bolangir(PG)
	Work awarded. Expected to be completed by June, 2015

	11
	220 kV Bolangir –Kesinga D/C line and LILO of one ckt at Bolangir(PG).
	220kV Bolangir - Kesinga D/C line is under construction. It is proposed to connect Bolangir (PG) through LILO arrangement of one ckt. Work has already been started.


[Action: CGM (Construction)]

Status of Discom’s action plan for power drawal from the S/Ss expected to be commissioned in near future. 
	   Sl. No
	    Name of the sub-station
	Probable month of commissioning
	Name of DISCOM
	Action taken by Discoms

	1
	132/33kV, 2x20 MVA  Banki 
	Charged
	CESU
	33 kV feeder shall be charged by April’15

	2
	132/33kV, 2x20 MVA  Konark 
	May’15
	CESU
	Line existing

	3
	132/33kV, 2x31.5 MVA  Samuka beach 
	Apr’15
	CESU
	33 kV Completed by end of Apr’15

	4
	132/33kV, 2x20 MVA  Khajuriakota 
	December’15
	CESU
	33 kV feeder work shall be completed by June’15

	5
	132/33kV, 2x40 MVA  Sarasmal 
	Charged
	WESCO Utility
	

	6
	132/33kV, 2x40 MVA  Kalunga 
	May’15
	WESCO Utility
	

	7
	220/33kV, 2x20 MVA Banei 
	Dec’15
	WESCO Utility
	

	8
	132/33kV, 2x12.5 MVA  Dabugaon 
	Apr’15
	SOUTHCO Utility
	33 kV Dabugaon and Papadahandi feeder completed

	9
	132/33kV, 2x12.5 MVA  Umerkote 
	Apr’15
	SOUTHCO Utility
	33 kV feeder shall be completed by May’15

	10
	132/33kV, 2x20 MVA  Nawapara 
	Charged
	WESCO Utility
	33 kV feeder work completed.

	11
	132/33kV, 2x20 MVA  Padmapur
	June’15
	WESCO Utility
	

	12
	132/33kV, 2x20 MVA  Udala 
	Dec-15
	NESCO Utility
	Line existing

	13
	132/33kV, 2x20 MVA  Somanathpur 
	May’15
	NESCO Utility
	33 kV feeder existing


As decided in the last meeting, CESU stated that action is being taken for construction of 33/0.4 kV S/S at Mendhasal to avail power supply for Mendhasal area. 

Action: [CGM (Const.) / All Dist. Utility]

E2: Installation of Energy Metering at Hydro / Traction & Solar projects.

ABT compliance meters have been installed in all OHPC stations except UIHEP. As per report received four sets of meters have been installed at 220kV UIHEP_Theruvali circuits. Installation of meters at ICT-I & II is yet to be done.
Billing from those energy meters is yet to be done by Gridco. 

WESCO Utility shall approach Rly. Authority for installation of required Class of CT & PT at their Bhalulata, Bamara and Chandiposi Traction points.

Deliberations in the meeting

OHPC stated that meters at Indravati ICT have been installed. Gridco may take action for billing from these newly commissioned feeder meters. SLDC suggested for providing PT supply to the energy meter from the respective feeder line PTs. 
WESCO Utility shall approach Rly. Authority for installation of required Class of CT & PT at their Bhalulata, Bamara and Chandiposi Traction points.

[Action: Sr. GM (O&M)-II / Gridco / WESCO Utility / OHPC] 
E3: Metering issue of TTPS.

Installation of feeder meters at TTPS outgoing feeders is yet to be completed.
Deliberations in the meeting

The meeting with NTPC authority is yet to be convened by Gridco. 

[Action: Gridco / TTPS] 
E4: Shifting of 33 kV line from Balasore Grid S/S yard to facilitate separation of Tfr and Balasore Alloy bays.

In the last meeting, NESCO Utility stated that estimate for shifting of 33 kV line from Balasore Switchyard is under process. CGM (O&M) stated that NESCO Utility has to expedite the work, as it is very much delayed.

Deliberations in the meeting:
NESCO stated that the work has already been started and completed by end of May 2015. 

[Action: NESCO Utility]
E5: Major Events in the month of March’15:
132/33kV, 2 X 40 MVA  Sarsamal sub-station & 132/33kV, 2 X 20 MVA  Samuka sub-station commissioned during March’ 2015.

E6: Important Grid Incidences during the month of February’15.

Important incidents occurred during the month of March’15 were reviewed.

Deliberations in the meeting:
GM (O&M) stated that all the S/Ss have already been instructed to furnish reports after due analysis in coordination of E&MR officers.
[Action: C.G.M. (O&M)]
E7: Outage of major transmission Elements during the month of March’15. (Above 10 hrs)
Outage of major transmission elements above 10 hours during the month of March’15 was reviewed.

Deliberations in the meeting

Most of the outages are due to conductor / jumper snapping and bursting of LAs. O&M may examine replacement of old LAs to avoid interruption. 
[Action: C.G.M. (O&M)]
E8: Review of Outage Program of State Generators / Transmission elements for the month of May’15:

Tentative Outage programme for State Generators for the month of May’15 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1

# 6
# 7
	18.04.15 to 31.07.15
17.02.14 to continue

28.02.15 to 30.04.15
	Capital Maintenance
Programming for R, M & U

Annual Maintenance

	2
	Chiplima
	# 1
#3
	15.05.15 to 31.05.15

15.02.14 to continue
	 Annual Maintenance

Programming for R & M 

	3
	Balimela
	# 1
#4
#8
	31.01.13 to continue
15.04.15 to 10.05.15

15.05.15 to 10.06.15
	Programming for R & M 

Annual Maintenance

Annual Maintenance

	4
	Rengali 
	# 1

# 2
	11.05.15 to 31.05.15

11.05.15 to 31.05.15
	Governor Rectification 

Governor Rectification

	5
	Upper Kolab 
	# 1
	05.05.15 to 28.08.15
	Capital Maintenance 

	6
	Upper Indravati 
	# 1

# 2
	27. 03.15 to 22.04.15

24.04.15 to 18.05.15
	Annual Maintenance

Annual Maintenance


E9: Generation Program for the month of May’15.

Generation schedule for the month of May’15 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Programme (MW)
	Reservoir Level as on 01.04.14
	Reservoir Level as on 01.04.15
	MDDL
	High Flood    Reservoir Level

	
	May’15
(1st fortnight)
	May’15
(2nd fortnight)
	
	
	
	

	HPS, Burla
	60+40
	30+20
	619.04ft 
	614.02ft
	590 ft.
	630 ft.

	Balimela
	80
	170
	1497.90ft 
	1493.30ft
	1440 ft.
	1516 ft.

	Rengali
	100
	100
	121.10mt

1.78mt mtr mt
	120.05mt mt
	109.72mtr 
	123.5 mtr.

	U.Kolab
	80
	80
	853.16mt mt
	853.76mt
	844 mtr 
	858 mtr.

	U.Indravati
	300
	300
	637.55mt mt
	636.18mt mt
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2736.35ft 
	2730.50ft ft
	2685 ft.
	2750 ft.

	TOTAL
	690
	730
	
	
	
	


PART F: OTHER ISSUES

F1:  Suspension of ABT for the block period from 42 to 49 on dated 27.03.2015 

On dated 27.03.2015 SLDC instructed TTPS for backing down of generation to limit he Auto-2 Power flow, to allow shutdown of 132 kV TTPS-Duburi D/C line. Auto-1 was under shutdown. During the process of shutdown all Stage-I Units of TTPS got tripped.   

However, TTPS on dated 31st March 2015 has requested for suspension of ABT for the block period from 42 to 49 of 27.03.2015 considering the case as a transmission constraint. Again on 20.04.2015 TTPS in its mail indicated that the Deviation Charges has been suspended for the block period from 41 to 49 of 27.03.2015.

Deliberations in the meeting:
TTPS (NTPC) stated that the commencing block for suspension of ABT was wrongly mentioned as “41” instead of “42”. As such the cancellation period of ABT may be considered from block 42 to 49. A separate letter in this regard shall be furnished by TTPS. It was decided that, since this is a case of Grid disturbance, as per provision under Regulation 6.5.17 of IEGC, the scheduled generation of TTPS shall be deemed to have been revised to be equal to their actual generation.
[Action: SLDC / Grido/TTPS]

F2:  Billing dispute raised by JSPL (Barbil)

JSPL (Barbil) has stated that NESCO is raising monthly energy bill without considering the quantum of energy import from their Angul CGP through Intra state Open access transaction.
Deliberations in the meeting:

NESCO utility officers stated that they are preparing the provisional bill considering the actual meter reading, which is revised deducting the OA quantum, on receipt of monthly Energy Accounting data from SLDC. It was suggested by SLDC to consider the block wise import schedule through OA while computing the SMD of the Industry. JSPL may approach NESCO for revision of contract demand.

[Action: NESCO / JSPL (Barbil)] 
F3.  Date and Venue of the next (86th) PSOC meeting:

The date and venue of 86th PSOC meeting shall be intimated to all the Members.

ANNEXURE
[image: image2.png]85" Power System Operational Co-ordination Review Meeting
[ At 11:00 A.M. on 29.04.2015]

[At Power Training Center, OPTCL, Chandaka, Bhubaneswar]

m Organisation Mobile No. E-mail Address
1

. P Titepativy T Em (Cen)

d
. .bpmishra’
conirns|_core, | 9438907019 |eleberglie o),
y ( frefe

Sad M R Mehaut Co G (P Si_pC

—_—
N

I
n

Signature

—

2 ¢ - -
& { . R

—
S

—
W

A
PR o i

17 P/l . k . S o AN h\jﬂ ™M (i.r(d’ G}\y( C}L’ 28 [ 21")")0 ke o € !‘Ail(‘mnil (onn

3 N3 cq0- Xt L[ 44 i =
5 ndwe s mafiia
/’VEg/ 0y Y389tk eet gw‘{%esc‘c 0l his - don,

Sentoyokt (3
Gwmatl . Cvmy
akbd - jcv\}ﬂu@ b mud

_18 S A Pollra r\«owf‘f{v L) e D

19 | F. AR DEY

Q42705 72°%

qy 375 St e 7[

0[Py ) g%‘// ()i I@,/;su AU Ke769 ¢ |f 6 Cesee ok A -

21 | PR Jena ACM NTPc/ﬂ?s O43F2649€0 Pmmtgam@ ntpcle Sin Do gl

22 1R v PMC»NDK ALY NTPQ/B@%%%?S?LU)} "(vradw«i(@v\ﬂc-coq

/

T Endal ek - ned

’ -
$ g R

26'&-‘@5\‘&&4\9» ACam | ST [ Tuzsegnee o8
27 | Sk e | P | 07T gyaeqe 72)L ek santitd v

ell. Cxmwr s hov

23 P L/\ /{"3[\ [QZ\&M D (;] /\/\_ /\[TrC/"’ TH (‘{ L/j)(\/'l,f Py ‘fﬁfvfa/\ﬂ“ ¢ N(/;(( , 4 /@'@mfé ly

24 |Svnitso potrasin [ DM TP Q717 4I S 5R6 [Santpapmec e e

25 Rf”*/*k T paEM Tole  [AA 38250074 | ) . Lol 1

bt Levee | Chould
o oflcl.o Lt n ‘CL YD./‘ N

Ele Likdal &

ST Hed. <« w

({L‘ Y Q““‘D:f é c\(‘




     [image: image3.png]Li ‘r\;‘xl‘;.}\;o\ép — L r\,(A‘th

(B ey, (e

54 32904/0
G L2290 73U |59 PP Chvecdic e io] L

q ¢(/ 1990772y ?é(pmfxz\nwe i N





