[image: image1.png]STATE LOAD DESPATCH CENTRE

OFFICE OF THE Sr. GENERAL MANAGER (POWER SYSTEM)

ODISHA POWER TRANSMISSION CORPORATION LIMITED
GRIDCO Colony, P.O.- Mancheswar Rly. Colony, Bhubaneswar-17, FAX-0674- 2748509

CIN - U401020R2004SGC007553

No-SGM (PS)-PL-15/2015 / 2 W (30) Dated: | 0.09.2015

From:

The Sr. G.M. (Power System),
OPTCL, Bhubaneswar-17.

To:

As per distribution list

Sub: Minutes of 89™ Power System Operational Co-ordination meeting held on
29.08.2015 at PTC, Chandaka .

Sir,
Please find enclosed herewith the minutes of 89" Power System Operational Co-

ordination meeting held on 29.08.2015 at Power Training Centre, Chandaka.

This is for your information & necessary action.

Yours faithfully;

Encl: As above _
‘ [0 - szS
Sr. GM

(Power System)

Copy along with enclosures forwarded to the Executive Assistant to CMD, Gridco / OPTCL
for kind information of CMD.




Distribution list 

1. The Director (Commercial), Gridco, Bhubaneswar
2. The Director (Operation), OHPC, Bhubaneswar
3. The CGM (O & M), OPTCL, Bhubaneswar
4. The CGM (Const.), OPTCL, Bhubaneswar
5. The CGM, (RT&C), OPTCL, Bhubaneswar
6. The C.G.M. (PP), GRIDCO, Bhubaneswar
7. The CGM (IT), OPTCL, Bhubaneswar
8. The Sr. G.M (C.P), OPTCL, Bhubaneswar
9. The Sr. G.M. (TP&C), OPTCL, Bhubaneswar
10. The Sr. G.M. (CPC), OPTCL, Bhubaneswar
11. The Sr. G.M.(O&M), Zone-I, Narendrapur

12. The Sr. G.M.(O&M), Zone-II, Meramundali

13. The Sr. G.M. (Telecom), OPTCL, Bhubaneswar
14. The Member Secy., (GCC), OPTCL, Bhubaneswar

15. The C.E.O., CESU, Bhubaneswar 
16. The C.O.O.,WESCO Utility, Burla
17. The C.O.O., NESCO Utility, Balasore
18. The C.O.O., SOUTHCO Utility, Berhampur
19. The Vice President (O), IMFA, Choudwar
20. The D.G.M (Electrical), IbTPS, OPGC, Banharpali
21. The G.M. (O &M), CPP, NALCO, Angul
22. The DGM (O & M), NTPC (TTPS), Talcher
23. The G.M., HINDALCO, Hirakud
24. The D.G.M. (Power Distribution), RSP, Rourkela
25. The D.G.M. (Elect.), JINDAL Stainless Ltd, Duburi
26. The G.M., Vedanta Aluminium Ltd., Jharsuguda
27. The G.M.(Elect.), Bhushan Steel & Power Ltd, Budhipadar
28. The Sr. G.M. (Elect.), Bhusan Steel Limited, Meramundali

29. The S.E., Machhakund
Odisha Power Transmission Corporation Ltd. Bhubaneswar.


Minutes of 89th PSOC meeting held on 29.08.2015 at PTC, Chandaka
List of participants is at Annexure.

Sr. G.M (Power System) welcomed all the participants to the 89th Power System Operational Coordination meeting and highlighted the system performance during the month of July’2015 and overall power scenario of the State. He also emphasized on the drawal by all the Discoms during the month. 
The meeting was chaired by CGM (O&M), OPTCL. 

D.G.M. (SS), SLDC took the agenda items for discussion. 

The review proceeded as follows: 
PART A: CONFIRMATION OF MINUTES
A.1: Confirmation of minutes of 88th PSOC meeting held on 29.08.2015
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2015/3203(30), dated 19.08.2015 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting

Since no comments have received from the members, the minutes of 88th PSOC meeting was confirmed. 
PART B : SYSTEM PERFORMANCE
B1: Review of Grid Performance for the month of July’2015.
(A)  Frequency 

It was noticed that, during the month of July’15, 66.01% of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 58.88% during the month of June’15. The maximum and minimum System frequency during the month was 50.23Hz & 49.65Hz respectively.

 (B)  Grid demand 

Grid demand for the month of July’15 was reviewed. The energy consumption during the month was 2337 MU. The maximum System demand of 3994 MW occurred on 04.07.2015 at 21:00 Hrs and minimum demand of 2431 MW occurred on 25.07.15 at 16:00 Hrs. 
Deliberation in the meeting

It is observed that energy consumption during the month of July’ 15 was decreased by 24 MU, while the peak demand was increased by 20 MW from that of June’15. The energy consumption during the month has been increased by 198 MU while the average energy consumption was increased by 266 MW in comparison to July’14. 
[Action: SLDC] 
(C)  Voltage Profile of important Sub Stations in OPTCL System.

The Voltage profile at different 220 kV buses in OPTCL system during the month of July’15 was reviewed. 
Deliberation in the meeting

The maximum voltage of 246.29 kV, 244.67 kV and 243.35 kV occurred at Bolangir, Joda & Jaynagar 220 kV bus, while Bhadrak, Nayagarh  and Narendrapur 220 kV bus have experienced the minimum Voltage of 174.12 kV, 179.72 kV and 179. 90 kV respectively. 

Sr. G.M (PS) stated that high voltage at Jayanagar has been arrested to some extent in comparison to previous months. High Voltage at Bolangir and Joda S/S needs to be investigated. Bhadrak Voltage profile shall be improved only after charging of Duburi ICT.









        [Action: CGM (O&M)]
   
(D) Energy Generation / import during the month of July’15 
Energy generation and exchange during the month of July’15 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2336.84 MU. 
 (E) Drawal of Machhakund Power
The drawal of Machhakund power during the month of July’15 was 24.036 MU against AP drawal of 26.266 MU. Total generation was 52.6518 MU
In the last meeting, Sr. G.M (PS) stated that Machhakund generation was reduced due to shutdown of Machhakund units from 19.05.15 to 10.06.2015. Machhakund has extended power supply from 16.06.2015 only. Although agreed by Machhakund authority earlier, SLDC is not being allowed to draw more power in off-peak period to compensate State’s under drawal during peak period. OHPC / Gridco may take up the matter with Machhakund authority in this regard. It is also noticed that Jayanagar S/S is not exploring optimization of State’s drawal by providing matching load on real time basis. 

Gridco stated that AP is unwilling to avail full Machhakund share at present. Southco Utility stated that work for connecting 33 kV Gumuda feeder with Akhusing S/S is under progress. The work is being delayed due to construction of pile foundation for river crossing locations. It was decided that Sr. G.M (Telecom) shall explore the display of Machhakund generation at Jayanagar S/S to enable them for optimizing State’s drawal. OHPC shall convene a meeting between Machhakund authority, Gridco, OPTCL and SLDC soon.

Tap changer of power transformers may be used to optimize Machhakund drawal. It is noticed that Grid S/Ss are not using the Tap changer facility on real time basis for regulating drawal. They may be instructed to utilize the same and also ensure healthiness of the Tap changer.
Deliberations in the meeting

DGM, Upper Kolab stated that the he along with G.M EHT(O&M), Jayanagar had visited Machhakund PH during the month of July for a meeting. Machhakund authority has agreed to the proposal for drawal of more power by Odisha during off peak period to compensate the State’s share. Jayanagar S/S may explore the drawal during off peak period by providing matching load. It was decided that OHPC shall convene a meeting between Machhakund authority, Gridco, OPTCL and SLDC. Southco may expedite the construction of 33 kV line to connect Gumuda with Akhusing S/S.

Sr.G.M (Telecom) stated that display of Machhakund generation is available at the Telecom terminal at Jayanagar, which can be displayed at Jayanagar S/S control room through RVDU only. SLDC may place the requisition for the RVDU. 
Sr.G.M (O&M)-I and Sr. G.M (O&M)-II have agreed to operate the OLTC of Power Transformers at Grid sub-stations for regulating drawal. 
 [Action: OHPC / Southco / Gridco / SLDC/ O&M]

 (F) DISCOM Drawal during the month of July’15 

The schedule and actual energy drawal by Discoms for the month of July’15 was reviewed. 
Deliberation in the meeting

It was noticed that CESU & WESCO have overdrawn substantially to the tune of 60.78 MU and 53.888 MU respectively, while NESCO and SOUTHCO has overdrawn marginally during the month.  

CESU stated that they are estimating the day a head demand from the past drawal displayed at SLDC. It was decided that SLDC shall take all steps for displaying CESU’s real time drawal more accurately. The sub-stations, not integrated with SCADA may be incorporated manually to the drawal of CESU and compare with the actual to ascertain its accuracy.   
 [Action: All Distribution Utilities / SLDC]
(G) Under Frequency relay operation in OPTCL System during the month of July’15.

There is no UF Relay operation occurred during the month of July’15 as the frequency had never gone beyond 48.50 Hz. 
PART C – Issues raised in 112th OCC meeting of ERPC held on 21.08.15

C1: Furnishing data on Power Purchase Agreements (PPA)

You are aware that Central Electricity Authority has been collecting data from different sources on various aspects of the power sector, to disseminate the information to all the stakeholders of the sector. As a part of the process, CEA decided to build a data base on Power Purchase Agreements (PPAs) which are required for assessing the installed generation capacity available in the states. Accordingly, a format was devised to collect the data from all the DISCOMs on a regular basis, for analysis and report on various PPA- related issues. The format is given at Annexure-B.7. This data would be used to make policy decisions for the overall development of the power sector and to bring out a quarterly publication for stake-holder benefit.

Therefore, constituents are requested to furnish the details of PPAs (long, medium and short term) from existing and proposed power plants as per the format to CEA by mail (email: rmrao@nic.in and rstomar@nic.in) with a copy to this office by mail (mserpc-power@nic.in).

Gridco may take necessary action for submission of information in the required format.
Deliberations in the meeting

Gridco stated that they have already furnished the data to ERPC.

C2: Meeting/ Interaction with Consultants for Task-I: To study the status of implementation of recommendations of enquiry committee by the Consultant

Second Grid Study Committee (GSC) meeting was held at NLDC, New Delhi on 16th July, 2015 to finalize the modalities for implementation of the review of protection audit by the joint venture of M/s Tractabel, Romania, M/s Tractabel, India and M/s Lehmeyer International Private Limited, India. In the meeting, it was decided that M/s Tractabel the Lead Partner would be mainly responsible for Task-I i.e. to study the status of implementation of recommendations of Enquiry Committee. The Questionnaire for Task-I, the latest status of implementation of Enquiry Committee recommendations pertaining to Eastern Region are circulated to all the nodal officers vide letter dated 07-08-2015 and also available in ERPC website.

In the meeting it was also decided that for Task-I the consultant will interact with each RPC and its constituents for seven days. Accordingly, the tentative schedule was prepared and the committee decided to visit ERPC from 31st August, 2015 to 4th September, 2015.

In view of above, respective nodal officers update latest status of implementation of Enquiry Committee recommendations under your control area and submit to ERPC at the earliest. The tentative schedule for interaction with constituents is as given below:

1) 31.08.2015- OPTCL, GRIDCO, OPGC, OHPC, CESU, WESCO, NESCO, SOUTHCO, IPPs of Odisha
2) 01.09.2015- WBSETCL, WBSEDCL, WBPDCL, CESC, DPL, Sikkim

3) 02.09.2015- DVC, BSPTCL, SBPDCL, JUSNL, JBVNL, JUUNL, TVNL

4) 03.09.2015- NTPC, NHPC, Powergrid / CTU, other IPPs

5) 04.09.2015- ERLDC, ERPC

Nodal officer of DISCOMs / OPTCL / SLDC / OHPC / OPGC / NTPC / IPP are requested to attend the meeting at ERPC as per the schedule 

Deliberations in the meeting

OPTCL, GRIDCO, OPGC, OHPC, CESU, WESCO, NESCO, SOUTHCO, IPPs of Odisha have already intimated their nominees name to ERPC for attending the meeting on 31.08.2015 at ERPC, Kolkata.

[Action: OPTCL, GRIDCO, OPGC, OHPC, CESU, WESCO, NESCO, SOUTHCO, IPPs]  

C3: On-site Protection Audit by the Consultant to conduct the study/ Analysis to ensure Secure and Reliable Operation of National Grid – Submission of Check List.

Second Grid Study Committee (GSC) meeting was held at NLDC, New Delhi on 16th July, 2015 to finalize the modalities for implementation of the review of protection audit by the joint venture of M/s Tractabel, Romania, M/s Tractabel, India and M/s Lehmeyer International Private Limited, India. In the meeting, it was decided that M/s Tractabel will carry out the onsite Protection audit of the 15 shortlisted substations of the Eastern Region. List of substations is enclosed at Annexure-B13.

The consultant also submitted the format of checklist and a format of bus bar and breaker failure protection details to be filled up by the respective constituents. The formats are already circulated to respective nodal officers vide letter dated 31-07-2015 and the softcopy of the format is also available in ERPC website www.erpc.gov.in.

Nodal officers are requested to fill the audit checklist of your respective substation as per the format available in ERPC website and submit to GM, NLDC and CE(GO), CEA with a copy to ERPC Secretariat by 17th August, 2015 so that M/s Tractabel can start the proceedings for onsite protection audit of Eastern Region.

1. 400 / 220kV Indravati sub-station 
– OHPC

2. 400 / 220kV Mendhasal sub-station – OPTCL

3. 220 / 132kV Tarkera sub-station 
– OPTCL

4. 220 / 132kV Joda sub-station 

– OPTCL

OPTCL / OHPC are requested to submit the data in the format available in ERPC website.

Deliberations in the meeting

OPTCL and OHPC may furnish the required data to ERPC.

[Action: OPTCL / SLDC]

C4: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s 

PGCIL has already commissioned the 2x315MVA 400/220kV Bolangir S/s by LILOing of 400kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.

OPTCL updated the completion schedule of inter-connecting system as follows:

	Sl. No.
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir S/S.
	Severe ROW problem

	b.
	LILO of one circuit of Katapalli-Sadeipalli 220 kV D/C line at Bolangir S/S.
	End of October’2015

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (OPTCL) 220 kV D/C line
	Yet to be awarded

	b.
	Keonjhar (PG)-Turumunga (OPTCL) 220 kV D/C Line.
	Yet to be awarded

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	It will take 1 year for completion.

	b.


	LILO of one circuit of Atri-Puri (Samangara) 220 kV D/C line at Pandiabil (PG)
	Work will be taken up after charging of Pandiabili (PG) Grid. 




[Action: CGM (Const) / CGM (O&M)]
C5: Third Party Protection Audit

Status of 1st Third Party Protection Audit:

The compliance status of 1st Third Party Protection Audit observations is as follows:

	Name of Constituents
	Observations
	Total  Complied
	% of Compliance

	Odisha
	59
	27
	45.76


Deliberations in the meeting

As already deliberated in the OCC, OPTCL have complied 34 Nos observations out of total 49. The balance 10 nos belong to OHPC and OPGC. OHPC stated that they have complied 5 Nos observations and sent to ERPC. Ib TPS may submit the compliance in respect of their S/S early. 
[Action: Ib TPS]
C6: Pollution mapping for Eastern Region

The Pollution Mapping work in ER was started with on-site measurement of ESDD and NSDD.

The latest available status is as follows:

	Utility
	Scope
	Installed Locations
	No. of locations where 1st set of Measurements Completed
	Remarks



	OPTCL 
	164
	102
	82
	Work is in progress.


Deliberations in the meeting

As already deliberated in the OCC, OPTCL have completed measurement of 87 Nos. of locations.
[Action: O&M, OPTCL]
C7: Mock Black start exercises in Eastern Region – ERLDC
	Sl. No.
	Name of Hydro Station
	Schedule

(1st)

	Tentative Date
	Schedule
(2nd)

	1
	U.Kolab
	Last week of May, 2015
	Done on 16/07/2015
	Last Week of January, 16



	2
	Rengali
	2nd week of June 2015
	August, 15
	Last week of November, 15

	3
	U. Indravati
	3rd week of June 2015
	Done on 16/07/2015
	2nd week of February 2016

	4
	Balimela
	1st week of November,15
	
	1st week of March 2016

	5
	Burla
	
	
	


In the OCC meeting of ERPC, it was deliberated that mock black start exercise in respect of Rengali shall be conducted during September’15.

A procedure for conducting mock black start exercise for Burla PH need to be developed by SLDC in co-ordination with OHPC.
Deliberations in the meeting
It was decided that SLDC shall develop a procedure for conducting mock Black start drill for Burla PH in coordination with OHPC.
[Action: SLDC / OHPC]
C8: TTC calculations by States--ERLDC

As per CERC regulation, states are supposed to declare their respective TTCs on a monthly basis. ERLDC had interacted with WBSETCL and DVC and their import TTC corresponding to summer 2015 had been jointly estimated, in the course of explaining them the procedure. But they are not yet declaring these figures officially.

On the other hand BSPTCL, JUSNL, OPTCL have not even responded to this issue.

In 13th FOLD meeting all SLDCs are agreed to take up the process of estimating import and export ATC/TCC on regular basis. Further, ERLDC requested SLDC to compute the same vide letter dated 3rd Feb, 2015 and 10th August, 2015. The letter is enclosed at Annexure-B.35.

SLDCs are requested to compute and publish ATC and TTC on monthly basis in their website clearly stating the assumptions and limiting constraints. A sample format may be found at Uttar Pradesh Power Transmission Corporation Limited website at following link: http://upptcl.og/pdfs/ttc_06042015.pdf.

Deliberation sin the meeting

It was decided that SLDC shall expedite the matter and publish ATC / TTC for the State.
[Action: SLDC / OHPC]
C9: Restoration of SCADA data

Updated latest status is circulated in the meeting. During deliberations in 99th OCC it was pointed out by most of the constituents that SCADA problem in many locations are due to behind the schedule progress of work on the part of CTU/PGCIL. OCC advised Powergrid / CTU to expedite and restore at least the priority RTUs by 31st July, 2014. 

Updated status as updated in SCADA meeting which was held on 28th January’15 is circulated in the meeting.

The status as updated in the SCADA meeting is as given below:

i) List of additional elements/feeders whose data is not available – station under ULDC project:

	Sl

no
	Name of Utility
	KV
	Name of station
	Reason for non-reporting
	Latest status



	1
	OPTCL
	220
	Vedanta (9x135 MW)


	No status points are available.
	No isolator status are available.  MW/ MVAR not available for Sterlite 1/2 line, station transformer / Smelter. CBs of Bus coupler not available. Bus-1 KV/ HZ not available.

Problem still not resolved


iv) The updated status of telemetry of OPTCL Sub-Stations under ULDC project is project as given below:

	S/n
	Name of RTU Locations
	Latest status

	1
	Nalco
	OPTCL informed that RTU is reporting but intermittent since it was not configured properly.

The issue was already taken up with Nalco and it will be resolved soon.

OPTCL has resolved the issue. Some Unit generation polarity will be resolved by Feb 2015.

Problem still not resolved


v) RTU telemetry provided but data are intermittent / new element not wired.
	SL

No
	Name of station/ Utility


	Reason for non reporting
	Latest status


	II
	JSPL (Meramundali -

400)
	Most of the data not available.


	OPTCL informed that they are taking matter with JSPL.

Problem still not resolved


In the last meeting Vedanta Limited stated that materials are expected to be received from ABB by August and completion of work is expected by Sept’15.

OPTCL stated that they have resolved the issue. Reversal of CT polarity for two Nos. of units has to be done by NALCO. GCC may write to NALCO in this regard.

It was decided that O&M may not issue Technical clearance for open access transaction in favour of the CGPs till compliance of data communication.  

Deliberation sin the meeting

Sr. GM (Telecom) stated that no response has been received from Vedanta Ltd and NALCO. It was decided that GCC shall write the defaulting CGP / Industry for restoration of data communication system. CGM (O&M) may consider the same while allowing Technical clearance for Open Access transaction.

[Action: GCC / Telecom /O&M]

C10: Status of commissioning of generating station and transmission elements

Status of new transmission elements as updated in the meeting:
	Sl No.
	Name of Element
	Expected date

	7
	LILO of Baripada-Mendhasal D/C at New Duburi
	August’2015

	11
	400 kV Meramandali-Dubri D/C
	September’2015

	12
	400 kV IB-Meramandali D/C
	October’ 2015

	14
	220 kV Bidhansai-Cuttack D/C
	March’2016


[Action: CGM (Const)]
PART-D – Operational Issues

D1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of July’15:

	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)

	1
	CESU
	26
	60.78

	2
	WESCO
	39
	53.89

	3
	NESCO
	13
	2.94

	4
	SOUTHCO
	5
	3.28

	
	Total
	83
	120.89


It is noticed that WESCO & CESU had overdrawn a substantial quantum of power to the tune of 53.89 MU & 60.78 MU respectively during the month. SOUTHCO & NESCO had also overdrawn appreciable quantum during the month.  It was also noticed that CESU was continuously overdrawing since last five months. As stated by CESU that they are predicting the drawal from the SCADA data. 

In the last meeting, it was decided that average power drawal of those S/Ss not integrated in the SCADA shall be incorporated to ascertain Discom drawal.

Deliberations in the meeting
It was decided that SLDC shall take all steps to display CESU’s real time drawal more accurately. The S/Ss not integrated with SCADA may be incorporated manually in the drawal display of CESU and compare with the actual to ascertain its accuracy. WESCO stated that the due to erratic drawal by large industries they are not able to predict the day a head demand. SLDC stated that WESCO may use historical data for demand estimation. All Discoms were requested to predict realistic drawal to comply their drawal schedule.    
[Action: CESU / WESCO/ NESCO / SOUTHCO /SLDC]
D2: Availability of data of real time power flow of feeders covered under Under-frequency Load shedding scheme (UFLS) and lower relief expected to obtain in real time system operation

In the last meeting Sr. G.M. (Telecom) stated that Cable has already been reached at site. Expected to be completed the work by September’15. Sr. G.M (PS) stated that 33 kV Banki feeder may be replaced by any other feeder as drawal of the feeder has been reduced.  

Deliberations in the meeting

Sr. G.M (Telecom) stated that MFMs have already been installed at the following S/Ss.
1. Khurda


2. Bhanjanagar

3. Jayanagar

4. Theruvali
5. Boinda


6. Chainpal


7. Dhenkanal

8. Balasore
9. Bhadrak

10. Jajpur Road

11. Bargarh

12. Bhadrak
13. Bolangir

14. Bolangir (New)

15. Rourkele

16. Sambalpur

Integration will be done soon after joint testing with EMR.

D3: Non compliance of Grid Code provision.

It is noticed that OHPC is availing shutdown of its unit without prior approval of SLDC. Even though, the planned shutdown is being approved earlier by SLDC, it is required to obtain approval for outage of generating units / Transmission elements while isolating from the Grid as per provision of OGC Regulation 5.8(5) which states;

“Not withstanding provision in any approved outage plan, no cross boundary circuits or generating units of a generator shall be removed from service without specific release from SLDC. This restriction shall not be applicable to individual generating unit of a CGP” 

Deliberations in the meeting
Director OHPC stated that SLDC is not responding the shutdown permission request of OHPC. However, OHPC have assured to intimate SLDC before availing shutdown of unit on real time. It was decided that SLDC shall intimate OHPC in writing for approval / Non approval of shutdown in future. 

[Action: SLDC / OHPC]  

D4: Revival of Station Transformer for Station Auxiliary supply at Balimela HEP.


It was suggested to keep minimum number of ckts in service while of low generation at Balimela to reduce Var injection. Also it was suggested to avoid keeping two units in synchronization with minimum generation (10 MW each) to meet the auxiliary requirement in contingency conditions, even though DG set is available. 

Although it was agreed in the last meeting by OHPC to keep one unit of Balimela synchronized and one No. 220 kV ckt during low generation period as per SLDC direction, it is noticed that BHEP is not complying the same.

Deliberations in the meeting
Sr. G.M (PS) stated that Balimela PH is keeping two Nos. of units in the bar all the times. On enquiry, it is learnt that the units are kept to maintain the barrage water level to enable to run the pumps for technical water supply. OHPC stated that due to profuse leakage, the barrage water level is reducing. It was suggested by Director (Com) that, OHPC may install new pumps with high suction head to lift the technical water requirement. It was decided that OHPC may write to Water Resources Dept. for early repair of the barrage to prevent the leakage. OHPC may not waste water, which is a pricey item in the present scarcity scenario. OHPC stated that SLDC is instructing to keep two nos. of Upper Kolab units to keep synchronized. It was decided that SLDC should not instruct to keep units with minimum generation unless the situation warranted.
[Action: SLDC / OHPC]

D5: Prolonged outage of transmission elements and tentative revival dates

The tentative revival dates of transmission elements are updated as follows
	Sl.No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220kV Jayanagar-Theruvali ckt-III breaker
	Breaker defunct
	September 2015

	2
	220/132 kV, 100 MVA Auto-II at Duburi  
	After inspection by repairer, date can be ascertained
	Spares received. Work will be taken up after rainy season. 

	3
	220/132 kV, 100 MVA Auto-I, Joda
	
	September’ 2015

	4
	220/132 kV, 100 MVA Auto-I, Bhadarak  
	
	September’ 2015

	5
	220kV Budhipadar-Tarkera ckt.-I
	
	September’ 2015


[Action: O&M]
D6: Communication issues 

(i) Installation of communication equipment by CGPs / Industries.

The status of data communication from CGPs as deliberated in the last meeting is as follows

	Sl. No
	Name of CGP
	Present status

	1
	M/s IFFCO, Paradeep
	Outdoor commissioning work completed. RTU was locally tested. After replacement of the faulty CVT data will be integrated.

	2
	M/s MSP Mettalicks
	PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited.

	3
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	4
	M/s Adhunik Metalliks
	Work order placed with ABB for supply of RTU.

	5
	M/s Rohit Ferrotech
	PLCC established and inspection by Telecom Engineers completed.  Data base has already been prepared by OPTCL.    

	6
	M/s VAL, Jharsuguda
	No isolator status is available. MW/ MVAR not available for Sterlite 1&2 line, station transformer / Smelter. CBs of Bus coupler data, Bus-1 kV/Hz are not available. As per MOM between OPTCL & Sesa Sterlite, Jharsuguda dtd 22.09.2014, provision for telemetry data will be extended within 6 months (March, 2015). The CGP is not responding. VAL intimated that data shall be made available in all respect by July, 2015. No progress of work.


It was decided in the last meeting that Member Secretary GCC shall write to the defaulting CGPs for compliance of data communication provisions. OPTCL, while issuing Technical clearance shall consider the provisions also.

[Action: Member Secretary GCC]
(ii) Availability of Tap position of 400kV ICTs at Meramundali.

It is noticed that tap position of Meramundali ICTS are not available for SCADA display.

Deliberations in the meeting
Sr. G .M (Telecom) stated that the work has been completed and shall be made available after joint testing with EMR by September’15.
(iii) Availability of data at SLDC.

The data for 

(a)  Auto loading of 220/132 kV, 100 MVA Mendhasal S/S.

(b) Power flow through 132 kV Paradeep- Jagatsinghpur ckt.

In the last meeting Sr. G.M. (Telecom) stated that acquisition of data for the above transmission elements shall be done by end of August15.

Deliberations in the meeting

Sr. G .M (Telecom) stated that the work has been completed and shall be made available after joint testing with EMR by September’15. 

[Action: Sr. G.M (Telecom)]
(iv) Interruption of SCADA.

It is noticed that there is frequent interruption of SCADA System, resulting problem in real time operation. Action may be taken to avoid such frequent interruption of SCADA.  

In the last meeting, Sr. G.M (Telecom) stated that Powergrid link between Rourkele-Kaniha is being used for data transfer. The link is not healthy due to heavy fibre loss. Powergrid have proposed to upgrade the existing SDH equipment to STM16. Work order has already been awarded.

Deliberations in the meeting

Sr. G.M. (Telecom) stated that the work is expected to be completed by September’15.
(v) Integration of new element.

M/s VAL-SEZ became a consumer of WESCO Utility with effect from 20.03.2015 and importing power through intra State open access from its CGP at Jharsuguda as well as from other utility. The drawal of VAL-SEZ needs to be integrated to SCADA to ascertain WESCO Utility drawal and State demand on real time basis. Since the SSL is reporting to ERLDC, Sr. G.M (Telecom) may write to ERLDC for integration of VAL-SEZ drawal in to the SCADA. 

At present generation data of VAL-IPP connected with State Transmission System is being received through ERLDC. But most of the times the data become suspected. SEZ drawal date is yet to be received. However, the calculated figure is being displayed. Sr. G.M (Telcom) may write to SSL to transmit uninterrupted date of IPP generation as well as integrate SEZ drawal to ERLDC.    

In the last meeting, Sr. G.M (Telecom) stated that M/S VAL is yet to respond. It was decided that SLDC and OPTCL, while issuing Technical clearance shall consider the provisions also.

Deliberations in the meeting
Sr. G.M. (Telecom) stated that response is yet to be received from SSL end
D7: Display of dashboard data.

On receipt of feedback from Dist. Utilities, IT representatives have made a demo at SLDC in presence of all Discoms, Telecom and SLDC, wherein some modifications were suggested. However, the dashboard display is functioning satisfactorily.  
The status of lease line of all Discoms as deliberated in the meeting are as detailed.

	Sl. No
	Dist. Utility
	Status of leased line
	Remarks

	1
	CESU
	Already connected. RVDU commissioned
	Data display available

	2
	WESCO
	Required amount deposited with BSNL
	Expected by 15th of Sept’15

	3
	NESCO
	Already connected. RVDU commissioned
	Data display available

	4
	SOUTHCO
	Already connected. RVDU commissioned
	Data display available


In the last meeting CGM (IT) stated that, IT representative had visited all four Discoms and found that the newly developed Dashboard is functioning satisfactorily. NESCO, WESCO and SOUTHCO have also issued certificate in this line. CESU stated that the Dashboard is functioning satisfactorily except some missing data.  It was decided that the Dashboard shall be kept in parallel with RDVU for three months.

Deliberations in the meeting.
WESCO stated that it is expected to connect BSNL lease line by 15th of September’15.

[Action: WESCO]

D8: Web based drawal / generation scheduling.

SLDC is going to implement web based drawal / generation scheduling for Dist. Utilities and State generating stations including IPPs and CGPs soon. A demo has been organized on 29.07.15. 

In the last meeting, CGM (IT) stated that, web based generation scheduling for State generating stations has done. Modules for Discom and CGP / IPP shall be made available before the next PSOC meeting. After approval by the stake holders the same shall be go live from September’15. All Users were requested to forward their respective schedule in the prescribed format. 

Deliberations in the meeting.

CGM (IT) stated that web based scheduling modules have already been done. SLDC may write all State generators, IPPs and CGPs to nominate their representative to attend one day demonstration cum training programme at SLDC for web base scheduling. The date of the training may be finalized in coordination with CGM (IT).

[Action: SLDC / CGM (IT) / All generators, IPPs and CGPs]    
D9: DISCOM Issues 

SOUTHCO:

1. Facilitating to get the data in Excel format for better ABT operation.

2. BSP bill for the month of July 2015 has not been prepared by Gridco as per the energy accounting statement issued by SLDC.

3. Machkunda power drawal.

Previous proposal of linking of 33kv system to draw Machhakund power from Akhusingi to Bissamcuttack is still under progress, however the same is not feasible due to long distance and thus it may be shared by 132 kV system only.

4. Renovation of Ganjam grid with capacity up-gradation with 3 nos 33kV feeders for area load.

Deliberations in the meeting

1. SLDC stated that data in Excel format is not feasible. Southco may log the data as per their requirement.

2. Director (Com) stated that a meeting has been convened today with all Discoms to finalize the issue.

3. Southco may expedite construction of 33 kV line for connecting 33 kV Gumuda feeder with Akhusing S/S.

4. CGM (O&M) stated that revival of Ganjam S/S is expected by March 2016.

[Action: SLDC / Sr. G.M (Telecom) / Southco]    

NESCO

1. The total drawal and data displayed in RVDU is not matching with Data displayed at SLDC, Bhubaneswar at any instant (near about 55MW difference). 

2. Suspected value of 132KV feeders / Power transformers has not been corrected in RVDU even after rectification of suspect value of drawal at SLDC site. (Ex- At 17.25 hrs, 25.8.2015, the drawl of Rohit Ferro alloys is 69MW at NESCO RVDU but 6MW at SLDC side). 
Deliberations in the meeting

SLDC stated that RVDU is receiving data from Chemtrol system, while SLDC control room data is being received from Areva system. Both are in parallel at present. Finally, Chemtrol system data will be displayed at RVDU and SLDC. The system is under observation. The errors will be rectified soon.
[Action: SLDC / Sr. G.M (Telecom) / Southco]
CESU

1. Mismatch of displayed and actual drawal lead to inaccurate drawal prediction on day-ahead basis.

2. Provision of AVR at Puri and Samuka grid sub-station as decided in the Nabakalebar meeting.

Deliberations in the meeting

CGM (O&M) stated that installation of AVR at Puri and Samuka is not feasible, which may lead to frequent tap operation and supply fluctuation. This proposal has already been dropped and intimated to CESU. Necessary action is being taken by SLDC to minimize the gap between the display and actual drawal of CESU. 
[Action: SLDC / Sr. G.M (Telecom) / CESU]

PART E: OPERATIONAL PLANNING

E1:  Commissioning status of New Transmission elements. 

The status of commissioning of new transmission elements is as follows:

	   Sl. No
	    Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by March 2016.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal, which is under progress.

	3
	Commissioning of 400 kV Ib-Meramundali D/C line.
	400kV SSEL-Meramundali line has been idle charged from SSEL end. Due to theft of conductor line could not be charged. Expected to be charged by end of Nov’2015. 

	4
	Commissioning of 400 kV Duburi-Meramundali D/C line.
	Work is in progress after disposal of Case. Expected by the end of August’ 2015 subject to completion of inspection by CEI. 

	5
	Commissioning of 220 kV Bidanasi-Cuttack line
	Work in progress and expected to be completed by March 2016.

	6
	Commissioning of 220/132 kV Cuttack S/S
	Work in progress and expected to be completed by October 2015.

	7
	Commissioning of 132 kV Baripada (PG)-Jaleswar line
	Work has already been started, which will be completed by December 2015. Availability of bay at Baripada PG is uncertain.

	8
	Commissioning of 220/132 kV Kesinga S/S
	Work under progress. Expected by September 2016.

	9
	Connectivity to Keonjhar PG
	Proposal is mooted to be placed in the BoD meeting for connecting the proposed 220 / 33 kV Keonjhar S/S and with Turumunga S/S through 2 Nos. 220 kV ckts each. 

	10
	LILO of 220 kV Burla - Bolangir line (one ckt) at Bolangir(PG)
	Work has been started. Expected to be completed by October, 2015

	11
	220 kV Bolangir –Kesinga D/C line and LILO of one ckt at Bolangir(PG).
	220kV Bolangir - Kesinga D/C line is under construction. It is proposed to connect Bolangir (PG) through LILO arrangement of one ckt. Land dispute is yet to be resolved.


Status of Discom’s action plan for power drawal from the S/Ss expected to be commissioned in near future. 
	   Sl. No
	    Name of the sub-station
	Probable month of commissioning
	Name of DISCOM
	Action taken by Discoms

	1
	132/33kV, 2x20 MVA  Khajuriakota 
	December’15
	CESU
	By July’15

	2
	132/33kV, 2x40 MVA  Kalunga 
	Sept’15
	WESCO Utility
	

	3
	220/33kV, 2x20 MVA Banei 
	Dec’15
	WESCO Utility
	

	4
	132/33kV, 2x20 MVA  Padmapur
	Dec’15
	WESCO Utility
	

	5
	132/33kV, 2x20 MVA  Udala 
	Dec-15
	NESCO Utility
	Line existing

	6
	132/33kV, 2x20 MVA  Somanathpur 
	Sept’15
	NESCO Utility
	33 kV feeder existing.


CESU stated that action is being taken for construction of 33/0.4 kV S/S at Mendhasal to avail power supply for Mendhasal area.

All DISCOMS may update the status / CGM (O&M) & CGM (Const.) may please deliberate.

E2: Installation of Energy Metering at Hydro / Traction & Solar projects.

In the last meeting, it was decided that Gridco and OHPC shall consider the Secure meter recordings for billing purpose.

WESCO shall take follow up action with Railway authority for replacement of CT & PT and meter panel at the traction points and intimate the progress in the next meeting. 

Deliberations in the meeting
OHPC stated that meters installed at Upper Kolab and Upper Indravati are yet to be tested. After completion of testing, Gridco shall consider the Secure meters for billing purpose. O&M may take action for testing of these energy meters early. WESCO may take follow up action with Rly Authority for replacement of CT, PT and Meter panels at traction S/Ss.

[Action: O&M / GRIDCO / OHPC / WESCO]

E3: TTPS Issue.

Implementation of Feeder Metering

In the last meeting, TTPS stated that in a subsequent meeting between Gridco and TTPS, it was decided to defer the feeder metering till completion of 132 kV TTPS-Duburi feeder meter testing by STL. It was decided that SLDC shall prepare mock deviation charge bill considering the feeder meter recordings.
Deliberations in the meeting

STL team had been to TTPS for testing of feeder meters. TTPS authority had asked them for testing of other meters instead of these meters. It is construed that TTPS is deliberately avoiding implementation of feeder metering.  Further OPTCL has agreed to spare a set of PT and CT of required accuracy for installation at TTPS-Duburi 132 kV feeder. TTPS is delaying to place requisition for the same. Members expressed their concern for such activity. It was decided that Director (Com) shall take up the matter with the higher authority of NTPC.

[Action: Gridco / TTPS]   
E4: Major Events in the month of July’15

1. 160 MVA, 220/132 kV Grid S/s at Puri (Samangara) S/s was commissioned on 14.07.2015 at 14:14 Hrs.

2. 132 kV LILO of Nimapara-Puri line to Puri (Samangara) S/s charged on 15.07.2015

3. 220/132kV, 100 MVA Auto-I at Mendhasal charged on 17.07.2015 at 21:43 Hrs.

E5: Important Grid Incidences during the month of July’15.
Important incident occurred during the month of July’15 were reviewed.

Deliberations in the meeting

Sr. G.M. (PS) stated that the reports are not being received soon after the occurrence of the incident. SLDC has to pursue the concerned SDO / Shift Engineer of substations including Power House for the same. All shift engineers may be instructed to report the incident within 24 hours of the occurrence.  
[Action: CGM (O&M) / OHPC]
E6: Reporting of major Incidents
It is noticed that, very often the reports in respect of major incident received from the field S/Ss are not in proper order and not containing the relay indications and sequence with justification. At times the report is being received after considerable lapses of time, even after 2-3 days, which lead to embarrassing situation in the protection coordination sub-committee meeting of ERPC 

In the last meeting, it was decided that the preliminary report shall be sent by the respective DGMs within 24 hours of occurrence of the incident to SLDC. The final report shall be sent to SLDC after due analysis by the concern E&MR Divisions.  
Deliberations in the meeting

CGM (O&M) has agreed to issue instructions to all the GM, EHT (O&M) Circles accordingly
[Action: CGM (O&M)]

E7: Outage of major transmission Elements during the month of July’15. (above 10 hrs).

Outage of major transmission elements above 10 hours during the month of JULY’15 was reviewed

Deliberations in the meeting

It was noticed that most of the outages are due to insulator failure and jumper snapping. O&M may take necessary preventive action to avoid such incidents.

[Action: O&M]
E8:  Review of Outage Program of State Generators / Transmission elements for the month of August & September’2015:

Tentative Outage programme for State Generators for the month of August/ September’2015 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 2
# 6
	18.04.15 to 05.09.15

10.04.15 to 15.09.15

17.02.14 to continue
	Capital Maintenance

470 Gallery Pump failure

Programming for R, M & U

	2
	Chiplima
	#3
	15.02.14 to continue
	Programming for R & M 

	3
	Balimela
	# 1
# 3

# 7
	31.01.13 to continue
26.06.15 to 30.09.15

10.07.15 to 30.09.15
	Programming for R & M 
Excitation problem

Excitation problem

	4
	Upper Kolab
	# 1
	29.07.15 to 31.01.16
	Capital Maintenance

	5
	TTPS
	# 5

# 2
# 4

# 3
	29.07.15 to 19.08.15

20.08.15 to 04.09.15

07.09.15 to 21.09.15

25.09.15 to 09.10.15
	Boiler Licensee renewal
Boiler Licensee renewal

Boiler Licensee renewal

Boiler Licensee renewal


Deliberations in the meeting

OHPC and TTPS have confirmed the outage programme.
E9: Generation Program for the month of September’15.
Generation schedule for the month of SEptember’15 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Programme (MW)
	Reservoir Level as on 25.08.14
	Reservoir Level as on 25.08.15
	MDDL
	High Flood    Reservoir Level

	
	Sept’15
(1st fortnight)
	Sept’15
(2nd fortnight)
	
	
	
	

	HPS, Burla
	120+40
	120+40
	620.33ft 
	621.39ft
	590 ft.
	630 ft.

	Balimela
	100
	100
	1491.00ft 
	1483.00ft
	1440 ft.
	1516 ft.

	Rengali
	160
	160
	120.87mt

1.78mt mtr mt
	118.70mt mt
	109.72mtr 
	123.5 mtr.

	U.Kolab
	100
	100
	853.44mt mt
	850.83mt
	844 mtr 
	858 mtr.

	U. Indravati
	200
	200
	640.46mt
	630.32mt mt
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2729.20ft 
	2727.50ft ft
	2685 ft.
	2750 ft.

	TOTAL
	750
	750
	
	
	
	


Deliberations in the meeting

OHPC has confirmed the generation schedule.

[Action: SLDC / GRIDCO] 

E10: Agenda by JSL, Duburi.
One Unit of JSL CGP will go under statutory shutdown in November 2015 (01st – 30th). JSL need to import power to operate the plant. JSL WILL IMPORT RENEWABLE ENERGY (Non-SOLAR) WHICH WILL ADDRESS THE RPO COMPLIANCE ALSO.  The clearance for Import of Power up to 60 MW must be allowed during Nov’15 (01st – 30th).
Deliberations in the meeting
CGM (O&M) stated that due to transmission constraint at Duburi command area, the proposal was not considered. However, after charging of 400 kV Meramundali-New Duburi D/C line the said proposal shall be considered.

[Action: Jindal stainless Ltd.] 

PART F: OTHER ISSUES

F1:  Date and Venue of the next (90th) PSOC meeting.

The date and venue of 90th PSOC meeting shall be intimated to all members

[image: image2.png]89" Power System Operational Co-ordination Review Meeting
[ At 11:00 A.M. on 29.08.2015]

[At Power Training Center, OPTCL, Chandaka, Bhubaneswar]

Name Designation | Organisation Mobile No. E-mail Address “
P. k. . Peachsw D IACH (D) équ‘d Lo m
B

Dyvek (0) | OMPC 9437 F0806b )

Ak MiChaa i
Pt Treprdhy Gm (00m) | oPTeL 9432907014 ?M-mm@,o‘ﬂk(ru* ‘
R-R - Panete m(end] DPieL  |0943890F3 %7 | Cym-Cm @ ot kg e
U N Miho Cem (PP avdep | J43890 2774 ; @/
M - Amani« Qo Ce6MODT) oPTer >3 6700% J‘
MR Mohsaty | Aibm(P)| QLB “?45@??" FRI0 fumctadlls (‘ Jést o
| mer.c A b [oen)T|_opTeL M350 7'@% Hé 4'

Bk Sahlle |Sbw(op)i| opTeL
10 ? W« Pc«j(dnk T’\cwmv{u OWvC AN3T\ 631y 2. ““k“‘\‘?\:&”‘“wa@f“"“ Came \“ weall
11 IDhasmenda MU [herape@) OHTC |AT781094 2.2 dnpato - ohpe @ fmal.com WL

2gn.0m)-999004t 045 ~o_

et CHeP ok T T
12 Anprasfan % %M@) Supe FUBLT050)33.  [hpsch P)”W@)‘M i !Qi‘.;
Wterrarse [P 3‘9ch‘ P's.

BlA K- Mbanlk~ | Mo Gy |H — , J
24 M'lZM 2 ¥ T ﬁ ¥
} 14 i%wtﬂ!; D&am TeL | qqz32256074 stf\JAl;l:uédww ‘i 4

NTee LK mMAghraol @ .
S.le - MiShed pom (os) | Bmen. | AM382320F PAPC -t T Qe

M | OPGC 93387 15y0 [Bracet, matapol Nuaw

16 1Dl m /
{

17 | T. 5. M&S) G QM) Lusen| 94370 S 728 R o 6l7mee /Ot

18 o A. 67(:‘;,(/7‘_;:‘: Moncgyev VESC T 9 H27oCT 0¥ “;‘e*n@!c’y %(‘: @ gf

P |B-c pandg Toh Ce) | OPTCl | 94259078 7¢ ldb.bcbonde Eobme M)
0| 6K Misha b0 | pore. | 4389975 |44 g ctm@ertd S
21 kK. TR, PPN 1D (1) ppre s Bu3ga0 8230-[7eh. kackery | YDvpanr).
2 RN, ket IMM (el gpret 03324 |14 . 0. Sob G
> ‘fawgywadu&, P (i)l epTer 9438907477 | del-swny @ephlol, okl

2 ¢ R MSha~ Q)| opTel |A42890F30€ efe. sl Poply, O

25 | Madhnsudan ok | Atu (€le) | GRIDCo | 492427996 JWeM&cégmv-mn Mg st

K. DHMCEl)| RTEC 9449907 C g7 [Ele.b ..
o |5 DA AMCER L M8 REqT Flobbdes @ | p o o

743570}9»—/’ éf’a,fmj:fg HW’
94389 0?403 1,11(4 LLIVC Yady-g, ﬂé

27 L~)Ja7&(¢ Cmloe) | ep1el
28 | Comacadi (ko | GV ) | SLpC.





[image: image3.png]943&674gm

%p G cecco

¢r7124§¢1 O
%d Uld.&f;@‘afm

XY 53060

FMMQW G

(/

X

aly3890b00 ¢

7eno/ra , ma///
NEsCO0 s sha -

4‘

4'(

-
©| 94437$50189

TJorgangons

9Y%€qoTY o [cll

7 -—"-‘

e i
.S(leuﬁ.us rr? fn

Q42890 F40¢

ek - progostday
E 1d.C owvege 19 Y

Q437000261

I

Cm

AMWﬂ@mifﬁ"W] St

GUIsIo7g s

etll'g

"‘44 3“6“‘)” ) 1>




