[image: image1.png]STATE LOAD DESPATCH CENTRE

OFFICE OF THE Sr. GENERAL MANAGER (POWER SYSTEM)

ODISHA POWER TRANSMISSION CORPORATION LIMITED
GRIDCO Colony, P.O.- Mancheswar Rly. Colony, Bhubaneswar-17, FAX-0674- 2748509

PTC

of Dafishe CIN - U401020R2004SGC007553

i’é‘e‘}
£
No-SGM (PS)-PL-15/2015/ A\ G Dated: ¥4.02.2016
From:

The Sr. G.M. (Power System),
OPTCL, Bhubaneswar-17.

To:
As per distribution list

Sub: Minutes of 93" Power System Operational Co-ordination meeting held on
30.01.2016 at PTC, Chandaka .

Sir,
Please find enclosed herewith the minutes of 93" Power System Operational Co-

ordination meeting held on 30.01.2016 at Power Training Centre, Chandaka.

This is for your information & necessary action.

Yours faithfully;

2

X?r. G.M (Power System)

Encl: As above

Copy along with enclosures forwarded to the Executive Assistant to CMD, Gridco / OPTCL
for kind information of CMD.




Distribution list

1. The Director (Commercial), GRIDCO, Bhubaneswar.

2. The Director (Operation), OHPC, Bhubaneswar

3. The CGM (O&M), OPTCL, Bhubaneswar.

4. The CGM (Const.), OPTCL Bhubaneswar.

5. The CGM (RT&C), OPTCL, Bhubaneswar.

6. The CGM (PP), GRIDCO, Bhubaneswar.

7. The CGM (IT), OPTCL, Bhubaneswar.

8. The Sr. G.M (Const)-I, OPTCL, Bhubaneswar.

9. The Sr. G.M (Const)-II, OPTCL, Sambalpur.

10. The Sr. G.M (CPC), OPTCL, Bhubaneswar.

11. The Sr. G.M (CP), OPTCL, Bhubaneswar.

12. The Sr. G.M. (O&M), Zone-I, Narendrapur.

13. The Sr. G.M.(O&M), Zone-II, Meramundali.

14. The C.G.M. (Telecom), OPTCL, Bhubaneswar.

15. The CEO, CESU, Bhubaneswar.

16. The A.O., WESCO, Burla

17. The A.O., NESCO, Balasore

18. The A.O., SOUTHCO, Berhampur.

19. The Member Secretary (GCC), OPTCL.

20. The Sr. G.M. (El.), BHEP, Balimela

21. The A.G.M. (El.), CHEP, Chiplima

22. The Sr. G.M. (El.), UIHEP, Mukhiguda

23. The Sr. G.M. (El.), RHEP, Rengali

24. The D.G.M. (El.), HHEP, Burla

25. The D.G.M. (El.), UKHEP, Bariniput, Koraput

26. The S.E. (O&M), Machhakund

27. The DGM (Elect.),  IbTPS, OPGC, Banharpali.

28. The Vice President (O), IMFA, Choudwar.

29. The D.G.M. (O&M), NTPC (TTPS), Talcher.

30. The AGM (Elect.), JINDAL Stainless Ltd., Duburi

31. The G.M, HINDALCO, Hirakud.

32. The G.M.CPP, NALCO, Angul.

33. The Director, M/s. Jindal Steel & Power Ltd., Angul

34. The AVP-Vedanta Ltd (IPP), Jharsuguda

35. The G.M, Vedanta Ltd (CGP), Jharsuguda.

36. The DGM (Power Distribution), RSP, Rourkela.

37. Joint President, Aditya Aluminium Ltd., Lapanga, Sambalpur

38. The G.M.(Elect.),  Bhusan Steel Limited. Meramundali

39. The G.M. (Elect.), Bhusan Power & Steel Ltd, Budhipadar.
40. The G.M.(Elect.), IFFCO Limited.

41. Director &COO, GMR Kamalanga Energy Limited, Satyanagar, Bhubaneswar

Odisha Power Transmission Corporation Ltd. Bhubaneswar.


Minutes of 93rd PSOC meeting held on 30.01.2016 at PTC, Chandaka
List of participants is at Annexure.

Sr. G.M (Power System) welcomed all the participants to the 93rd Power System Operational Coordination meeting and highlighted the system performance during the month of December’2015 and overall power scenario of the State. He also emphasized on the drawal by all the Discoms during the month. 
The meeting was chaired by Director (Commercial), GRIDCO. 

D.G.M. (SS), SLDC took the agenda items for discussion. 

The review proceeded as follows: 
1: Confirmation of minutes of 92nd PSOC meeting held on 29.12.2015
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2015/4402(41), dated 11.01.2016 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting

Since no comments have received from the members, the minutes of 92nd PSOC meeting was confirmed. 
PART A: LIST OF ITEMS
List of items to be discussed in the meeting are given in the subsequent parts 
PART B : SYSTEM PERFORMANCE
B1: Review of Grid Performance for the month of December’2015.
(A)  Frequency 

It was noticed that, during the month of December’15, 66.27% of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 64.82% during the month of November’15. The maximum and minimum System frequency during the month was 50.21 Hz & 49.72Hz respectively.

 (B)  Grid demand 

Grid demand for the month of  December’15 was reviewed. The energy average consumption during the month was 2723 MW. The maximum System demand of 3813 MW occurred on 01.12.2015 at 19:00 Hrs and minimum demand of 2042 MW occurred on 16.12.15 at 15:00 Hrs. 
Deliberation in the meeting

It is observed that the average demand during the month of December’ 15 was decreased by 172 MW and the peak demand was decreased by 155 MW from that of November’15. The average energy consumption during the month has been increased by 119 MW in comparison to Dec’14. The decrease in maximum demand is due to shutdown of transmission elements for annual maintenance during the month and impact of winter season.
 (C)  Voltage Profile of important Sub Stations in OPTCL System during the month of Dec’15.

The Voltage profile at different 220 kV buses in OPTCL system during the month of December’15 was reviewed. 
Deliberation in the meeting

The maximum voltage of 248.37 kV occurred at Jaynagar 220 kV bus, while Narendrapur 220 kV bus has experienced the minimum Voltage of 182.26 kV.
Sr. G.M (PS) stated that the Voltage profile at Jayanagar has been improved due to induction of  125 MVAr reactor at Jayanagar (PG). 









        
        [Action: CGM (O&M)]

(D) Energy Generation / import during the month of December’15 
Energy generation and exchange during the month of  December’15 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP / IPP support during the month was 2026.20 MU. 
(E) Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of December’15.

Auto loading of all 220 kV S/Ss was reviewed. It was noticed that some of the ICTs have not been provided with energy meter. TTPS Auto loading is not being received by SLDC.
Deliberation in the meeting.

CGM (O&M) stated that tendering for procurement of energy meters is under process. TTPS stated that provision for recording of on line Auto loading data at TTPS is not available. 









        
        [Action: CGM (O&M)]

(F) DISCOM Drawal during the month of December’15 
The schedule and actual energy drawal by Discoms for the month of December’15 was reviewed. 
Deliberation in the meeting

It was noticed that CESU, WESCO & SOUTHCO were overdrawn 20.03 MU, 34.11 MU and 7.62 MU respectively during the month, while NESCO had under drawn  9.818 MU from their schedule. All Discoms were requested to comply with their respective drawal schedule. 
WESCO stated that their RVDU is not functioning. CGM (Telecom) stated that the damaged Hard Disc has already been replaced. WESCO may load the Operating System (OS) to make the RVDU functional. 
[Action: All Distribution Utilities / SLDC]
 (G) Drawal of Machhakund Power during the month of December’15

The drawal of Machhakund power during the month of December’15 was 26.510 MU against AP drawal of 22.520 MU. 
In the last meeting, Sr. GM (Telecom) stated that providing of RVDU shall be taken up with M/s Chemtrol. SLDC shall place requisition for providing a RVDU at Jayanagar control room. Southco stated that construction of 33 kV Gumuda-Akhusing feeder is expected to be completed by March 2015. 

Sr. G.M (O&M) -I stated that it is proposed for extending power supply to Rayagada Rly traction S/S from Rayagada S/S. Normally Rayagada is on Machhakund system. There may be frequent interruption of  Rly. Supply with the changeover of Rayagada sub-station from Machhakund to BTH system. Moreover, traction load has adverse impact on Machhakund units for which the traction feeder has already been disconnected from Machhakund PH.  It was decided to examine for connecting the proposed Rayagada Rly traction S/S feeder with Theruvali Grid S/S. 
Deliberations in the meeting

Sr. G.M (PS) stated that Jayanagar Grid is not taking required measures for reducing Machhakund drawal, resulting hand tripping of feeder by Machhakund authority at their end in case of over drawal. Sr. G.M (O&M), II may issue necessary instruction to Jayanagar Grid.
C.G.M. (Telecom) stated that requisition for RVDU at Jayanagar has been placed before M/s Chemtrol. Offer from their end is awaited. Southco stated that construction of 33 kV Gumuda-Akhusing feeder has been completed. Inspection is left. 
Sr. G.M (O&M) -I stated that it is proposed for extending power supply to Rayagada Rly traction S/S from Rayagada S/S temporarily. Sr. G.M (PS) stated that in that case, Rayagada supply shall be isolated from Machhakund system. In case Kakariguma Rly. supply is fed from Sunabeda end, HAL may object for Voltage fluctuation. Rly. authority may be asked for availing power supply at 220 kV Voltage level. 

  [Action: CGM (Const.) / CGM (O&M) / OHPC / Southco  / SLDC]

 (H) Under Frequency relay operation in OPTCL System during the month of December’15.

There is no UF Relay operation occurred during the month of December’15 as the frequency had never gone beyond 48.50 Hz. 
PART C – Issues raised in 117th OCC meeting of ERPC held on 21.01.16
C.1: Charging of 220 KV Raigarh (PGCIL)- Budhipadar line

WRPC vide letter dated 21.10.15 & 18.12.15 informed that as per the study committee of WR’s recommendations the LILO of 220 KV Raigarh(CSPTCL)-Budhipadar line at 400/200 KV PGCIL Raigarh s/s has been completed two months back and to save theft incidents the LILO for both the section has been idle charged from 11.08.2015. GM, WRLDC has taken up the matter with ERLDC and Odisha state to charge the line from Budhipadar end since PGCIL is ready for  charging the both portion of above line from Raigarh(PGCIL) end. The charging of 220 KV Raigarh (CSPTCL)-220 KV Raigarh (PGCIL)- Budhipadar line will provide additional inter regional link in addition to existing inter regional link between 220 KV Korba (E) and Budhipadar in this section.

Further, both CSPTCL and PGCIL are ready with the Chhattisgarh section. It is, therefore, requested to kindly look into the matter and arrange for charging of the said line at the earliest so that additional inter regional link in addition to existing inter regional link between 220 KV Korba(E) and Budhipadar in this section are available.

In the 117th OCC meeting of ERPC, ERLDC deliberated that OPTCL has to submit the required information in prescribed FORMATs for Budhipadar bay considering the 220kV Budhipadar-Raigarh (PG) as a new transmission element. Relay co-ordination for the said circuit at Budhipadar is required.

Deliberations in the meeting.
 CGM (O&M) stated that POWERGRID has to intimate OPTCL the details of connectivity.
[Action: CGM (O&M) / SLDC / POWERGRID]

C.2: Status of PLCC system installed in Eastern Region

In 30th TCC/ERPC, Powergrid agreed to restore the PLCC system at both ends (its own end as well as the constituent end) of a line wherein the other ends are not operational for some reasons or others as one time job.

In 115th OCC, all the constituents were requested to go through the details of their respective control area and give their comments/suggestion, if any, by next OCC.

In 116th OCC, JUSNL informed that they have submitted the cost estimation to their management for approval.

WBSETCL informed that they have referred the cost estimation to their communication wing.

OPTCL submitted that they are installing OPGW and they are planning to implement carrier protection using OPGW.

It was felt that implementing digital carrier protection using OPGW is much costlier than PLCC and advised OPTCL to review the proposal once again.

Deliberations in the meeting.

C.G.M. (Telecom.) stated that a letter has been issued to PGCIL for joint verification regarding restoration of communication links for which OPTCL has laid OPGW. OPTCL will not go back with PLCC mode.   
[Action: CGM (Telecom) / SLDC / POWERGRID]

C.3: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly the updated status to on the same to Chief Engineer, Distribution Planning & Development Division, CEA.NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In 113th OCC, Member Secretary informed that during interaction with consultants of Grid Study Committee, NLDC agreed that they will plan for conducting workshops on crisis management plan for Cyber Security and few workshops will also be held in Eastern Region.

In the last meeting CGM (IT) stated that after attending the workshop at New Delhi on 15th January’2016, an action plan for crisis management will be prepared.
Deliberations in the meeting.

CGM (IT) stated that the draft crisis management plan is under preparation.
[Action: CGM (IT)]

C.4: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.

In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In 85th OCC NTPC informed that, NTPC-Farakka has been certified with IS 18001. Other constituents including OHPC requested to interact with BIS with intimation to ERPC and get certified as per CEA direction. The matter is getting reviewed by highest authorities with top priority.

In the last meeting CGM (O&M) stated that BIS is not responding for certification. SLDC may be get clarified from ERPC whether ISO or BIS is required. 

Deliberations in the meeting.

It was decided that CGM (O&M) shall again write to BIS for certification.
[Action: CGM (O&M)]

C.5: Pollution mapping for Eastern Region 

The Pollution Mapping work in ER was started with on-site measurement of ESDD and NSDD. 

The latest available status is as follows:

	Utility
	Scope
	Installed Locations
	Number of locations where 1st set of Measurements Completed

	OPTCL
	164
	102
	99


OCC advised all constituents to complete the 1st set of measurements and send to Powergrid/ CPRI. Powergrid vide mail dated 5th November, 2015 requested to complete the 2nd set of measurements by end of Novemebr, 2015, as it is already passed 4 months after completion of 1st set of measurements for the most of the locations.

In the last meeting CGM (O&M) stated that only Southco locations are left due to non-availability of testing kit. Since CPRI is not responding for supply of more kits, the existing kits will be diverted to Discom locations after completion of measurement for O&M locations.

Deliberations in the meeting
CGM (O&M) stated that testing kits will be diverted to Discom locations after completion of O&M locations.

[Action: CGM (O&M)]
C.6: Dynamic data of Generator Models required in PSSE for Simulations -- ERLDC

To carry out proper simulation studies in PSSE, actual generator parameters are required as incomplete or incorrect modeling of generator may not give valid simulation result. Hence all the generating companies are requested to furnish data for generator, exciter, governor, PSS of their all generating units in the format.

In 114th OCC, the house was informed that the formats are available at ERPC website.(www.erpc.gov.in)

OCC advised all the generating utilities to submit the relevant information as per the format.

All generating utilities agreed to submit.

Till 115th OCC, the data received only from NTPC Kahalgaon & Barh, NHPC Teesta-V, GMR and

CESC.

In 116th OCC, all the other constituents were advised to send the requisite information and ERLDC was requested to give the description of symbols and abbreviations for proper understanding of the constituents.

Subsequently, Vedanta Ltd. has submitted the relevant information vide mail dated 11.01.2016.
In the 117th OCC meeting, it was suggested that all the Generators shall forward the data to ERLDC at an early date.

Deliberations in the meeting
All the generators were requested to forward the data to ERLDC.
[Action: All Generators]

C.7: Information regarding commissioning of new transmission element

1. 765kV New Ranchi-Dharamjaygarh-II first time charged at 16:41hrs of 24/12/15.

2. 400kV Meramundali-Sterlite-D/C first time charged at 19:33 and 19:34hrs respectively of 30/12/15 
C.8: Mock Black start exercises in Eastern Region – ERLDC
	Sl. No.
	Name of Hydro Station
	Schedule
(1st)
	Tentative Date
	Schedule
(2nd)

	1
	U.Kolab
	Last week of May, 2015
	Done on 16/07/2015
	Last Week of January, 16

	2
	Rengali
	2nd week of June 2015
	Done on 13/10/2015
	February, 16

	3
	U. Indravati
	3rd week of June 2015
	Done on 16/07/2015
	2nd week of February 2016

	4
	Balimela
	1st week of November,15
	Done on 24/11/2015
	1st week of March 2016

	5
	Burla
	
	Done on 19/01/2016
	January 2016


Deliberations in the meeting
SLDC stated that the Mock black start exercise shall be done as per schedule.
[Action: SLDC / OHPC]

C.9: Restricted Governor Mode of Operation.
The latest status of units of ER under RGMO is available at ERPC website (http://www.erpc.gov.in/) under Operation>Important data. 

In 108th OCC, ERLDC informed that the RGMO/FGMO response of the generators needs monitoring on continuous basis. 
OCC advised ERLDC to intimate the event of sudden drop in frequency to the generators and requested all generators to provide the RGMO/FGMO response data to ERLDC during the said incidents. 

ERLDC informed that on 12.10.2015 there was sudden load loss of 900 MW in NR and they observed 0.11 Hz change in the grid frequency.

As per the data of ERLDC they have received the RGMO/FGMO response only from Burla, Kahalgaon, Teesta-V and SSL generators. The response of other generators are not satisfactory.

In the OCC meeting, reports received from OPGC & Chiplima PH have been handed over to ERLDC. 

In the OCC meeting, it was decided that hydro units of 10MW capacity & thermal units of 200MW capacity shall intimate the response of governor to ERLDC. 

ERLDC intimated that a new web group was formed for sharing governor response of various generator in ER. The url of the group is https://in.groups.yahoo.com/neo/groups/er_gov_respons/info
ERLDC requested to send email ids (preferably Yahoo mail ids) of the Generators where invitation will be sent. Governor response for the event of 12-11-2015 at 23:05 hrs based on ERLDC SCADA data is already posted in the group.
CERC in the RoP dated 14.07.15 in Petition No. 84/MP/2015 filed by NRLDC has directed as under:

“10. The Commission also directed SLDCs to approach their respective SERCs to initiate appropriate action under the Act against the State generating stations which have not provided adequate primary response during both grid events reported by the petitioner.” 

Deliberations in the meeting
SLDC stated that email ID of all generators has already been forwarded to ERLDC.

C.10: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s 

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.

In 117th OCC, OPTCL updated the completion schedule of inter-connecting system as follows:
	Sl. No.
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir S/S.
	7 out of 14 completed. Severe ROW problem. Negotiation under progress.

	b.
	LILO of one circuit of Katapalli-Sadeipalli 220 kV D/C line at Bolangir S/S.
	All work completed. Inspection left.

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (OPTCL) 220 kV D/C line
	Work order expected to be issued by Feb-16

	b.
	Keonjhar (PG)-Turumunga (OPTCL) 220 kV D/C Line.
	Yet to be awarded

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	It will take 1 year for completion.

	b.


	LILO of one circuit of Atri-Puri (Samangara) 220 kV D/C line at Pandiabil (PG)
	After commissioning Pandiabili S/S by Powergrid.


[Action: CGM (Const) / CGM (O&M) ]
C.11: Replacement / repair of meters on Various Locations

i. Replacement/Repair of Defective meter at Mendhasal – SLDC, Odisha

Meter at Mendhasal (GRIDCO) end of Mendhasal (GRIDCO) – Baripada (PG)- I is defective since more than last two months. SLDC, Odisha vide mail dated 05.01.2016 have requested for early replacement / repair of meter at Mendhasal. 

In the 117th OCC meeting Powergrid assured to make the replacement of meter by end of Jan’16.
ii. Installation of New SEMs at B/C panels at Joda Grid S/s of OPTCL - OPTCL

OTPCL vide mail dated 30.12.2015 have requested for installation of new SEMs at B/C panel at their Joda GSS for 220kV Joda- Ramchandarpur & Joda – Jindal Interstate tie lines.

In the 117th OCC meeting Powergrid requested to intimate the details of metering requirement at Joda sub-station.

Deliberations in the meeting

It was decided that OPTCL shall intimate the details of metering requirement at Joda.
[Action: CGM (O&M)]
C.12: Non-payment of Reactive energy charges by WBSETCL/WBSEDCL

xxxxxx         xxxxxxxx           xxxxxxxx

ERPC Secretariat also pointed that Meramundali S/s is also injecting VAR during high voltage and therefore OPTCL is paying huge VAR charges.

OPTCL was advised to take appropriate action to control the VAR injection during high voltage at Meramundali S/s.

In the 117th OCC meeting it was deliberated by SLDC to examine lowering 400kV bus voltage at Angul PG sub-station by tap changing. However, SLDC, Odisha is taking action for isolation of 400kV circuits during high voltage condition.

Deliberations in the meeting
Sr. G.M (PS) stated that on request of SLDC, POWERGRID has lowered the transformer tap position at Angul (PG) resulting decrease of the 400 kV Bus Voltage. All generators have been asked to control the VAr injection. 
[Action: SLDC / All Generators including CGPs]
C.13: Restoration of SCADA data

Updated latest status is circulated in the meeting. During deliberations in 99th OCC it was pointed out by most of the constituents that SCADA problem in many locations are due to behind the schedule progress of work on the part of CTU/PGCIL. OCC advised Powergrid / CTU to expedite and restore at least the priority RTUs by 31st July, 2014. 
The status as updated in the SCADA meeting is as given below:

	S/n
	Name of RTU Locations
	Latest status

	1
	Vedanta Ltd.(CGP)
	No isolator status is available.  MW/ MVAR not available for ICT-I & II, Station transformer / Smelter. CBs of Bus coupler not available. Bus-1 KV/ HZ not available.



	2
	Vedanta Ltd.(IPP) & SEZ
	Frequent interruption of data noticed.

	3
	Nalco
	OPTCL informed that RTU is reporting but intermittent since it was not configured properly.

The issue was already taken up with Nalco and it will be resolved soon.

OPTCL has resolved the issue. Some Unit generation polarity will be resolved by Feb 2015.

Problem still not resolved

	4
	JSPL (Meramundali -

400)
	Most of the data not available.




Deliberations in the meeting
CGM (Telecom) stated that reminder letter has been issued to Vedanta Limited (CGP). Vedanta (IPP) is reporting through ERLDC. MW / MVAr etc. data are available except some digital data. Nalco data are not yet restored. JSPL is on the job for restoration of data. CGM (RTC) may take action to approach OERC through Petition.

[CGM (Telecom) / CGM (RT&C)] 
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of DEcember’15 was reviewed.
It is noticed that CESU & WESCO had overdrawn a substantial quantum of power to the tune of 20.03 & 34.11 MU respectively, while SOUTHCO had over drawn 7.62 MU. 
Deliberations in the meeting.
SLDC stated that maximum number of messages were issued to WESCO followed by CESU for compliance of drawal schedule. All the Discoms were advised to submit realistic drawal schedule and to comply the schedule to maintain grid discipline and security.   
[Action: All Discom utilities]

D.2. High Voltage at 400 kV Meramundali & Duburi S/S_ Reactive Power Injection by OPTCL


Persistent high Voltage is being observed at Meramundali & Duburi 400 kV buses. Since these buses are the inter State exchange points, Reactive power injection penalty is being charged to Gridco. It is learnt that one no of 50 MVAr line reactor at Meramundali is not functioning. O&M may take action for rectification of the same early. It may also be examined for installation of 2nd reactor at Duburi to arrest the high Voltage. Further Powergrid may be requested to shift the line reactor of the 400 kV Baripada- New Duburi-Mendhasal ckt from Mendhasal to New Duburi. 

In the last meeting it was suggested for installation of additional reactor at Meramundali to control VAr injection at high Voltage conditions. Gridco may examine to approach the Commission for sharing of the penalty by the Generators / CGPs responsible for injection of VAr at high voltage condition. SLDC may monitor the VAr flow on real time basis and take all possible measures.

Deliberations in the meeting

It was again suggested that OPTCL to examine enhancement of reactor capacity at Meramundali S/S. 

[Action: CGM (O&M)]

D.3. Operation of Balimela unit with minimum generation


It is noticed that Balimela HEP is requesting to keep one unit in the bar with minimum generation to maintain the tail race level for pumping water requirement for cooling purpose. This lead to injection of power at high frequency conditions with penalty. The State is losing water potential and revenue as well.  

Deliberations in the meeting.

Director (Commercial) stated that OHPC may explore alternate arrangement to meet the cooling water requirement. Keeping unit with minimum generation results payment of penalty for injection at high frequency as well as wastage of water, which is precious in the present scenario.         

[Action: OHPC]
D.4: Revival of Station Transformer for Station Auxiliary supply at Balimela HEP.

It was suggested in earlier meetings for revival of station supply for Balimela HEP from Balimela Grid S/S. 
In the last meeting, OHPC stated that revival of station supply from Balimele 220/33 kV S/S will be done by end of January’ 2016.

Deliberations in the meeting
OHPC stated that the transformer in under the process of overhauling. 11 kV breakers are to be procured. At Balimela Grid, relays are not available. OPTCL may take action for commissioning of the relays soon. OPTCL stated that 11 kV VCB are available at Jharsuguda. OHPC may take the VCB for use at Balimela PH.

[Action: OHPC / OPTCL]

D.5: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl.No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220kV Jayanagar-Theruvali ckt-III breaker
	Breaker already erected but not commissioned. Isolator problem
	February’2016

	2
	220/132 kV, 100 MVA Auto-II at Duburi  
	
	Work will be taken up on February’16. 


[Action : CGM (O&M)]
D.6: Communication issues 
(i) Installation of communication equipment by CGPs / Industries.
The status of data communication from CGPs as deliberated in the last meeting is as follows

	Sl. No
	Name of CGP
	Present status

	1
	M/s IFFCO, Paradeep
	Outdoor commissioning work completed. RTU was locally tested. After replacement of the faulty CVT data will be integrated.

	2
	M/s MSP Mettalicks
	PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited.

	3
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	4
	M/s Adhunik Metalliks
	Integrated to SCADA

	5
	M/s Rohit Ferro tech
	PLCC established and inspection by Telecom Engineers completed.  Data base has already been prepared by OPTCL.    

	6
	M/s Vedanta Ltd. (IPP), Jharsuguda
	Generators data remains Suspect most of the times.


Deliberations in the meeting

It was decided that GCC, OPTCL may file a case before the OERC through RT&C wing of OPTCL against those CGPs not complying the data communication provisions with SLDC.
[Action: GCC / CGM (RT&C)/ CGM (Telecom)]
(ii) Interruption of SCADA.

It is noticed that there is frequent interruption of SCADA System, resulting problem in real time operation. Action may be taken to avoid such frequent interruption of SCADA.  

In the last meeting, Sr. G.M (Telecom) stated that Powergrid link between Rourkela-Kaniha is being used for data transfer. The link is not healthy due to heavy fibre loss. Powergrid have proposed to upgrade the existing SDH equipment to STM16. Work order has already been awarded.

Sr. G.M. (Telecom) stated that Powergrid will complete the work by 1st week of December’2015

In the last meeting it was decided that C.G.M. (PP) may raise this issue in the commercial sub-committee meeting of ERPC for passing on the penalty paid by Gridco by way of deviation charges to Powergrid. 

Deliberations in the meeting

C.G.M. (Telecom) stated that SDH equipment has already been commissioned.

D.7. Islanding Scheme of Ib TPS

The islanding scheme for IbTPS has already been commissioned but not functioning due to non- incorporate the trip commands to the breakers at Budhipadar from the Islanding Relay. This has already been discussed in the 81st PSOC meeting, wherein Telecom wing of OPTCL assured to complete the optical fibre link, provided IbTPs allow for working in their premises. Ib TPS had also agreed to allow them. The link is yet to be completed yet.

In the 91st meeting, Sr. G.M. (Telecom) stated that all works have been completed. It was decided that Sr. G.M (Telecom) shall intimate the same to Ib TPS and mark a copy to ERPC. 

Deliberations in the meeting

It was decided that OPGC shall finalize the date and intimate to CGM (Telecom) for providing connectivity and testing.

[Action : OPGC / CGM (Telecom)]

D.8: Web based drawal / generation scheduling.

SLDC is going to implement web based drawal / generation scheduling for Dist. Utilities and State generating stations including IPPs and CGPs soon. A demo has been organized on 29.07.15. 

In the last meeting, CGM (IT) stated that, web based generation scheduling module for State generating stations has been already been developed by IT wing. Modules for Discom and CGP / IPP shall be made available before the next PSOC meeting. After approval by the stake holders the same shall be go live from September’15. All Users were requested to forward their respective schedule in the prescribed format. 
In the last meeting IT representative deliberated that SLDC shall finalize the date for one day demonstration cum training programme at SLDC for web base scheduling. SLDC has written a letter to IT to make a demonstration at SLDC prior to finalization of the training programe.
In the last meeting SLDC stated that the issues in the software, raised by SLDC need to be rectified before finalizing the training date. 
Deliberations in the meeting

CGM (IT) stated that the problems identified by SLDC have been rectified. A demo shall be given at SLDC on 4th February. After that all generators will be invited for a Demo.

[Action: CGM (IT) / SLDC]

D.9: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

The work for Automatic Meter Reading (AMR) for all the interface points is in progress. 

In the last meeting all Discoms have agreed to display the meter data on the dashboard required for analysis purpose.
Deliberations in the meeting

CGM (IT) stated that from 1st March onwards the AMR shall be made “Go live”. Data will be available after one hour lapses of time.
[Action: CGM (IT)]

D.10: DISCOM Issues 
CESU

A.In the last meeting, it was decided that CESU shall approach O&M through a meeting to resolve bilateral issues. The discussion in the meeting may be placed in the next PSOC meeting.
B.

(i)   Mismatch of SCADA drawal with the billing meter data to the tune of 23 MU during December’15. 

(ii)   Fixed data indicated on Dashboard may be linked with SCADA. 

(iii)   Debit bill of CESU served by Gridco should not be linked with current bill, as decided in the meeting taken by CMD, Gridco. 

Deliberations in the meeting
A. CESU stated that the meeting with CGM (O&M) for resolving bilateral issues is yet to be done. 

B. SLDC stated that the SCADA data are for monitoring purpose only. It may not match with the meter data. CESU may analyze and ascertain the error correction factor at different time blocks for prediction of their drawal. It is not feasible to change the fixed data with respect to time. CESU may adopt the drawal pattern and change the fixed data for their use. Director (Commercial) stated that CESU is paying the BST bill deducting the rebate.
[Action: CESU]

PART E: OPERATIONAL PLANNING

E.1:  Commissioning status of New Transmission elements. 

The status of commissioning of new transmission elements is as follows:
	   Sl. No
	    Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by June 2016.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal, which is under progress. ICT is at BHEL factory

	3
	Commissioning of 220 kV Bidanasi-Cuttack line
	Work in progress and expected to be completed by March 2016.

	4
	Commissioning of 220/132 kV Cuttack S/S
	Work in progress and expected to be completed by March 2016.

	5
	Commissioning of 132 kV Baripada (PG)-Jaleswar line
	Work has already been started, which will be completed by June 2016. 

	6
	Commissioning of 220/132 kV Kesinga S/S
	Work under progress. Expected by September 2016.


Status of Discom’s action plan for power drawal from the S/Ss commissioned / expected to be commissioned in near future. 
	   Sl. No
	    Name of the sub-station
	Probable month of commissioning
	Name of DISCOM
	Action taken by Discoms

	1
	132/33kV, 2x20 MVA  Khajuriakota 
	March’16
	CESU
	Action being taken

	2
	132/33kV, 2x40 MVA  Kalunga 
	Charged 
	WESCO Utility
	Connected

	3
	220/33kV, 2x20 MVA Banei 
	Dec’16
	WESCO Utility
	Stayed by Court.

	4
	132/33kV, 2x20 MVA  Padmapur
	January’16
	WESCO Utility
	Line is ready

	5
	132/33kV, 2x20 MVA  Udala 
	Dec-16
	NESCO Utility
	Line existing


CESU stated that action is being taken for construction of 33/0.4 kV S/S at Mendhasal to avail power supply for Mendhasal area.
In the last meeting, it was suggested that WESCO shall explore the work for diversion of 11kV line at Sarsmal (Jharsuguda) and connecting 33 kV feeders with Lapanga Grid. 

Deliberations in the meeting

A.O WESCO stated that diversion of 11 kV lines from Jharusuguda S/S will be done soon.
[Action: CGM (Const) / CGM (O&M)/ All DISCOMS] 
E.2: Energy Metering at Hydro stations.
In the last meeting, OHPC stated that billing for all the OHPC stations except Upper Kolab is being done from the newly installed energy meters. The energy meters at Upper Kolab are have been rectified in the mean time.

In the last meeting it was decided that Gridco may consider these meters for billing purpose & SLDC will prepare the energy accounting for all State Generators.

Deliberations in the meeting

OHPC stated that there are mismatch in the recording for some of the energy meters. It was decided that OHPC shall identify those meters and intimate OPTCL. GRIDCO stated that energy meter for island feeder at Burla PH is yet to be installed. OPTCL shall take necessary action for installing / testing of those meters.

[Action: OHPC / OPTCL]

E.3: TTPS Issue.

Implementation of Feeder Metering
In the last meeting TTPS deliberated that all the meters were tested & calibrated by the STL on 09.10.2015. The 132kV CTs for TTPS-Duburi-1 have been replaced. Further, as per the PPA dated 08.03.1995, the energy meters are to be installed at GT end. Since the meter locations will be shifted to feeders, the corresponding clause in the PPA is required to be amended. Accordingly, the proposal has been sent to the competent authority of NTPC for approval.
As per the decision by Gridco the feeder metering has been implemented with effect from 1st October. SLDC has prepared the Deviation charge bill considering the feeder meter data for the month of October. 

TTPS in their letter No.045/GGM/TTPS, Dated. 20.11.2015 addressed to CGM (PP) Gridco pointed out that, as per clause 7(1), 1st proviso of CEA (Installation and operation of Energy meters) Regulation, 2006 as amended in 2010 “ for existing stations the location of Main, Check and Standby meters shall not be changed unless permitted by the Authority”.

In the present case, for the first time, energy meters have been installed at the interface points, which should have been installed earlier, without changing the position of the existing meters. As such the regulation as mentioned by TTPS is not applicable. However the existing meters will be treated as standby meters.  

In the last meeting, TTPS stated that they have written to CEA for clearance to the feeder meter installation, in view of which the metering may be considered from 1st November’ 2015. Director (Commerce) stated that installation of feeder meters will be informed to CEA by Gridco and NTPC. 

It is noticed that there are considerable time delay to the tune of 0.5 - 8 hours between the Generator meter & feeders resulting wide mismatch of both the meter data, which calls for time synchronization.

In the last meeting TTPS stated that they have written to CEA for clearance to the feeder meter installation. It was decided that TTPS shall forward a copy of the letter to Gridco. OPTCL may explore installation of new meters at TTPS feeders.

Deliberations in the meeting

GRIDCO stated that, in response to the letter of GRIDCO, CEA has sought for some information such as location of Main, Check and Standby meters. TTPS was requested to comply those queries.  
[Action: TTPS / GRIDCO/ OPTCL]

E.4: Major Events in the month of December’15

30.12.2015: 400 kV Vedanta-Meramundali D/C line charged.

E.5: Important Grid Incidences during the month of December’15.
There was only one major incident during the month of December 2015 at Meramundali S/S due to bursting of 400 kV LA. 
E.6: Outage of major transmission Elements during the month of December’15. (above 10 hrs).
Outage of major transmission elements above 10 hours during the month of Dec-15 was reviewed. 
Major outages are due to LA bursting.
E.7:  Review of Outage Program of State Generators / Transmission elements for the month of February’2016:
Tentative Outage programme for State Generators for the month of February’2016 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 2
# 4
# 6
	08.02.16 to 15.07.16
25.01.16 to 24.02.16
17.02.14 to continue
	Capital Maintenance

Annual Maintenance

Programming for R, M & U

	2
	Chiplima
	#3
	15.02.14 to continue
	Programming for R, M &U 

	3
	Balimela
	# 1

# 6
	31.01.13 to continue

18.01.16 to 11.02.16
	TGB problem and started R,M & U

Annual maintenance

	4
	Upper Kolab
	# 1
	29.07.15 to 25.02.16
	Capital Maintenance

	5
	Rengali
	# 2
	06.01.16 to 05.02.16
	Annual maintenance

	6
	Upper Indravati
	# 3
	23.11.15 to 30.04.16
	Capital Maintenance


E.8: Generation Program for the month of February’16.
Generation schedule for the month of February’16 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Programme (MW)
	Reservoir Level as on 15.01.15
	Reservoir Level as on 15.01.16
	MDDL
	High Flood    Reservoir Level

	
	Feb’16

(1st fortnight)
	Feb’16

(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	15
	15
	624.451ft 
	623.73ft
	590 ft.
	630 ft.

	HPS-II, Chipilima
	10
	10
	-
	-
	-
	-

	Balimela
	30
	30
	1507.70ft 
	1495.70ft
	1440 ft.
	1516 ft.

	Rengali
	25
	25
	120.92mt

1.78mt mtr mt
	118.07mt mt
	109.72mtr 
	123.5 mtr.

	U.Kolab
	100
	100
	856.30mt mt
	855.54mt
	844 mtr 
	858 mtr.

	U. Indravati
	75
	75
	639.77mt
	634.83mt mt
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2742.80ft 
	2741.45ft
	2685 ft.
	2750 ft.

	TOTAL
	285
	285
	
	
	
	


E.9: RSP (SAIL), Rourkela Issue.
(i) Review of relay settings of Tarkera grid to RSP 220kV feeders

(ii) Clearance for construction of two 220kV bays at Tarkera grid sub-station and construction of 220kV D/C line.

In the last meeting, CGM (O&M) stated that WESCO has not intimated the proposal regarding enhancement of contract demand RSP. Field inspection report for feasibility of 220 kV bay at Tarkera is yet to be received.
The item could not be discussed as RSP was not present in the meeting.
E.10:  Operating procedure for Odisha System.

As per provision in the Regulation 5.1(4) of Odisha  Grid Code, the draft Operating Procedure for Odisha System has been prepared and uploaded in the SLDC site (path: Document    information). Members are requested and forward their comments / suggestions to SLDC before 15th December2015. No comments has been received from Members except OHPC. The final Operating Procedure shall be placed in the next meeting. 

E.11: Anticipated power generation and demand for the month of February’2016.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	850
	1250

	2
	WESCO
	880
	1150

	3
	NESCO
	770
	980

	4
	SOUTHCO
	370
	550

	5
	Total
	2870
	3930

	Availability
	
	

	
	Hydro
	285
	1280

	
	State Thermal
	640
	600

	
	IPP, small hydro &RE
	700
	700

	
	ISGS share (including OA)
	1000
	1100

	
	CGP support (OA)
	250
	250

	6
	Total availability
	2875
	3950

	7
	Surplus / Deficit
	5
	20


PART F: OTHER ISSUES

F.1:  Date and Venue of the next (94th) PSOC meeting.

Deliberations in the meeting

The date and venue of 94th PSOC meeting shall be intimated. Vote of thanks was offered by the G.M. (GO).
ANNEXURE

[image: image2.png]93rd Power System Operational Co-ordination Review Meeting
~ [At11:00 A.M. on 30.01.2015]
[At Power Training Center, OPTCL, Chandaka, Bhubaneswar]

S
&
S

—

4 cvore oon | oure 01 1700
Tt 1+ seretm ] OpralTrmtsone
2] M

U 33907823 (1S9 g mvho
Hovie 24
y%9060| L RS LIRS Ay |

>
-
(&)

~
kB

Fr, Se#)y S.GcMm o0HPL

s

\

5|
<
X
2
<
>
[a]
i
~
)
O
=
3
\o
n
i
O
n

N
<
7
S\
3
Ly
i
N
3
‘\.
~O
X
§
S
S
Q\‘;
o3
X
N
e

dEEEE
SN
E i
g\ g
= & &
]V
At
S
F .-
o S
wd
&
Q
<
P
N\
¢
s
5
<

7—

V/’

-—

T
s
)

‘A;
-
3

L
N4
IS

(\_
=8
%
[EAY
30
"o ¥
1Y
.
I

7| SR, S SR
f 'r-i-’t' Quel | 7#520 20108 0\
ﬂ’%}%ée% : o =
fr K A 7438967 Y73
Fu26%7 14t
2| Sk D#
3¢ R MiskvalfamED) opreL [9438507305
74359 78
§-\<~H‘ anded -

-

;

!
3
=

i
<
2
N
3
%





     [image: image3.png]29

C R B ey BT %3
K Miehve G’rm-(m
e

7
)

Q&
I
>

] e
IRk
gig
.| 2o
3
0D
=

W
EN

BY
.;:-’

b
b

:

3

—

ok
i





