[image: image1.png]: STATE LOAD DESPATCH CENTRE
ﬁg OFFICE OF THE CHIEF LOAD DESPATCHER
- . ODISHA POWER TRANSMISSION CORPORATION LIMITED
P T L GRIDCO Colony, P.O.- Mancheswar Rly. Colony, Bhubaneswar-17, FAX-0674- 2748509
Lifeline of Odishs CIN — U401020R2004SGC007553
No-SGM (PS)-PL-15/2015/ | l4 %ﬂ?}*u"v Dated:22.05.2016
From:

The Chief Load Despatcher
SLDC, OPTCL, Bhubaneswar-17.

To:

As per distribution list

Sub: Minutes of 97" Power System Operational Co-ordination meeting held on
17.05.2016 at PTC, Chandaka .

Sir,
Please find enclosed herewith the minutes of 97™ Power System Operational Co-

ordination meeting held on 17.05.2016 at Power Training Centre, Chandaka.

This is for your information & necessary action.

Yours faithfully;
Encl: As above

Chief L¥ad espatcher,
SLDC, OPTCL

Copy along with enclosures forwarded to the Executive Assistant to CMD, Gridco / OPTCL
for kind information of CMD.




Distribution list

1. The Director (Commercial), GRIDCO, Bhubaneswar.

2. The Director (Operation), OHPC, Bhubaneswar

3. The CGM (O&M), OPTCL, Bhubaneswar.

4. The CGM (Const.), OPTCL Bhubaneswar.

5. The CGM (RT&C), OPTCL, Bhubaneswar.

6. The CGM (PP), GRIDCO, Bhubaneswar.
7. The CGM (Telecom), OPTCL, Bhubaneswar.

8. The CGM (IT), OPTCL, Bhubaneswar.

9. The Sr. G.M (Const)-I, OPTCL, Bhubaneswar.

10. The Sr. G.M (Const)-II, OPTCL, Sambalpur.

11. The Sr. G.M (CPC), OPTCL, Bhubaneswar.

12. The Sr. G.M (CP), OPTCL, Bhubaneswar.

13. The Sr. G.M. (O&M), Zone-I, Narendrapur.

14. The Sr. G.M.(O&M), Zone-II, Meramundali.

15. The CEO, CESU, Bhubaneswar.

16. The A.O., WESCO Utility, Burla

17. The A.O., NESCO Utility, Balasore

18. The A.O., SOUTHCO Utility, Berhampur.

19. The Member Secretary (GCC), OPTCL.

20. The ED, Power Grid Corporation of India, Bhubaneswar.

21. The Sr. G.M. (El.), BHEP, Balimela

22. The A.G.M. (El.), CHEP, Chiplima

23. The Sr. G.M. (El.), UIHEP, Mukhiguda

24. The Sr. G.M. (El.), RHEP, Rengali

25. The D.G.M. (El.), HHEP, Burla

26. The D.G.M. (El.), UKHEP, Bariniput, Koraput

27. The S.E. (O&M), Machhakund

28. The DGM (Elect.),  IbTPS, OPGC, Banharpali.

29. The Vice President (O), IMFA, Choudwar.

30. The D.G.M. (O&M), NTPC (TTPS), Talcher.

31. The AGM (Elect.), JINDAL Stainless Ltd., Duburi

32. The G.M, HINDALCO, Hirakud.

33. The G.M.CPP, NALCO, Angul.

34. The Director, M/s. Jindal Steel & Power Ltd., Angul

35. The AVP-Vedanta Ltd (IPP), Jharsuguda

36. The G.M, Vedanta Ltd (CGP), Jharsuguda.

37. The DGM (Power Distribution), RSP, Rourkela.

38. Joint President, Aditya Aluminium Ltd., Lapanga, Sambalpur

39. The G.M.(Elect.),  Bhusan Steel Limited. Meramundali

40. The G.M. (Elect.), Bhusan Power & Steel Ltd, Budhipadar.
41. The G.M.(Elect.), IFFCO Limited.

42. Director & COO, GMR Kamalanga Energy Limited, Satyanagar, Bhubaneswar.

43. The CEO, Bhubaneswar Power Pvt. Ltd, IRC Village, Nayapalli, Bhubaneswar
Odisha Power Transmission Corporation Ltd. Bhubaneswar.


Minutes of 97th PSOC meeting held on 17.05.2016 at PTC, Chandaka
List of participants is at Annexure.

Chief Load Despatcher, SLDC, OPTCL welcomed all the participants to the 97th Power System Operational Coordination meeting and highlighted the system performance during the month of April’2016 and overall power scenario of the State. He also emphasized on the drawal by all the Discoms during the month. 
The meeting was chaired by CGM (O&M), OPTCL. 

D.G.M. (SS), SLDC took the agenda items for discussion. 

The review proceeded as follows: 
1: Confirmation of minutes of 96th PSOC meeting held on 25.04.2016
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2015/1319(43) dated 07.05.2016 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members.

Deliberation in the meeting:
Since no comments have received from the members, the minutes of 96th PSOC meeting was confirmed. 
PART A: List of items
List of items to be discussed in the meeting are given in the subsequent parts 
PART B : SYSTEM PERFORMANCE
B1: Review of Grid Performance for the month of April’2016.
(A)  Frequency 

It was noticed that, during the month of April’16, 71.66 % of times the frequency remained in the IEGC band i.e.  49.90Hz - 50.05Hz in comparison to 73.46 % during the month of  March’16. The maximum and minimum System frequency during the month was 50.16 Hz & 49.73 Hz respectively.

 (B)  Grid demand 

Grid demand for the month of  April’16 was reviewed. The average consumption during the month was 3233 MW. The maximum System demand of 4097 MW occurred on 27.04.16 at 21:00 Hrs and minimum demand of 2315 MW occurred on 15.04.16 at 10:00 Hrs. 
Deliberation in the meeting

It is observed that the average demand during the month of  April’ 16 was increased by 3 MW and the peak demand  was decreased by 78 MW from that of March’16. The average energy consumption during the month has been increased by 236 MW in comparison to April’15. 
 (C)  Voltage Profile of important Sub Stations in OPTCL System during the month of Apr’16.

The Voltage profile at different 220 kV buses in OPTCL system during the month of April’16 was reviewed. 
Deliberation in the meeting:
The maximum Voltage of 242.88 kV occurred at Jaynagar 220 kV bus while Narendrapur, 220 kV bus has experienced the minimum Voltage of 166.39 kV. Bus Voltages at Samangara and Lapanga could not be incorporated due to non availability of energy meter in those S/Ss.

CGM (O&M) stated that the tender for procurement of energy meters is under process. Khurda Voltage profile has been improved after feeding from Atri S/S. Narendrapur Voltage profile can be improved after charging of Pandiabili PG S/S. 
Order for procurement of Apex meters has been placed.
Since the reserve bus of Khurda is being engaged for 132kV Kaipadar Traction feeder all the times, it is suggested that Railway authority may be insisted to avail power supply from 220 / 132kV Atri  sub-station for better stability.









        
        [Action: CGM (O&M)]

(D) Loading of 220/ 132 kV Auto at 220 kV S/Ss in OPTCL system for the month of April’16.

Auto loading of all 220 kV S/Ss was reviewed. It was noticed that some of the ICTs have not been provided with energy meter. 
Deliberation in the meeting:
 It was deliberated that tender for procurement of Energy Audit meters has already been placed.










        
        [Action: CGM (O&M)]

(E) DISCOM Drawal during the month of April’16 
The schedule and actual energy drawal by Discoms for the month of April’16 was reviewed. 
Deliberation in the meeting:
It was noticed that CESU had overdrawn 32.346 MU followed by WESCO Utility 21.619 MU during the month, while NESCO Utility and Southco Utility had drawn  energy almost as per their schedule. All Distribution Utilities were requested to comply with their respective drawal schedule. 
CESU stated that Bidanasi & Mendhasal data are not being displayed. SLDC stated that CESU is not revising its drawal schedule in case of overdraw in spite of reminder from SLDC. Further, the revision request by CESU is being received after lapses of considerable time e.g. 2 to 3 blocks that to not for the full drawal quantum.
It was decided that in case the Distribution Utilities are not complying their drawal schedule, SLDC shall revise the drawal schedule as per actual after due intimation to them after one time block to which all Distribution Utilities agreed.

CESU should analyze the data comparing with the actual metered drawal and ascertain the correction factors in different blocks. 
[Action: All Distribution Utilities / SLDC]
(F) Energy Generation / import during the month of April’16 
Energy generation and exchange during the month of  April’16 was reviewed. The total quantum of energy drawn from all the generation sources including Central Sector Share and CGP/IPP support during the month was 2327.68 MU. 
 (G) Drawal of Machhakund Power during the month of April’16
The drawal of Machhakund power during the month of April’16 was 19.714MU against AP drawal of 21.032 MU. 
Deliberations in the meeting:
Sr. GM (O&M) -I proposed that, Jayanagar S/S shall monitor Machhakund generation and take the responsibility for drawal of State’s share of power to which SLDC agreed.

Southco stated that inspection of 33 kV Akhusing –Gumuda feeder has been completed. The feeder will be charged after receive of inspection report. 

CGM (Telecom) stated that the offer of M/s Chemtrol for the installation of RVDU at Jayanagar control room has been forwarded to SLDC for views. CLD, SLDC shall forward the proposal to CMD.
  [Action: Sr.GM (O&M)-I / OHPC / Southco / Gridco / SLDC]

 (H) Under Frequency relay operation in OPTCL System during the month of April’16.

There is no UF Relay operation occurred during the month of April’16 as the frequency had never gone beyond 48.50 Hz. 
(I) Status of Open Access applications during the month of April’2016

Status of Open Access Applications received and disposed by SLDC was reviewed.

PART C – Issues to be raised in 121th OCC meeting of ERPC scheduled on 23.05.16

C.1: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implementation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

In 119th OCC, advised all the SLDCs to implement the ADMS in their respective control area by 30.06.2016.

Subsequently, on request from DVC & WBSEDCL, ERPC vide letter dated 05.04.2016 requested Powergrid to take up the issue for inclusion of DMS/ADMS application software in the new SCADA system under new ULDC project which would be of great help for the ER constituents in implementing the ADMS system in their respective control area and subsequent compliance of CERC directive
As decided in the 95th PSOC, SLDC has invited offer for providing consultancy service to prepare the tender documents for implementation of ADMS in OPTCL system. 

In the 120th OCC meeting, Powergrid informed that it is possible to implement in new SCADA system.

After detailed deliberation, OCC referred the issue to 7th PRM meeting for further course of action.
Agenda placed in 7th PRM meeting held on 09.05.2016

Powergrid vide letter dated 22.04.16 communicated that automatic load shedding & restoration feature, named "Load Shed Support (LSS)", is already provisioned in the supplied new SCADA System for substations above 132 kV and this feature has already been tested / demonstrated for SLDCs of Eastern Region during commissioning stage. 

However, the implementation of ADMS at distribution level (below 132kV) may be ensured by respective SLDCS / SEBS.

In the last PSOC meeting, CLD, SLDC stated that SLDC has already invited offer for providing consultancy service to prepare the tender documents for implementation of ADMS in OPTCL system.  

Offer for consultancy has already been received from two firms which are yet to be evaluated. Prior to take a decision, it must be ascertained regarding incorporation of automatic load shedding & restoration feature, named "Load Shed Support (LSS)" in distribution system. CGM (Telecom) may take necessary initiative with Powergrid in this regard.
Deliberations in the meeting:
CGM (Telecom) stated that 30 Nos. of RTUs have been installed by M/S Chemtrol, in which provision of “Load Shed Support (LSS)” does not exist. OPTCL is processing tender for installation of 60 Nos of RTU for replacement of existing RTUs. The LSS feature shall be incorporated in these RTUs.  CLD, SLDC stated that Telecom may raise this issue before ERPC to insist POWERFRID for adding this feature in the RTUs already installed by Chemtrol. However, implementation of ADMS can be carried out with those new RTUs.
[Action: SLDC/ CGM (Telecom)/O&M]

C.2: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s 

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha. The status deliberated in the last meeting as detailed.
	Sl. No.
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir S/S.
	7 out of 14 completed. Severe ROW problem. Negotiation under progress.

	b.
	LILO of one circuit of Katapalli-Sadeipalli 220 kV D/C line at Bolangir S/S.
	Charged on 04.05.2016

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (OPTCL) 220 kV D/C line
	Work order for 220 kV S/S at Keonjhar and associated lines is under process

	b.
	Keonjhar (PG)-Turumunga (OPTCL) 220 kV D/C Line.
	Work will be taken up under JICA scheme.

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	Work order placed.

	b.


	LILO of one circuit of Atri-Puri (Samangara) 220 kV D/C line at Pandiabil (PG)
	Pandiabili S/S is expected to be completed by July’16. LILO of Atri-Samangra 220 kV line at Pandiabili by July’16.


Sr. G.M (O&M)-II stated that 220 kV BolangirPG-Bolangir line may be overloaded at any time, as more upcoming loads are expected at Bolangir(N) S/S. To avoid this, commissioning of Kesinga 220 kV S/S and LILO of Bolangir- Kesinga 220 kV line trough Bolangir PG is essential.  
[Action: CGM (Const) / CGM (O&M)] 
C.3: Restoration of PLCC system of important lines

1)   In 119th OCC, JUSNL informed that the following:

In 220 KV Ramchandrapur-Joda line auto-reclosure has been enabled and termination done in PLCC panels at Ramchandrapur end but due to non-availability of PLCC panels at Joda (OPTCL) end the A/R and PLCC scheme could not be implemented.

Further, it was informed that JUSNL is ready to share their standby PLCC panels (BPL make) with WBPDCL (for Santaldih end) and OPTCL (for Joda end) to complete the PLCC schemes of both the above lines.

OCC advised WBPDCL and OPTCL to accept the JUSNL offer and implement the PLCC scheme at the earliest for both the 220 kV lines.

WBPDCL and OPTCL agreed and nominated their coordinators as follows to complete the work:

2)  For 220 kV Ramchandrapur-Joda line:

Sh. L. Nayak, GM, OPTCL, M.- 943890780, e-mail: ele.lanayak@optcl.co.in

(ERPC Secretariat has issued a fax message vide no. 138 dated 21.03.2016 to JUSNL for taking up the issue with the above nominated coordinators for restoring the PLCC scheme of both the lines at the earliest.)
OPTCL vide mail dated 16.03.2016 informed the PLCC communication status of the important links under OPTCL as follows:

1. Jeypore(PG)-Jayanagar (Commn. in OPGW exists)

2. Rourkela(PG)-Tarkera (Commn. in OPGW exists)

3. Rengali(PG)-Rengali S/Y (Proposal for Commn. in OPGW is pending)

4.Indravati(PG)-Indravati(PH) (Proposal for Commn. in OPGW pending)

5.Baripada(PG)-Baripada ( Tendering in Progress for OPGW)

6.Baripada(PG)-Rairangpur (Tendering in Progress for OPGW)

Subsequently, JUSNL vide letter dated 13.04.2016 has asked for consent of OPTCL and WBPDCL for cost estimate details for further needful action.

Deliberations in the meeting:
C.G.M (Telecom) stated that the approved estimate for Sl. 3 & 4 has been sent to CPC for initiating tendering process. 
[Action: CGM (Telecom) / CGM (O&M)]

C.4: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In 113th OCC, Member Secretary informed that during interaction with consultants of Grid Study Committee, NLDC agreed that they will plan for conducting workshops on crisis management plan for Cyber Security and few workshops will also be held in Eastern Region.

In the last meeting, CGM (IT) stated that the draft report has been prepared, which has to be finalized by the consultant. After finalizing the report, a workshop shall be organized by IT.

In the 95th PSOC IT representative stated that tendering for consultancy has been done. It may take one month time.
Deliberations in the meeting:
CGM (IT) stated that tender documents for providing consultancy service are with finance wing of OPTCL. Appointment of Consultant is expected to be done by June’2016.
 [Action: CGM (IT)]

C.5: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.

In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In 85th OCC, NTPC informed that NTPC-Farakka has been certified with IS 18001. Other constituents including OHPC requested to interact with BIS with intimation to ERPC and get certified as per CEA direction. The matter is getting reviewed by highest authorities with top priority.

In the 95th PSOC, O&M stated that BIS, Kolkata have responded to send their offer
Deliberations in the meeting:
O&M stated that the data required by BIS, Kolkata will be furnished. 
[Action: CGM (O&M)]

C.6: Dynamic data of Generator Models required in PSSE for Simulations – ERLDC

To carryout proper simulation studies in PSSE, actual generator parameters are required as incomplete or incorrect modeling of generator may not give valid simulation result. Hence all the generating companies are requested to furnish data for generator, exciter, governor, PSS of their all generating units in the format.

In 114th OCC, the house was informed that the formats are available at ERPC website.(www.erpc.gov.in)

OCC advised all the generating utilities to submit the relevant information as per the format.

In the 95th PSOC meeting, OHPC stated that only 30 % data are available with them. SLDC stated that they may forward the data to ERPC / ERLDC. All other generators including CPPs may furnish their data to ERPC.
Deliberations in the meeting:
OPGC and OHPC stated that they have submitted the data in respect of their units to ERPC. 
[Action: OHPC/ All generators /CPPs]

C.7: Realization of Revenue loss by OPTCL due to shut down of EHV lines for diversion work for the Railway Line and other beneficiaries.
OPTCL vide letter dated 17.03.2016 intimated that OPTCL has devised a formula with due approval by its Board of Directors and started claiming shut down charges due to shutdown of EHV lines for diversion work for the Railway Line and other beneficiaries. Thus, the same may be claimed by other organization so that this uniform policy can be adopted by all Transmission Utilities.

In the 120th OCC meeting, OPTCL informed that they are yet to start the implementation of the said mechanism. Other constituents informed that they are not claiming any shutdown charges from other utilities however, they need to devise a mechanism.

OCC requested all the constituents to communicate their views.

Deliberations in the meeting:
CGM (Const) stated that Rly authority have already started payment as per the mechanism.

[SLDC: To deliberate in OCC]

C.8: Status of Emergency Restoration System (ERS Towers) for Eastern Region constituents

The latest status of Emergency Restoration System (ERS towers) as well as the future plan of procurement as informed by OPTCL:

 220 kV ERS towers: 42 nos located at Mancheswar, Chatrapur & Budhipadar

 400 kV ERS towers: 2 nos located at Mancheswar.

     12 nos. of new 400 kV ERS towers have been approved by Board of Director for procurement in the current financial year.

 Another 16 nos of 400 kV towers accompanied with 6 sets of T&P are required.
Deliberations in the meeting:
CGM (O&M) stated that Order has been placed for 12 Nos of 400 kV ERS towers.

[Action: CGM (O&M)]
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of April’16 was reviewed.
It is noticed that CESU had overdrawn a substantial quantum of power to the tune of 32.346 MU followed by WESCO to the tune of  22 MU, while SOUTHCO & NESCO had almost drawn as per the schedule. 
Deliberations in the meeting:
SLDC stated that number of messages were issued to CESU for compliance of drawal schedule. All the Discoms were advised to remain in the schedule to maintain grid discipline and security.   
[Action: All Discom utilities]

D.2: Revival of Station Transformer for Station Auxiliary supply at Balimela HEP.

It was suggested in earlier meetings for revival of station supply for Balimela HEP from Balimela Grid S/S. 
In the 95th PSOC meeting, OHPC stated that revival of station supply from Balimela 220/33 kV S/S will be done by end of March’ 2016.
Deliberations in the meeting:
OHPC stated that the 33 kV feeder has already been charged. Southco Utility may take action for installation of energy meters.
 
[Action: Southco Utility] 
D.3: Reporting of major incidents to SLDC.

On 10.05.2016, 400 kV Meramundali-New Duburi D/C line tripped due to collapse of towers. Since the incident was not reported to SLDC by the field unit of O&M, SLDC could not reply the query of ERLDC. It should be ensured that all such major incidents should be reported to SLDC, soon after its occurrence.

Deliberations in the meeting:
CGM (Cons) stated that the tower collapse can only be ascertained after line patrolling. However, the incident with relay indications shall be reported to SLDC.
[Action: O&M]
D.4: Shutdown of Transmission elements.

It is noticed that, permission for shutdown of 400 kV lines are forwarded by officers below the rank of DGM, for which ERLDC is objecting. Shutdown request for such elements should be forwarded by D.G.M level officers. Also, sometimes the senior officers are not aware of the shutdown proposal. All shutdown proposals should be forwarded by the appropriate level officers in consultation with their respective DGM, G.M and Sr. G.M. All O&M field units may be instructed accordingly. 

Deliberations in the meeting:
CGM (O&M) stated that it is not necessarily required for routing the shutdown proposal through DGM, as many O&M Divisions are headed by AGM. However, the shutdown proposal should be routed through the Divisional head. 

[Action: Sr. G.M (O&M)-I &Sr. G.M(O&M)- II]

D.5: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl.No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	132 kV Jayanagar-Sunabeda line
	For conversion to double ckt
	June’16.

	2
	220 kV TTPS-Joda ckt-I
	Replacement of conductor
	May’2016

	3
	220 kV Meramundali-Bhanjanagar ckt-I
	Replacement of conductor
	April’2016


Deliberations in the meeting:
CGM (Const) stated that permission for Rly. line crossing, NH crossing and 33 kV line crossing have been availed from the concerned authorities. After completion of the above crossings the shutdown of 132 kV Jayanagar-Sunabeda line will be returned. 
 [Action: C.G.M. (O&M)]
D.6. Maintenance of 400 kV Indravati (OHPC)- Indravati (PG) S/C line.

Indravati(OHPC)-Indravati(PG) 400 kV S/C line was being maintained by Powergrid since commissioning of the line. At present Powergrid is insisting OHPC / OPTCL for maintenance of the said line. As per Powergrid’s statement, the line and bay at PGCIL end belongs to the then OSEB. A meeting was convened between Powergrid, OPTCL, Gridco and SLDC to resolve the ownership dispute. Powergrid vide their letter dated 19.03.2016, addressed to CGM (O&M) also indicated the same and requested OPTCL to take up the maintenance work. The line was tripped at PG end due to blasting of R-phase CB. OHPC and OPTCL may verify the records and resolve the issue.

In the 95th PSOC meeting Powergrid stated that since the line and bay at Indravati PG belongs to OPTCL / OHPC they should take up the maintenance work. Director (Commercial ) stated that OHPC may collect the documents pertaining the ownership of the line and ICT at Indravati (OHPC) S/S from Govt. office, as the matter was dealt by the then Indravati Cell of under Electricity-cum –Electrical Projects. OHPC may intimate to OPTCL, the details of the 400 kV SC line. CGM (O&M) stated that let Powergrid maintain the bay at Indravati (PG) and OPTCL the two nos of bays at Mendhasal S/S (Baripada PG and Duburi line) for smooth operation of the system. It was decided that a meeting shall be convened to take a decision in this regard by 15th April’16. It was further decided that OPTCL shall provide the breaker pole and Powergrid will take up the restoration work. OHPC shall coordinate.

Deliberations in the meeting:
CGM (O&M) stated that the meeting with Powergrid could not be held. OPTCL shall convey the meeting again to discuss the issue.

[Action: CGM (O&M) / OHPC / POWERGRID]

D.7: Communication issues 
Installation of communication equipment by CGPs / Industries.
The status of data communication from CGPs as deliberated in the last meeting is as follows

	   Sl. 
	Name of CGP
	Present status

	1
	M/s IFFCO, Paradeep
	Outdoor commissioning work completed. RTU was locally tested. After replacement of the faulty CVT, data will be integrated.

	2
	M/s MSP Mettalicks
	PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited.

	3
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC / SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	4
	M/s Rohit Ferro tech
	PLCC established and inspection by Telecom Engineers completed.  Database has already been prepared by OPTCL.    

	5
	M/s Vedanta Ltd. (IPP), Jharsuguda
	Generators data remains suspect most of the times.


It was decided that GCC, OPTCL may file a case before the OERC through RT&C wing of OPTCL against those CGPs not complying the data communication provisions with SLDC.
Deliberations in the meeting:
CGM (Telecom.) intimated that the status mentioned above remains same. It was decided that GCC shall convey a special meeting with the defaulting CGPs & industries. 
[Action: GCC / O&M / RT&C/ C.G.M. (Telecom.)]
D.8: Web based drawal / generation scheduling.

SLDC is going to implement web based drawal / generation scheduling for Dist. Utilities and State generating stations including IPPs and CGPs soon. 
SLDC had organized a training on web based scheduling on 11.05.2016 for all the CGPs connected with OPTCL network. The feedback of the CGPs will be forwarded to IT wing.
Deliberations in the meeting:
CGM(IT) stated that SLDC shall compile the feedback received from CGPs and sent to IT wing for necessary action.
[Action: CGM (IT) / SLDC] 

D.9: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

The work for Automatic Meter Reading (AMR) for all the interface points is in progress. 

In the last meeting all Discoms have agreed to display the meter data on the dashboard required for analysis purpose.
In the last meeting CGM (IT) stated that from 1st March onwards the AMR shall be made “Go live”. Data will be available after one hour lapses of time.

CGM (IT) stated that AMR data for six types of meters has been mailed to GM (SLDC) for checking and acceptance. Action will be taken after acceptance of the data.

In the 95th PSOC IT stated that after receiving report from SLDC the process will be implemented.

It was decided in the 96th PSOC that SLDC will finalize the checking and sent the report to IT by end of April’2016.
Deliberations in the meeting:
SLDC stated that presently the billing is being done without considering harmonics. IT shall convene a separate meeting with TCS, SLDC & GRIDCO to address the issue.
 [Action: SLDC / IT]
D.10: Software for Deviation charge billing.

Hon’ble OERC may notify “Intra State Deviation settlement and related matters” Regulation at any time. For implementation of the regulation, required software for Deviation Charge billing need to be developed and tested. CGM (IT) may take necessary steps for development of the software.

In the 95th PSOC, IT stated that the proposal for appointment of outside agency for development of the software has been placed before the CMD for approval.

In the last meeting CGM (IT) stated that the proposal for appointment of outside agency for development of the software is pending with the finance wing of OPTCL, after which it will be forwarded to CMD, OPTCL for approval.

Deliberations in the meeting:
CGM (IT) stated that CMD has already approved the proposal. IT has invited offer from M/s TCS. SLDC suggested to expedite the software development.
[Action: SLDC/IT]   

D.11: DISCOM Issues 
CESU

A. CESU has advised to all of their SEs/EEs to undertake joint survey for resolve of different issues relating to augmentation of EHT S/S capacity, conversion of S/C line to D/C, bay extension at different S/Ss etc., to (O&M) and Construction wings of OPTCL in line with the discussions made in the technical workshop on “Effective Grid Management” held on 19.04.2016. 

B.

(i)      Mismatch of SCADA drawal with the billing meter during April’16. 

(ii)     Fixed data indicated on dashboard may be converted to variable for accurate drawal display. 

(iii)     Interruption in RVDU data.

(iv)     Provision of on line recording of drawal data for CESU on real time basis.

(v)     Gridco to facilitate for realizing the long outstanding dues of CESU from WESCO & NESCO.

(vi)    Provision of RVDU at CESU Head quarter.

(vii)    Providing realististic drawal incorporating “correction factor” by SLDC.

(viii) Expedition of AMR project.

(ix)   Implementation of UI bill instead of deviation charge bill.

Deliberations in the meeting:
A. CGM(O&M) stated that the proposals from CESU are yet to be received by O&M.
B. CESU may contact the Telecom wing to address the issues.
[Action: CGM (Telecom) / CGM (O&M) / CESU ]
SOUTHCO

A. RVDU found to be defective since 03.05.2016. Telecom authorities have already been intimated.

B. Revision of schedule for dated 29.04.2016 of Southco.
Deliberations in the meeting:
CGM (Telecom.) stated that Chemtrol has replaced the defective RVDU on 16.05.2016.
SLDC stated that the schedule cannot be revised on post facto.

[Action: Southco ]

WESCO

Revision of BST bill by deducting power import by solar projects.

Deliberations in the meeting:
Director (commercial) stated that WESCO may contact Gridco to resolve the issue
[Action: Gridco / Wesco ]

PART E: OPERATIONAL PLANNING

E.1:  Commissioning status of New Transmission elements. 
The status of commissioning of new transmission elements is as follows:
	   Sl. No
	    Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by December’ 2016.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal, which is under progress. ICT is at BHEL factory

	3
	Commissioning of 220 kV Bidanasi-Cuttack line
	Work in progress and expected to be completed by June’ 2016.

	4
	Commissioning of 220/132 kV Cuttack S/S
	Work in progress and expected to be completed by June’ 2016.

	5
	Commissioning of 132 kV Baripada (PG)-Jaleswar line
	Work has already been started, which will be completed by June 2016. 

	6
	Commissioning of 220/132 kV Kesinga S/S
	Work under progress. Expected by December’ 2016.


Status of Discom’s action plan for power drawal from the S/Ss commissioned / expected to be commissioned in near future. 
	   Sl. No
	    Name of the sub-station
	Probable month of commissioning
	Name of DISCOM
	Action taken by Discoms

	1
	132/33kV, 2x20 MVA  Khajuriakota 
	July’16
	CESU
	Action being taken

	2
	220/33kV, 2x20 MVA Banei 
	Dec’17
	WESCO Utility
	Stayed by Court.

	3
	132/33kV, 2x20 MVA  Udala 
	Dec-17
	NESCO Utility
	Line existing

	4
	132/33 kV, 1x12.5 MVA, Mania
	Charged
	CESU
	33 kV line not done by CESU


WESCO shall take action for diversion of 11 kV lines from Jharusuguda S/S.
Action: CGM (O&M)/ CGM (Const.) / All Discoms]
E.2: Energy Metering at Hydro stations.
Energy meters have already been installed at all hydro stations. Billing for all OHPC stations, except Upper Kolab, is being done from the newly installed energy meters. The energy meters at Upper Kolab are have been rectified in the mean time.

In the last meeting OHPC stated that Upper Kolab and Balimela PH meters are showing error. Mismatch noticed at both ends metering data of Burla-Chipilima Tie line. Rengali-TTPS feeder meter is not functioning. The meter data can be considered for billing purpose only after rectification of all defects. OHPC has already written to CGM (O&M) in this regard. It was decided that O&M shall take up the matter with the vender for rectification of energy meters.

In the 96th PSOC meeting, OHPC stated that energy meters at Kolab HEP have been rectified. The meter defects at Balimela, Burla and Chipilima have not yet resolved. O&M stated that the matter has already been taken up with the vender and rectification action is being taken.
Deliberations in the meeting:
OHPC stated that energy meters at Balimela, Upper Kolab, Burla & Chiplima HEP have been rectified. The meters at Rengali PH for TTPS feeder need to be replaced.

[Action: O&M / OHPC]   
E.3: TTPS Feeder metering.

Implementation of Feeder Metering
In the earlier PSOC meeting, TTPS deliberated that all the meters were tested & calibrated by the STL on 09.10.2015. The 132kV CTs for TTPS-Duburi-1 have been replaced. Further, as per the PPA dated 08.03.1995, the energy meters are to be installed at GT end. Since the meter locations will be shifted to feeders, the corresponding clause in the PPA is required to be amended. Accordingly, the proposal has been sent to the competent authority of NTPC for approval.
TTPS in their letter No.045/GGM/TTPS, Dated. 20.11.2015 addressed to CGM (PP) Gridco pointed out that, as per clause 7(1), 1st proviso of CEA (Installation and operation of Energy meters) Regulation, 2006 as amended in 2010 “ for existing stations the location of Main, Check and Standby meters shall not be changed unless permitted by the Authority”.

In the present case, for the first time, energy meters have been installed at the interface points, which should have been installed earlier, without changing the position of the existing meters. As such the regulation as mentioned by TTPS is not applicable. However the existing meters will be treated as standby meters.  

In the 96th PSOC meeting, DGM (O&M), Meramundali stated that installation of panel and meters is expected to be completed by end of April’16. As requested by TTPS, the on line data can be shared to them. Issue of on line time synchronization will be examined.
Deliberations in the meeting:
TTPS stated that installation of feeder meters shall be completed by end of May, 20156. CGM (O&M) stated that TTPS should extend co-operation to O&M for carrying out the installation work.
[Action: TTPS / O&M]
E.4: Major Events in the month of April’16

29.04.2016: 132 kV Atri – Argul DC line charged.
E.5: Important Grid Incidences during the month of April’16.
Important Grid incidents during the month of April’16 were reviewed. The incidents to be analyzed and deliberated in the PCC meeting of ERPC.
[Action: O&M / SLDC]
E.6: Outage of major transmission Elements during the month of April’16. (above 10 hrs).
Outage of major transmission elements above 10 hours during the month of April’16 was reviewed. Most of the outages are for jumper snapping & CT/PT bursting.
[Action: O&M]
E.7:  Review of Outage Program of State Generators / Transmission elements for the month of June’16:
Tentative Outage programme for State Generators for the month of June’2016 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 6
	17.02.14 to continue
	Programming for R, M & U

	2
	Chiplima
	# 3
# 1

# 2
	15.02.14 to continue
16.05.16 to 15.06.16

16.05.16 to 15.06.16
	Programming for R, M &U 
Power Chanel maintenance

-do-

	3
	Balimela
	# 1
	31.01.13 to continue
	TGB problem and started R,M & U

	4
	Upper Kolab
	# 1
	29.07.15 to 25.06.16
	Capital Maintenance

	6
	Upper Indravati
	# 3
	23.11.15 to 30.06.16
	Capital Maintenance

	7
	OPGC
	# 2
	07.05.16 to 28.05.16
	Annual Maintenance & boiler license renewal


Deliberations in the meeting:
SLDC stated that TTPS may defer its shutdown program to the month of July16.
E.8: Generation Program for the month of June’16.
Generation schedule for the month of June’16 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Programme (MW)
	Reservoir Level as on 01.05.15
	Reservoir Level as on 01.05.16
	MDDL
	High Flood    Reservoir Level

	
	June’16

(1st fortnight)
	June’16

(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	25
	30
	608.83ft 
	609.54ft
	590 ft.
	630 ft.

	HPS-II, Chipilima
	0
	20
	-
	-
	-
	-

	Balimela
	185
	185
	1489.70ft 
	1477.00ft
	1440 ft.
	1516 ft.

	Rengali
	50
	50
	119.47mt

1.78mt mtr mt
	114.24mt mt
	109.72mtr 
	123.5 mtr.

	U.Kolab
	90
	90
	852.66mt mt
	849.56mt
	844 mtr 
	858 mtr.

	U. Indravati
	155
	155
	634.62mt
	631.76mt mt
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2724.20ft 
	2721.10ft
	2685 ft.
	2750 ft.

	TOTAL
	535
	560
	
	
	
	


Action: [OHPC/ SLDC]
E.9: Anticipated power generation and demand for the month of June’2016.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1000
	1350

	2
	WESCO
	960
	1200

	3
	NESCO
	800
	1000

	4
	SOUTHCO
	400
	550

	5
	OPEN ACCESS
	200
	200

	6
	Total
	3360
	4300

	Availability
	
	

	1
	Hydro
	450
	970

	2
	State Thermal
	780
	780

	3
	IPP, small hydro &RE
	850
	800

	4
	ISGS share (including OA)
	1000
	1100

	5
	CGP support (OA)
	150
	150

	6
	Banking
	160
	500

	7
	Total availability
	3390
	4300

	8
	Surplus / Deficit
	0
	0


PART F: OTHER ISSUES

F.1:  Recording provision in Video Conferencing
SLDC stated that there is no recording provision in the Video conferencing installed at SLDC. CGM (Telecom) stated that SLDC may place requisition for providing such facility.

Action: [Telecom./ SLDC]
F.2:  Date and Venue of the next (98th) PSOC meeting
It was decided that the 98th PSOC meeting will be held at Chandipur (Balasore) under the aegis of NESCO Utility. NESCO Utility was requested to confirm the same through a letter to CLD, SLDC.
Annexure
List of participants in the 97th PSOC meeting dated 17.05.2016

[image: image2.png]97th Power System Operational Co-ordination Review Meeting
[ At 11:00 A.M. on 17.05.2016]
[At Power Training Center, OPTCL, Chandaka, Bhubaneswar]

S I o e T 7y ey
| .
e W
o ot e | [ [proT et WL
7
2

|

/
I7 MG s D S e g Loy [
0 5O e (O A g
NPT PN P Yy Srem iy
i e
srter (11500750t €0
(1T TS s oy a7
7. belo
I S P T A TR o Sy
|

k

4
YV

,
| p c, <5





[image: image3.png]Sworendrae mallim

Pnesco Ool'sa,

3 I

E

L)
N

&

<=
H
e

o

<

9

> |
&

EN

®

<

v |
a A
[0
8!

o
AN
Pl
E Be \ "

it-dthandh @

S K Bebern pv (3T) | IT Dept. ity SrbeherQREE . A
9435907240
9432907410
st )
P Bt

DamliD |17 Beptt] Q438907240 |- prafrn@ phelee
pem L ?43890‘7‘”*'0 '
p.k. Mirhye .ct;m"( 91890 )7 —
2 | L
e P
T
Mm A phoma Sahoo SLDC. MW_M@Y,:W L4
Quo ey 2 fretieebn ) 4y | 3o

Ny,

4

3

‘&

A

E

1,

fﬂ





