                                                                                                                  
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image1.png]PTC




Agenda

for

115th Power System Operational Coordination Meeting

Date: 24.11.2017
Venue: CPTI, RSP, Rourkela 
Programme details

	10:00
	10:30
	Arrival at Meeting venue – CPTI, RSP

	10:30
	10:35
	Welcome address by GM (Electrical)

	10:35
	10:40
	Address by Director, Commercial, GRIDCO

	10:45
	11:00
	Tea Break

	11:00
	14:00
	Discussion of Agenda items

	14:00
	14:05
	Vote of thanks by G.M (Grid Operation), SLDC

	14:05
	14:30
	Lunch

	14:30
	
	Departure from Venue


Venue:
  Central Power Training Institute (CPTI), RSP, Rourkela


   (Inside Project Complex, RSP)
Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 115th PSOC Meeting to be held on 24.11.2017 at RSP, Rourkela
Item no. 1: Confirmation of the minutes of the 114th PSOC Meeting held on 27.10.2017
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2016/3785(46) dated 03.11.2017 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members. Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   : Grid Performance for the month of October’2017
C.1: Status of projects funded under PSDF scheme

C.2: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s
C.3: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

C.4: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.
C.5: Replacement of old RTU in Eastern Region for reporting of RTU / SAS to back-up control centre
C.6: Implementation of Automatic Demand Management Scheme
C.7: Pollution mapping for Eastern Region

C.8: Mock Black start exercise in Eastern Region 
D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Prolonged outage of transmission elements and tentative revival dates
D.3: Communication issues 
D.4: Web based drawal / generation scheduling.

D.5: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.6: Software for Deviation charge billing.
D.7: DISCOM Issues 
E.1: Commissioning status of New Transmission elements. 

E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
E.3: Declaration of standby energy meter
E.4: Replacement of defective meters at renewable sources.
E.5: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
E.6: Major Events in the month of October’17

E.7: Important grid incidences during the month of October’17.
E.8: Outage of major transmission Elements during the month October’17. (above 10 hrs).
E.9: Review of Outage Program of State Generators for the month of December’2017
E.10: Generation Program for the month of December’2017.
E.11: Anticipated power generation and demand for the month of December’2017.
F.1:  Installation of OPGW in 400kV Indravati (PG)- Indravati (OHPC)
F.1:  Date and Venue of the next (116th) PSOC meeting
PART B: GRID PERFORMANCE
Review of Grid Performance for the month of October’17.
(A) Frequency:

Hourly frequency variation for the month of October’17.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	Aug’17
	0.00
	0.01
	5.58
	70.68
	23.73
	49.98

	Sept’17
	0.00
	0.03
	10.01
	77.41
	12.56
	49.96

	Oct’17
	0.00
	0.02
	10.69
	76.19
	13.10
	49.98


 
Maximum & Minimum frequency during the month of October’17.
	Month
	Freq (Hz)
	Date
	Time

	Sept’17
	Maximum – 50.17
	17.09.17
	06:00 Hrs

	
	Minimum – 49.72
	23.09.17
	18:15 Hrs

	Oct’17
	Maximum – 50.10
	19.10.17
	18:30 Hrs

	
	Minimum – 49.76
	03.10.17
	22:00 Hrs


Members may please discuss.

(B) Grid Demand up to the month of October’17

	 Month
	Maximum Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	April’17
	88.91
	27.04.17
	2493
	3463
	4299
	26.04.17
	24:00
	2466
	03.04.17
	07:00

	May’17
	88.13
	23.05.17
	2534
	3406
	4281
	04.05.17
	24:00
	2553
	06.05.17
	23:00

	June’17
	82.72
	03.06.17
	2269
	3151
	4009
	04.06.17
	24:00
	2091
	15.06.17
	18:00

	July’17
	86.54
	06.07.17
	2437
	3276
	4233
	05.07.17
	20:00
	2596
	23.07.17
	14:00

	Aug’17
	85.74
	26.08.17
	2500
	3360
	4269
	26.08.17
	24:00
	2647
	17.08.17
	16:00

	Sept’17
	93.49
	16.09.17
	2566
	3567
	4375
	26.09.17
	21:00
	2523
	12.09.17
	17:00

	Oct’17
	91.78
	13.10.17
	2655
	3569
	4491
	23.10.17
	20:00
	2763
	20.10.17
	06:00

	Oct’16
	78.31
	04.10.16
	2252
	3026
	3995
	04.10.16
	21:00
	2319
	26.10.16
	15:00


(C) Voltage Profile of 220 kV Buses in OPTCL system for the month of: October’17
	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Balasore
	236.94
	20
	08:00
	219.56
	14
	18:45

	2
	Barkote
	235.55
	02
	14:00
	228.22
	14
	19:00

	3
	Bhadrak
	238.79
	20
	07:45
	216.56
	17
	22:30

	4
	Bhanjanagar
	239.48
	06
	17:00
	223.72
	21
	18:00

	5
	Bidanasi
	236.59
	09
	16:30
	217.14
	23
	18:15

	6
	Bolangir
	228.05
	08
	11:45
	215.86
	29
	18:00

	7
	Budhipadar
	230.47
	01
	14:30
	222.68
	21
	18:45

	8
	Chandaka
	233.70
	20
	01:30
	217.65
	21
	18:00

	9
	Duburi(O)
	238.96
	20
	07:45
	225.97
	14
	18:45

	10
	Duburi (N)
	228.05
	20
	07:45
	215.63
	14
	18:45

	11
	Jayanagar
	240.00
	20
	01:30
	223.83
	26
	17:15

	12
	Joda
	240.06
	20
	06:15
	217.60
	08
	12:00

	13
	Katapalli
	229.32
	02
	14:00
	221.58
	13
	16:45

	14
	Laxmipur
	239.71
	01
	01:30
	223.31
	26
	17:00

	15
	Mendhasal
	235.55
	20
	01:30
	218.98
	21
	18:00

	16
	Meramundali
	231.28
	21
	02:30
	223.66
	14
	18:40

	17
	Narendrapur
	233.99
	06
	13:30
	211.88
	21
	18:00

	18
	Nayagarh
	235.49
	06
	17:00
	219.16
	21
	18:00

	19
	Paradeep
	237.57
	20
	08:00
	213.21
	25
	17:45

	20
	Tarkera
	236.07
	02
	14:00
	217.14
	12
	11:30

	21
	Theruvali
	237.23
	14
	10:00
	213.90
	26
	17:15


The maximum Voltage of 240.00 kV & 240.06 kV occurred at Jayanagar &Joda 220 kV bus respectively, while Narendrapur 220 kV bus has experienced the minimum Voltage of 211.88 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Meramundali bus during the month of October 2017 is shown.
[image: image2.emf]200

205

210

215

220

225

230

235

240

245

250

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF JAYANAGAR 220 kV BUS

For OCTOBER 2017


[image: image3.emf]200

205

210

215

220

225

230

235

240

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFIL OF NARENDRAPUR 220 kV BUS

FOR OCTOBER 2017


[image: image4.emf]405

406

407

408

409

410

411

412

413

414

415

416

417

418

419

420

421

422

423

424

425

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MERAMUNDALI 400 KV BUS

FOR OCTOBER 2017


Members may discuss.
(D) Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of Oct-17
[image: image5.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  OCTOBER'2017

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

121.24 1 10:00 12.80 11 12:00

136.48 3 12:45 13.00 11 12:00

1x100 58.52 19 10:30 10.48 3 8:15

1x160 91.52 23 17:45 11.76 11 8:30

OUT OF SERVICE

1x160 85.92 26 8:15 21.12 5 17:00

1x160 75.92 26 8:15 18.36 5 17:00

1x160 NOT AVAILABLE

1x100 32.12 11 11:30 7.96 17 7:15

1x100 32.08 11 11:00 7.96 17 7:15

2x160 128.08 23.00 18:30 37.56 16 12:00

135.40 23.00 18:30 39.60 16 12:00

79.88 31 20:30 28.36 2 13:45

79.48 31 20:30 24.68 1 9:15

1x100 63.40 27 18:15 14.92 15 9:00

1x160 116.16 15 14:45 38.60 20 2:15

1x100 72.28 15 14:45 31.60 1 6:15

1x160 97.28 13 11:30 36.84 20 20:30

UNDER SHUT DOWN

60.72 14 15:15 9.44 21 10:30

57.88 14 21:15 9.08 21 2:45

1x160 61.84 26 13:30 13.24 21 15:45

1x160 61.72 26 13:30 13.24 21 15:45

METER NOT INSTALLED

METER NOT INSTALLED

METER NOT INSTALLED

1x100 26.40 12 10:30 8.36 1 18:45

1x100 26.68 12 10:30 8.64 1 18:45

1x160 METER NOT INSTALLED

1x160 27.40 27 6:00

26.80 27 5:45

50.52 24 17:45 14.12 21 2:30

49.56 24 17:45 13.92 21 2:30

48.84 24 18:00 14.84 21 2:30

Mendhasal                                           

 { Part 

area load of Khurda S/S}

1x100 40.80 2.00 4:00 11.40 8.00 12:00

2x160 126.24 23 17:15 47.24 26 14:00

116.72 30 18:15 24.00 20 23:45

1x100 72.88 23 17:15 28.52 6 13:30

1x160 109.64 7 19:00 8.40 11 8:30

1x100 77.96 11 9:30 11.40 20 10:15

1x50 METER NOT AVAILABLE

4x100  64.60 26 18:00 13.08 13 11:15

66.20 26 18:00 14.12 5 15:30

64.88 26 18:00 13.40 5 15:30

52.52 21 19:00 12.36 24 15:30

2x100 86.52 18 16:45 12.92 4 12:00

81.08 18 16:45 13.28 1 11:30

1x160  58.00 11 13:00 0.00 21 13:00

1x160 58.00 11 13:00 0.00 21 13:00

2x160

1x100

CUTTACK 1x160

3x100 

TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 



MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100

BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

2x160 



BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), MCL, 

Sundergarh,Brajarajnagar, Rajgangpur}

2x160 



BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

BHADRAK 220/132 KV

{Bhadrak area load, Bhadrak(T),Soro,  

FACOR (I), Dhamra Port}

LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 



"*" - Alternate P/S from Kuchei.



KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & Katapali 

area load.}



DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, Jajpur 

Road, Kalarangi, Jajpur Town}



SAMANGARA                                          

{ 

Puri, Nimapara & Konark}

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, Digapahandi, 

Mohana.}

THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

Rayagada & Paralakhemundi 

can be fed from Machhkund 

system.

ATRI                                                    

 {

Banki, 

Khurda, Chandpur & Argul}

Supported by Burla & Chipilima 

power.

JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

Drawal details

Maximum Minimum

JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]



3x100  Auto-II under shutdown.

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}

CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }

BIDANASI 220/132 KV

{Bidanasi, Khurda }


Energy meter at Mendhasal Auto has been installed. Installation of meters in other Autos is under process. 
CGM (O&M) may please deliberate the status.
(E) DISCOM Drawal up to the month of October’17
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	April’17
	727.397
	760.945
	789.421
	17.199
	772.222
	11.277

	
	May’17
	751.644
	839.125
	871.775
	20.892
	850.883
	11.758

	
	June’17
	727.397
	750.856
	775.766
	20.502
	755.264
	4.408

	
	July’17
	751.644
	726.897
	761.921
	20.064
	741.857
	14.96

	
	Aug’17
	751.644
	765.985
	793.287
	17.844
	775.443
	9.458

	
	Sept’17
	727.397
	730.617
	768.066
	17.257
	750.809
	20.192

	
	Oct’17
	751.644
	734.68
	758.405
	15.23
	743.175
	8.495

	WESCO
	April’17
	582.74
	637.3
	689.833
	54.234
	635.599
	-1.701

	
	May’17
	602.164
	626.029
	673.256
	38.953
	634.303
	8.274

	
	June’17
	582.74
	557.308
	595.666
	41.282
	554.384
	-2.924

	
	July’17
	602.164
	577.765
	731.982
	154.21
	577.772
	0.007

	
	Aug’17
	602.164
	622.033
	687.379
	70.539
	616.84
	-5.193

	
	Sept’17
	582.74
	628.342
	841.153
	202.065
	639.088
	10.746

	
	Oct’17
	602.164
	639.382
	918.578
	284.197
	634.381
	-5.001

	NESCO
	April’17
	466.849
	493.551
	597.753
	108.907
	488.846
	-4.705

	
	May’17
	482.411
	468.854
	578.963
	114.176
	464.787
	-4.067

	
	June’17
	466.849
	432.223
	548.642
	109.141
	439.501
	7.278

	
	July’17
	482.411
	446.662
	556.119
	102.767
	453.352
	6.69

	
	Aug’17
	482.411
	494.041
	595.207
	100.708
	494.499
	0.458

	
	Sept’17
	466.849
	475.21
	589.343
	103.64
	485.703
	10.493

	
	Oct’17
	482.411
	458.363
	575.413
	93.521
	481.892
	23.529

	SOUTHCO
	April’17
	289.315
	303.102
	305.398
	0.651
	304.747
	1.645

	
	May’17
	298.959
	308.789
	314.808
	0.213
	314.595
	5.806

	
	June’17
	289.315
	279.684
	276.185
	0.433
	275.752
	-3.932

	
	July’17
	298.959
	294.376
	294.742
	0.629
	294.113
	-0.263

	
	Aug’17
	298.959
	310.404
	307.768
	0.391
	307.377
	-3.027

	
	Sept’17
	289.315
	294.522
	292.885
	0.074
	292.811
	-1.711

	
	Oct’17
	298.959
	290.344
	292.58
	0.052
	292.528
	2.184


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
Members may please discuss.

(F) Energy Generation / Import up to the month of October’17 
Figures in MU  
	Month
	Thermal (TTPS+IB)
	OHPC

& MKD
	CGP Support
	IPP Support
	Renewable
	ISGS
	Total

	Apr’17
	514.91
	581.71
	323.53
	349.53
	17.70
	705.86
	2493.24

	May’17
	543.19
	647.85
	296.06
	212.84
	10.45
	823.85
	2534.95

	June’17
	548.07
	610.00
	358.88
	203.70
	10.17
	537.95
	2268.75

	July’17
	554.18
	688.13
	190.09
	140.71
	10.46
	853.89
	2437.46

	Aug’17
	442.30
	746.49
	281.20
	167.14
	10.06
	853.01
	2500.20

	Sept’17
	363.01
	731.72
	189.82
	173.94
	9.45
	1091.74
	2565.69

	Oct’17
	453.38
	572.67
	155.32
	152.27
	35.85
	1311.67
	2655.33

	Total
	3419.04
	4578.57
	1794.9
	1400.13
	104.14
	6177.97
	17455.6


(G)  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of October’17 are as detailed:
	Month
	Total Generation
	Odisha Drawal
	AP Drawal 

	
	MU
	MW
	MU
	MW
	MU
	MW

	April’17
	65.960
	91.61
	32.320
	44.88
	30.950
	42.98

	May’17
	65.532
	88.08
	29.078
	39.08
	33.832
	45.47

	June’17
	45.678
	63.44
	19.509
	27.10
	24.105
	33.48

	July’17
	33.211
	44.63
	15.056
	20.24
	16.232
	21.81

	Aug’17
	51.798
	69.62
	24.448
	32.86
	25.220
	33.90

	Sept’17
	39.018
	54.19
	18.135
	25.18
	19.070
	26.49

	Oct’17
	34.353
	46.17
	16.510
	22.19
	16.164
	21.72

	TOTAL
	345.550
	
	155.056
	
	165.573
	


In the 114th PSOC meeting it was deliberated that 132/ 33 kV Podagada sub-station is going to be commissioned soon after which matching load on Machhakund system is likely to be increased by 2 – 3 MW.
CGM (Const) may update the progress

(H) Under Frequency Relay operation in OPTCL System during the month of October’17.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of October’17.
(I) Status of Open Access applications up to the month of October’2017
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’17
	21
	71
	0
	29
	121
	20
	71
	0
	28
	119
	2

	2
	May’17
	12
	31
	0
	32
	75
	12
	29
	0
	25
	66
	9

	3
	June’17
	23
	56
	0
	58
	137
	23
	56
	0
	40
	119
	18

	4
	July’17
	20
	85
	0
	36
	141
	20
	85
	0
	26
	131
	10

	5
	Aug’17
	9
	113
	0
	37
	159
	7
	110
	0
	31
	148
	11

	6
	Sept’17
	17
	140
	0
	52
	209
	15
	140
	0
	41
	196
	13

	7
	Octo’17
	17
	112
	0
	35
	164
	16
	112
	0
	31
	159
	5

	
	Total
	119
	608
	0
	279
	1006
	113
	603
	0
	222
	938
	68


PART C – Issues likely to be discussed in the 139th OCC meeting of ERPC on 27.11.2017
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting held on 29.04.16 at New Delhi, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format. 
The latest status as updated by OPTCL is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	Amount

Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	3
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	10.05.15
	10.05.17
	162.5 Cr.


	25.16 Cr.
	Total contract awarded for

Rs. 51.35 Cr




In the 113th PSOC meeting CGM (O&M) stated that that the DPR for installation of reactor has been sent to NLDC for PSDF funding as per the suggestion given by ERLDC during a joint study. CPC has been requested to take necessary action for tendering the 400 kV Bus reactor to be installed at Meramundali S/S.
In the 114th PSOC meeting CGM (O&M) stated that the automation of 7 nos of 220kV sub-stations needs to be incorporated for PSDF funding. A proposal in this regard is under process to be placed before BoD for approval. 

CGM (O&M) may please update.
C.2: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s

PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.

In 138th OCC of ERPC, SLDC to deliberate the completion schedule of inter-connecting system as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir S/S.
	Construction of 220 kV Sadeipali-Kesinga portion has started. Expected by March’18

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Line is expected by Dec’2017

Keonjhar(220/33 kV) by Dec’17

	b.
	Keonjhar (PG)-Turumunga (220/133 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	March 2018 

	b.


	LILO of one circuit of Atri-Puri (Samangara) 220 kV D/C line at Pandiabil (PG). 
	Atri – Pandibili 220 kV one ckt charged on 19.05.2017

Pandiabili – Samangara 220 kV one ckt. charged on 20.05.17


In the 113th PSOC meeting AGM (Construction) stated that 2nd ckt of 220 kV Atri-Samangara line will be made LILO at Pandiabili. CGM (Telecom) stated that tender for installation of RTU at Samangara S/S will be opened on 20.09.2017. Installation is expected to be completed by 30.09.2017.

In the 114th PSOC meeting Telecom stated that installation of RTU at Samangara S/S is under progress & shall be completed by 31st October 2017.
CGM (Const.) / CGM (Telecom.) may please deliberate.
C.3: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In the 107th PSOC meeting, CGM (IT) informed that “Crisis management plan” work is awarded to M/s Digital Age Strategies Pvt. Ltd. The said firm has completed the study of Servers and Firewalls at SLDC, Bhubaneswar and back-up SLDC at Meramundali. Presently the data centers of SLDC and GRIDCO are being audited for IT security vulnerability assessment.

SLDC is requested to nominate one officer for attending the Cyber Security training to be held at Bengaluru during 11th to 15th April’2017. Nominations from GRIDCO and OPTCL have since been received. Top management awareness-cum Seminar on the subject shall be organized subsequently.

In the 110th PSOC meeting, IT stated that the meeting was held on 23.06.2017. SLDC shall comply with the action to be taken relating to SCADA.

In the 111th PSOC meeting DGM (Telecom) stated that the compliance of action to be taken on SCADA related issues is under process.
In the 113th PSOC meeting CGM (Telecom) stated that after testing of dual reporting of RTU and back up control center and compliance of audit report, Telecom will process for tendering. 

In the 114th PSOC meeting it is suggested that Telecom. may forward the report to IT wing soon as the issue has been much delayed.  
CGM (IT) / Telecom may please deliberate.
C.4: Certification through BIS as per IS 18001:2007 to all generating / transmission units.
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In the 110th PSOC meeting CGM (O&M) stated that BIS office at Bhubaneswar was contacted in this regard. It was decided that OPTCL shall nominate its officers to take training. After completion of training they will conduct audit and certify.
In the 111th PSOC meeting CGM (O&M) stated that 22 nos of officers are nominated from Chandaka, Mendhasal, Atri, Kesura, Bidanasi & Cuttack S/Ss to undergo training. Awareness training shall be started from 1st week of August’17. After receiving the price offer, order will be placed. 

In the 113th PSOC meeting CGM (O&M) stated that certification for 6 Nos of S/Ss will be done by December’2017.
In the 114th PSOC meeting CGM (O&M) stated that training has already been imparted to OPTCL officers.

CGM (O&M) may please update the status.
C.5: Replacement of old RTU in Eastern Region for reporting of RTU / SAS to back-up control centre
The matter for replacement of old RTU in Eastern Region for reporting to back up control centre has been discussed in a special project review meeting held on 14th February 2017 at ERPC & also on 35th TCC/ERPC meeting held on 24th / 25th February 2017, It was also mentioned that there would not be any service support for the old RTUs from POWERGRID after 15 years of operation period. It was accordingly advised to ERLDC to form a committee with POWERGRID as a nodal agency for assessment of such old RTUs vis-a-vis further action plan on replacement.

It was also advised to submit a report in the next TCC/ERPC meeting.

The matter for replacement of old RTU in Eastern Region for reporting to back up control centre has been discussed again in 19th SCADA O&M meeting held at ERLDC, Kolkata on 07th April 2017, wherein nomination of nodal person name from OPTCL, WBSETCL, DVC, BSPTCL, JUSNL, POWERGRID ERTS-1, POWERGRID ERTS-2, ERLDC, MPL & Jorethang has been collected.

Nomination from NTPC all stations including Nabinagar, NHPC all stations, Dikchu, Teesta-III, Chuzachen, JITPL, GMR, Ind Bharat & APNRL are yet to be provided. ERLDC has already issued letter ref no: ERLDC / SCADA O&M / 2017/ dated 11.04.2017 for the same. It is requested to provide the nomination from these stations.
In the 112th PSOC meeting CGM (Telecom) stated that RTU specification has been finalized on 7th August’17. Tendering will be done after approval of CMD, OPTCL.

In the 114th PSOC meeting Telecom. stated that requirement of RTUs shall be reduced in view of the proposal for automation of 24 nos of sub-stations. The revised proposal for RTU procurement will be placed in the BoD. Tendering will be done after finalization of the proposal. 

CGM (O&M) / CGM (Telecom) may please deliberate.
C.6: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************
The DPR for ADMS has already been approved by BoD, OPTCL. SLDC shall submit the proposal for funding by PSDF for ADMS to O&M wing of OPTCL for further action.
In the 108th PSOC meeting, SLDC stated that filling of format for PSDF and floating of tender is under process. The DPR will be sent to ERPC. CGM (Telecom) stated that SLDC may contact the consultant of PSDF for filling the format. The proposal has already been sent to NLDC to include for funding through PSDF.
In the 113th PSOC meeting SLDC stated that CPC has been requested to prepare the “Expression of Interest” before processing the tender.
In the 114th PSOC meeting SLDC stated that the EoI document is yet to be prepared by CPC. It is decided that SLDC may persue the matter with CPC.

SLDC may please deliberate.
C.7: Pollution mapping for Eastern Region
Powergrid updated the latest status as follows: 

	
	No of locations
	Installed locations
	1st set of measurements
	2nd set of measurements
	3rd set of measurements
	4th set of measurements
	5th set of measurements

	OPTCL
	164
	102
	100
	90
	79
	78
	24


Powergrid added that they prepared an online format to submit the details of measurements.

Powergrid requested to fill the Google form (https://goo.gl/6375HJ) for onward submission of measurements for better analysis of results.

Further, the schedule for measurement as informed vide letter dated 20.01.2016 & mail dated 21.01.2016 are as follows:

Measurement Schedule

	4th set
	5th set
	6th set

	21st -30th Sep 2016
	21st -31st Jan 2017
	21st -31st May 2017


OCC advised all the constituents to complete the measurements as per the schedule.

It is also requested to send the onward measurement results to following emails in addition to current email ids

1. vbhaskar@powergridindia.com

2. ritesh.kumar@powergridindia.com

In the 114th PSOC meeting O&M stated that measurement shall be done after rainy season.
O&M stated that SLDC may deliberate in the OCC meeting of ERPC for up-dating the status of completion in the 5th set of measurements as 90 in place of 24.

CGM (O&M) may please deliberate.
C.8: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2017-18 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2017
	Conducted on 30th May 2017
	Last week of January 2018
	

	3
	Rengali
	2nd week of June 2017
	Conducted on 29.06.17
	Last week of November 2017
	

	4
	U. Indravati
	3rd week of June 2017
	2nd week of July-2017
	2nd week of February 2018
	

	6
	Balimela
	3rd week of October  2017
	
	1st week of March 2018
	

	9
	Burla
	Last week of June 2017
	Can be conducted after synchronization of #2
	Last week of February 2018
	


In the 114th PSOC meeting it was decided to conduct the black start exercise for Balimela & UIHEP during second week of November’17 and for Burla HEP during the month of December 2017.

OHPC / SLDC may please deliberate.
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of Oct’17:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	8.495
	1.156

	2
	WESCO
	2
	-5.001
	0.782

	3
	NESCO
	0
	23.529
	5.133

	4
	SOUTHCO
	0
	2.184
	0.752

	
	Total
	2
	29.207
	


It is noticed that CESU had overdrawn during the month.
SLDC/ Discoms may please deliberate.
D.2: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl. No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220/132 kV, 100 MVA, Auto- 1 at Duburi
	Main tank severely damaged
	March-2018

	2
	220/132kV, 100MVA  Auto-2  at Bhadrak
	Fire hazard on 31.05.2017
	March-2018


CGM (O&M) may update the progress.

D.3: Communication issues 
The status of data communication from CGPs as deliberated in the last meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s IFFCO, Paradeep
	Outdoor commissioning work completed. RTU was locally tested. CVT already replaced. Data will be integrated after restoration of OPGW between New Duburi & Paradeep.

	2
	M/s MSP Mettalicks
	PLCC / RTU installed. Database has already been prepared by OPTCL. Final RTU integration with OPTCL system by the vendor is awaited.

	3
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	4
	M/s Rohit Ferrotech
	PLCC established and inspection by Telecom Engineers completed.  Database has already been prepared by OPTCL.    

	5
	CONCAST
	No kV/Hz. (Industry is under lock up)

	6
	VISA
	CB & Status data are not available

	7
	Paradeep
	Data not available at ERLDC (Transducers need replacement)

	8
	Vedanta (400kV) 
	Frequent interruption of Line data & Generation data 

	9
	GMR
	GMR line data not available as reported by ERLDC.

	10
	Samangar & Lapanga
	No data available as reported by ERLDC

	11
	NALCO
	No data available since 14.07.17. NALCO is not responding


In the 113th PSOC meeting GCC was requested to examine for filing a case before the OERC against the CGP / Industry, those who failed to comply establishment of communication facility as the matter has been delayed considerably. 
In the 19th SCADA O&M meeting of ER held at ERLDC, Kolkata on 07th April 2017 ERLDC informed that scheduling of GMR is being done at ERLDC so data must be reported to ERLDC directly from GMR. ERLDC requested OPTCL to take up the matter with GMR so that data & voice should be available directly to ERLDC. OPTCL agreed for the same.
In the 114th PSOC meeting GMR agreed to lay OPGW for data communication to ERLDC directly. GCC stated that case will be filed against the defaulting CGP / Industry within a week.

GCC has requested CGM(Telecom) to furnish the updated status of the defaulting CGP / Industry to file a case before OERC.
CGM (Telecom) / GCC / GMR / RT&C may deliberate the status.
D.4: Web based drawal / generation scheduling.

In the 111th PSOC meeting it was decided that from 1st August 2017 the schedule submitted through web portal will be considered. The web based schedule will be implemented for TTPS and Ib TPS from 1st September’2017. 
At present all State thermal generating stations including IPPs & CGPs are furnishing their schedule through web portal except IbTPS. Provisions for acceptance of backing down schedule for past block are not kept in the software. IT has already been intimated about this issue. Provision for automatic extraction of Power Exchange schedule for incorporation in the schedule of respective Generator / CGP may be kept in the software.
In the 114th PSOC meeting IbTPS has agreed to depute their representatives to SLDC for interaction regarding scheduling through web portal. DGM (IT) has assured to resolve the issues identified by SLDC.
SLDC / IT / OPGC may update 
D.5: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

The work for Automatic Meter Reading (AMR) for all the interface points is in progress. 

It was deliberated that from 1st March onwards the AMR shall be made “Go live”. Data will be available after one hour lapses of time.

In the 112th PSOC meeting DGM (IT) stated that TCS has complied with the discrepancies in August data. 679 Nos meter data have been collected during this month. Further, 750 Nos meter data will be available by next month. It was also decided that on 1st day of the month, SLDC will download the meter data and TCS will collect data on 2nd day and complete by evening of the day. On the 3rd day, SLDC and TCS will analyze the mismatch of data, if any. Further, a meeting may be convened by GRIDCO with all the DISCOMs to discuss acceptance of meter data through Text file.
In the 113th PSOC meeting IT stated that data from 690 Nos of meters have received during last month. It was decided that the data received by 2nd working day of the month shall be considered as final. It was further decided that the script shall be stopped on the 1st working day to enable for meter data collection by SLDC. 
In the 114th PSOC meeting IT stated that data from 640 no of sub-stations have been received on 2nd day of October. On 4th day data from some sub-stations was received. Data from remote sub-stations could not be collected due to communication network problem. Further, he stated that data from such sub-stations has to be collected manually each month. TCS has agreed to incorporate the billing software of secure meter. SLDC suggested to provide the AMR data to DISCOMs for monitoring of their real time drawal may be after lapses of 15 to 30 minutes time.
SLDC / IT may update the status.
D.6: Software for Deviation charge billing.

Hon’ble OERC may notify “Intra State Deviation settlement and related matters” Regulation at any time. For implementation of the regulation, required software for Deviation Charge billing need to be developed and tested. CGM (IT) may take necessary steps for development of the software.

As decided a committee has been constituted for development of the software in house. The work is in progress. 
In the 114th PSOC meeting, IT stated that the software will be completed by end of November 2017.

CGM (IT) / SLDC may please deliberate.
D.7.DISCOM Issues

CESU

1. Wide mismatch of drawal display through SCADA with actual meter data to the tune of 259MW on one side and 71MW on the other side. 
2. Necessary action may please be taken to reduce the gap between SLDC dash board drawal data and actual (dump) drawal data of CESU on every 15minute block basis to enable CESU to give more accurate day ahead schedule forecast.
. 
 NESCO Utility
It is ascertained from the meter data for the month of October’17 that there is a wide variation between RVDU drawal data and actual drawal data. The drawal in RVDU is showing less in comparison to actual drawal resulting more deviation. NESCO is unable to calculate the actual deviation due to abnormal low recording in the RVDU. Therefore, NESCO requests to waive out the deviation for the month of October’17. The detail calculation sheet of Schedule Vs RVDU Drawal Vs Actual Drawal is enclosed for your kind ready reference.

WESCO Utility
1. The power import by GEDCOL Solar is not being deducted from WESCO energy drawal since April’2016

2. CESU has not made claim for the energy exported by CESU to WESCO control area for the month of November’2017. 

3. Power restriction to Industrial area may be avoided as WESCO is losing reliability surcharge. 
SOUTHCO Utility

1. Deduction of the station transformer loss from SOUTHCO drawal for energy accounting & replacement of defective meters used for station consumption at OPTCL Grid sub stations.

2. Deduction of energy export to WESCO through Mukhiguda feeder from Tentulikhunti Grid substation and to Mega lift project of WESCO from Kantamala 33 / 11kV substation from SOUTHCO drawal.

3. Providing adopted CT / PT ratio for all interface metering points of SOUTHCO.

4. Provision for indicating the status of transmission elements of OPTCL system in the RVDU.
CESU / NESCO / WESCO / GRIDCO/  SLDC / (Telecom) may deliberate.
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by December’ 2017.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by December’2017.

	3
	Commissioning of 132 kV Baripada (PG)-Jaleswar D/C line (One ckt. made LILO at Bhograi)
	Line idle charge on 29.07.17 from Jaleswar & Bhograi end. 

	4
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	December’17

	5
	400/220 kV, 2x315 MVA Lapanga S/S
	March’18

	6
	220/33 kV, 2x20 MVA Baliguda S/S
	Mar-18

	7
	220/33 kV, 2x20 MVA Kalimela S/S
	June-18

	8
	220/33 kV, 2x20 MVA Kasipur S/S
	June-18

	9
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	Dec’17

	10
	220/33 kV, 2x20 MVA Narasinghpur S/S
	February’18

	11
	220/132 /33 kV, 2x100 MVA Aska S/S
	June’18

	12
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	Nov’17

	13
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	June’18

	14
	220/132/33 kV Jayapatana S/S(320 MVA)
	Jun’18

	15
	220/132 kV Pratapassan S/S(320 MVA)
	March’18

	16
	220/132 kV Kesinga S/S (320 MVA)
	March’18

	17
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	March’18

	18
	400 KV Restoration of IB - Lapanga line D/C
	September’17

	19
	132/33 kV Ghense S/S
	December’17

	20
	132/33 kV Dhenkikote S/S 
	December’17

	21
	132/33 kV Betanati S/S
	March’18

	22
	132/33 kV Kantabanji S/S
	November’17 (Line charged)

	23
	132/33 kV Podagada S/S
	November’17

	24
	132/33 kV Muniguda S/S
	November’17

	25
	132/33 kV R.Udyagiri S/S
	March’18

	26
	132/33 kV Chikiti S/S
	March’18

	27
	132/33 kV Athagarh S/S
	December’17

	28
	132/33 kV Tirtol S/S
	December’17 (Bus charged)


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. 

CGM (Construction) / DISCOMs may deliberate the status.
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators, the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the last meeting, O&M stated that IB TPS has placed requisition for 6 Nos of Apex meters. SLDC stated that for replacement of all meters including generators, 10 nos of meters will be required. IBTPS may place their requisition for 10 Nos. of meters.

In the 113th PSOC meeting O&M has agreed to install 4 Nos meters as check meter in 220 kV Ib-Budhipadar line.

In the 114th PSOC meeting O & M stated that the energy meters have already been released. Ib 
TPS was advised to co-ordinate with Budhipadar sub-station for installation of meters.
OPTCL / IB TPS may deliberate    
E.3: Declaration of stand-by Energy Meter 
OPTCL should declare a meter as “Standby Meter” for Generators & EHT consumers for the purpose of energy accounting in case of failure of main & check meter. As per Section 2 (v) of Central Electricity Authority (Installation and Operation of Meters) Regulations, 2006, ‘Standby Meter’ means a meter connected to CT and VT, other than those used for main meter and check meter and shall be used for accounting and billing of electricity in case of failure of both main meter and check meter. The standby meter must be a ABT compliance meter.
Further, due to frequent problems noticed in the CVTs, it is suggested to replace the CVT by IVT for metering purpose. In the 114th PSOC meeting it was suggested that OPTCL may notify the stand by meters.

OPTCL may update the status.
E.4: Replacement of defective meters  at Renewable sources.
It is noticed that the energy meter installed at the following renewable sources are showing “power off” mostly during night time resulting non-recording of energy imported by the renewable projects.

1. Jay Iron & Steel, Bamra

2. MGM Green Energy Ltd., Chandpur
3. Molisati Vinimay Pvt. Ltd., Barkot
4. Rajratan Energy Holding Pvt. Ltd., Bolangir

5. Abacus Holdings Pvt. Ltd., Sonepur

6. Alex Green Energy Pvt. Ltd., Patnagarh
In the 114th PSOC meeting it was suggested to investigate the issue by GRIDCO & DISCOMs 

GRIDCO / DISCOMs may deliberate.
E.5: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same. Another meeting was proposed to be convened in the month of August’17 to finalize the mechanism of data communication. In the 113th PSOC meeting, it was decided that GRIDCO will take follow up action with all the RE generators to provide real time generation data to SLDC. ERLDC has reminded again to intimate the status.   

In the 114th PSOC meeting Director (Commercial) has agreed to convene a meeting soon to discuss the issue.

Telecom / GRIDCO may deliberate the status.
E.6: Major Events in the month of October’17
03.10.2017 – 220/132 kV, 160 MVA Auto at Balasore charged

16.10.2017 – 220/33 kV, 20 MVA 2nd Tfr at Bonei Charged

26.10.2017 – 132 kV Rairakhol Traction feeder charged

E.7: Important Grid Incidences during the month of October’17.
On 01.10.17 at 09:26 hrs 220 kV Budhipadar-Korba Ckt-III (idle charged from Budhipadar) tripped on D/P, ‘B’ ph to E/F, dist-2.55 km at Budhipadar end. Simultaneously all the 220 kV lines in bus-I at Budhipadar tripped on bus bar protection. On investigation it was found that insulator of 220 kV Budhipadar-Korba Ckt-III damaged at Loc. No. -8, 9 and 10

E.8: Outage of major transmission Elements during the month of October’17. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration
Dt/time
	Reason

	1
	220 kV Jaynagar-Balimela Ckt-I
	01.10.17

21:37
	02.10.17

16:41
	‘R’ph. Insulator damaged at Loc. No-1537

	2
	132 kV Budhipadar-Kalunga Ckt
	04.10.17

17:55
	06.10.17

16:51
	‘Y’ ph conductor snapped at Loc. No-261

	3
	132 kV Burla-Lapanga Ckt-I
	05.10.17

17:48
	06.10.17

12:24
	Line patrolling was done but no fault found.

	4
	132 kV OPCL-Kamakhyanagar Ckt
	07.10.17

14:42
	08.10.17

13:05
	‘R’ ph conductor snapped between gantry and Loc. No-1 of Kamakhyanagar.

	5
	400 kV Meramundali-Angul  Ckt-I
	16.10.17

14:42
	18.10.17

01:45
	Conductor snapped in transmission line

	6
	220 kV Chandaka-Mendhasal Ckt.-III
	17.10.17

10:22
	17.10.17

10:38
	Tree fault

	7
	400 kV Meramundali-Mendhasal Ckt
	21.10.17

07:33
	21.10.17

18:34
	Bamboo tree touched

	8
	400 kV Vedanta-Raigarh Ckt
	23.10.17

00:43


	23.10.17

19:51


	‘R’ ph conductor snapped between Loc. No-83/0 and 84/0

	9
	220 kV Joda-Ramchandrapur Ckt
	23.10.17

12:23
	26.10.17

12:14
	‘B’ph. Insulator damaged at Loc. No-179

	10
	132 kV Budhipadar-Sundergarh Ckt-I
	28.10.17

19:15
	29.10.17

18:24
	‘R’ ph LA burst at Sundergarh.

	11
	220 kV Balasore-New Duburi Ckt
	31.10.17

12:54
	08.09.17
11:00


	‘Y’ph. Insulator damaged at Loc. No-135


C.G.M. (O&M) may please deliberate.
E.9:  Review of Outage Program of State Generators / Transmission elements for the month of Dec’17:
Tentative Outage programme for State Generators for the month of Dec’2017 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1

# 5

# 6
	01.12 to 31.12.17

25.10.16 to continue

16.10.15 to continue
	Annual Maintenance

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to continue
	Under R,M & U

	3
	Balimela
	# 1
# 2

# 7
	05.08.16 to continue
01.11.17 to continue

12.10.17 to 15.12.17
	Under R,M & U
Programming for R&M

Governor problem 

	4
	Rengali
	# 5
	21.03.17 to 16.12.17
	Hoist gate problem

	5
	Upper Kolab
	# 2
	28.05.17 to 30.10.17
	MIV Problem

	6
	Upper Indravati
	# 1

# 3
	01.12.17 to 31.12.17

01.01.18 to 31.01.18
	Annual Maintenance

Annual Maintenance


OHPC / SLDC may deliberate. 
E.10: Generation Program for the month of December’17.
Generation schedule for the month of November’17 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.11.16
	Reservoir Level as on 01.11.17
	MDDL
	High Flood    Reservoir Level

	
	Dec’17
(1st fortnight)
	Dec’17
(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	30
	30
	630.06 ft 
	 629.25 ft
	590 ft.
	630 ft.

	HPS-II, Chiplima
	20
	20
	-
	-
	-
	-

	Balimela
	30
	30
	1507.20 ft 
	1486.50 ft
	1440 ft.
	1516 ft.

	Rengali
	10
	10
	123.00 mt

1.78mt mtr mt
	123.28 mt mt
	109.72mtr 
	123.5 mtr.

	U.Kolab
	20
	20
	856.65 mt mt
	854.06 mt
	844 mtr 
	858 mtr.

	U. Indravati
	50
	50
	639.28 mt
	634.40 mt mt
	625mtr 
	642 mtr

	MKD (O/D)
	40
	40
	2747.40 ft 
	2748.90 ft
	2685 ft.
	2750 ft.

	TOTAL
	200
	200
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

OHPC / SLDC may deliberate & Members may discuss. 
E.11: Anticipated power generation and demand for the month of December’2017.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	800
	1000

	2
	WESCO
	700
	900

	3
	NESCO
	550
	750

	4
	SOUTHCO
	400
	500

	6
	Total Discom
	2450
	3150

	
	System Loss & others
	150
	200

	
	Total Demand
	2600
	3350

	Availability
	
	

	1
	Hydro
	200
	900

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	400
	400

	4
	ISGS share (including OA)
	1050
	1100

	5
	CGP support (OA)
	200
	200

	6
	Total availability
	2600
	3350

	7
	Surplus / Deficit
	0
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Installation of OPGW in 400kV Indravati (PG) – Indravati (OHPC).

POWERGRID shall install OPGW in 400KV Indravati(PG) - Indravati(HPS) as per the  Fibre Optic Expansion package of ER in the month of December 2017. POWERGRID have requested ERLDC for issue of clearance for availing shutdown on the said line with effect from 06-12-2017 to 10-12-2017 from 08:00 hrs to 17:00 hrs on daily basis which needs approval basing on the consent of OPTCL in the upcoming 139th OCC meeting of ERPC scheduled to be held on 27.11.17. 
C.G.M. (Telecom) / OHPC / OPTCL / SLDC may please deliberate.
F.1:  Date and Venue of the next (116th) PSOC meeting.
PAGE  

