                                                                                                                  
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image1.png]PTC




Agenda

for

116th Power System Operational Coordination Meeting

Date: 27.12.2017
Venue: PTC, Chandaka, Bhubaneswar 
Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 116th PSOC Meeting to be held on 27.12.2017 at PTC, Chandaka, Bhubaneswar
Item no. 1: Confirmation of the minutes of the 115th PSOC Meeting held on 27.10.2017
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2016/3785(46) dated 03.11.2017 to all the members and also uploaded in the SLDC website. No comment has been received from any of the members except from IT wing of OPTCL. Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   : Grid Performance for the month of November’2017
C.1: Status of projects funded under PSDF scheme

C.2: Persistence overdrawal by West Bengal & Odisha

C.3: PPA details for the year 2017-18 to 2019-20

C.4: Data for preparation of Load Generation balance report (LGBR) of ER for the year 2018-19

C.5: 220kV Interconnecting line of OPTCL with 400/ 220kV Bolangir PG, Keonjhar & Pandiabil s/s

C.6: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

C.7: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.
C.8: Updating of GT & ICT tap position of all EHV transformers
C.9: Checklist for submission of updated data for protection data base

C.10: Status of disturbance recorder, stand alone event logger & time synchronization equipment

C.11: Status of ERS for ER constituents

C.12: Implementation of Automatic Demand Management Scheme
C.13: Mock Black start exercise in Eastern Region 
D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Prolonged outage of transmission elements and tentative revival dates
D.3: Communication issues 
D.4: Web based drawal / generation scheduling.

D.5: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.6: Software for Deviation charge billing.
D.7: DISCOM Issues 
E.1: Commissioning status of New Transmission elements. 

E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
E.3: Declaration of standby energy meter
E.4: Replacement of defective meters at renewable sources.
E.5: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
E.6: Major Events in the month of November’17

E.7: Important grid incidences during the month of November’17.
E.8: Outage of major transmission Elements during the month November’17. (above 10 hrs).
E.9: Review of Outage Program of State Generators for the month of January’2018
E.10: Generation Program for the month of January’2018.
E.11: Anticipated power generation and demand for the month of January’2018.
F.1:  Date and Venue of the next (117th) PSOC meeting
PART B: GRID PERFORMANCE
Review of Grid Performance for the month of November’17.

(A) Frequency:

Hourly frequency variation for the month of November’17.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	Sept’17
	0.00
	0.03
	10.01
	77.41
	12.56
	49.96

	Oct’17
	0.00
	0.02
	10.69
	76.19
	13.10
	49.98

	Nov’17
	0.00
	0.05
	13.74
	72.83
	13.38
	49.98


Maximum & Minimum frequency during the month of November’17.
	Month
	Freq (Hz)
	Date
	Time

	Oct’17
	Maximum – 50.10
	19.10.17
	18:30 Hrs

	
	Minimum – 49.76
	03.10.17
	22:00 Hrs

	Nov’17
	Maximum – 50.12
	26.11.17
	21:45 Hrs

	
	Minimum – 49.70
	07.11.17
	06:30 Hrs


Members may please discuss.

(B) Grid Demand up to the month of November’17
	 Month
	Maximum Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	April’17
	88.91
	27.04.17
	2493
	3463
	4299
	26.04.17
	24:00
	2466
	03.04.17
	07:00

	May’17
	88.13
	23.05.17
	2534
	3406
	4281
	04.05.17
	24:00
	2553
	06.05.17
	23:00

	June’17
	82.72
	03.06.17
	2269
	3151
	4009
	04.06.17
	24:00
	2091
	15.06.17
	18:00

	July’17
	86.54
	06.07.17
	2437
	3276
	4233
	05.07.17
	20:00
	2596
	23.07.17
	14:00

	Aug’17
	85.74
	26.08.17
	2500
	3360
	4269
	26.08.17
	24:00
	2647
	17.08.17
	16:00

	Sept’17
	93.49
	16.09.17
	2566
	3567
	4375
	26.09.17
	21:00
	2523
	12.09.17
	17:00

	Oct’17
	91.78
	13.10.17
	2655
	3569
	4491
	23.10.17
	20:00
	2763
	20.10.17
	06:00

	Nov’17
	79.46
	28.11.17
	2116
	2938
	4158
	01.11.17
	19:00
	2231
	24.11.17
	15:00

	Nov’16
	73.78
	02.11.16
	1980
	2750
	3866
	01.11.16
	19:00
	2017
	15.11.16
	24:00


(C) Voltage Profile of 220 kV Buses in OPTCL system for the month of: November’17
	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Balasore
	235.73
	27
	01:45
	222.74
	03
	18:15

	2
	Barkote
	235.49
	27
	03:45
	228.74
	09
	17:45

	3
	Bhadrak
	240.75
	22
	09:45
	223.14
	08
	17:45

	4
	Bhanjanagar
	237.40
	15
	21:45
	226.20
	28
	17:45

	5
	Bidanasi
	236.24
	30
	03:30
	224.99
	09
	17:45

	6
	Bolangir
	229.26
	18
	13:45
	218.29
	09
	17:45

	7
	Budhipadar
	230.47
	01
	14:30
	222.68
	21
	18:45

	8
	Chandaka
	233.30
	16
	02:00
	217.02
	29
	17:30

	9
	Cuttack
	233.16
	25
	02:00
	222.16
	01
	10:15

	10
	Duburi(O)
	238.73
	27
	01:45
	228.10
	08
	17:45

	11
	Duburi (N)
	227.70
	27
	01:45
	217.77
	10
	17:45

	12
	Jayanagar
	240.98
	04
	04:30
	222.62
	09
	16:15

	13
	Joda
	239.88
	05
	14:00
	223.25
	28
	19:00

	14
	Katapalli
	231.05
	18
	13:45
	222.79
	04
	18:15

	15
	Lapanga
	230.96
	11
	23:30
	224.36
	01
	17:30

	16
	Laxmipur
	240.29
	04
	04:30
	222.22
	24
	10:15

	17
	Mendhasal
	235.15
	27
	03:15
	221.81
	12
	17:45

	18
	Meramundali
	232.49
	27
	03:15
	209.75
	23
	08:45

	19
	Narendrapur
	233.36
	15
	21:45
	214.77
	09
	18:00

	20
	Nayagarh
	234.51
	18
	18:15
	222.10
	09
	18:00

	21
	Paradeep
	235.26
	27
	03:15
	216.67
	10
	18:45

	22
	Tarkera
	236.24
	27
	02:00
	229.03
	09
	17:45

	23
	Theruvali
	235.90
	16
	09:15
	214.42
	23
	05:45


The maximum Voltage of 240.98 kV occurred at Jayanagar 220 kV bus, while Meramundali 220 kV bus has experienced the minimum Voltage of 209.75 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Meramundali  and New Duburi bus during the month of November 2017 is shown below.
[image: image2.emf]200

205

210

215

220

225

230

235

240

245

250

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE  OF 220kV JAYANAGAR BUS 

FOR NOVEMBER 2017


[image: image3.emf]200

205

210

215

220

225

230

235

240

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF 220 kV NARENDRAPUR BUS 

FOR NOVEMBER 2017


[image: image4.emf]405

406

407

408

409

410

411

412

413

414

415

416

417

418

419

420

421

422

423

424

425

0:000:451:302:153:003:454:305:156:006:457:308:159:009:45

10:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF 400 kV  Meramundali BUS 

FOR NOVEMBER 2017


[image: image5.emf]405

406

407

408

409

410

411

412

413

414

415

416

417

418

419

420

421

422

423

424

425

426

427

428

429

430

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF 400 kV New Duburi BUS 

FOR NOVEMBER 2017


Members may discuss.
(D) Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of Nov-17
[image: image6.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  NOVEMBER'2017

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

74.08 6 15:15 27.36 18 9:15

74.16 6 15:15 27.36 18 9:15

111.80 28 7:15 21.00 26 0:45

1x100 50.56 22 18:45 8.24 30 9:15

1x160 91.32 22 18:45 15.28 30 9:15

1x160 100.68 30 6:15 22.60 23 9:45

1x160 88.88 30 6:30 19.76 23 9:45

1x160 39.52 1 10:15 4.36 16 3:30

1x100 31.20 1 10:45 2.84 16 3:15

1x100 27.32 1 10:15 2.84 16 3:15

2x160 147.56 8.00 15:15 12.88 22 9:00

131.00 22.00 17:45 13.52 22 9:00

94.20 26 21:00 14.44 21 22:30

85.92 2 15:30 18.76 23 11:45

1x100 57.64 8 18:00 5.40 22 10:30

1x160 101.52 8 18:00 31.20 26 3:45

1x100 63.16 8 18:00 20.36 26 15:45

1x160 79.96 20 18:15 25.64 25 11:30

CUTTACK 1x160

34.20

17 9:45 5.40 27 3:30

Out of service

63.56 28 17:45 5.92 25 3:00

32.24 4 18:00 4.24 7 9:15

1x160 71.16 30 19:45 24.24 18 6:15

1x160 71.08 30 19:45 21.20 18 6:15

66.40 24 16:45 25.76 10 13:45

66.68 24 10:45 25.64 10 13:45

66.00 24 16:30 25.84 10 13:45

1x100 22.72 2 7:15 3.68 24 12:45

1x100 22.76 2 7:15 3.40 24 12:45

1x160 16.80 22 16:30 3.00 24 12:30

2x160 30.60 21 11:15 7.80 20.00 12:00

30.00 21 11:15 7.80 20.00 12:00

43.36 13 19:45 6.80 2 14:15

42.24 13 19:45 6.80 2 14:00

37.64 27 19:30 6.04 2 14:00

2x100 21.60 22.00 9:15 3.60 6 6:00

38.40 6.00 9:15 4.80 22.00 5:45

2x160 129.48 16 7:45 27.00 30 23:45

105.12 24 15:45 6.24 29 14:30

1x100 74.28 16 7:45 6.16 29 15:15

1x160 93.80 1 18:30 16.64 16 8:30

1x100 57.36 1 18:00 7.76 16 8:30

1x50

4x100  66.44 4 18:30 7.00 12 5:30

66.84 4 18:30 19.84 8 12:00

66.64 4 18:30 12.52 8 12:15

64.88 14 17:30 7.88 12 23:45

2x100 85.96 8 17:30 3.76 15 8:45

85.16 15 17:45 8.40 29 10:00

1x160  42.00 4 13:00 4.00 27 22:00

1x160 42.00 4 13:00 4.00 27 22:00

2x160

1x100

KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & Katapali 

area load.}



DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, Jajpur 

Road, Kalarangi, Jajpur Town}

Mendhasal 

{ Part area load of Khurda S/S}

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }



"*" - Alternate P/S from Kuchei.



BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), MCL, 

Sundergarh,Brajarajnagar, Rajgangpur}

2x160 

BHADRAK 220/132 KV

{Bhadrak area load, Bhadrak(T),Soro,  

FACOR (I), Dhamra Port}

LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 

BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

SAMANGARA                                          

{ 

Puri, Nimapara & Konark}

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, Digapahandi, 

Mohana.}

THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

Rayagada & Paralakhemundi 

can be fed from Machhkund 

system.

ATRI                                                    

 {

Banki, 

Khurda, Chandpur & Argul}

Supported by Burla & Chipilima 

power.

PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 



JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]

JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

BIDANASI 220/132 KV

{Bidanasi, Khurda }

3x100 

3x100 

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}

3x160 



BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

Drawal details

Maximum Minimum


In the 115th PSOC meeting, it was deliberated by OPTCL that commissioning of meters for all the remaining Auto is under process. 
CGM (O&M) may please deliberate the status.
(E) DISCOM Drawal up to the month of November’17
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	April’17
	727.397
	760.945
	789.421
	17.199
	772.222
	11.277

	
	May’17
	751.644
	839.125
	871.775
	20.892
	850.883
	11.758

	
	June’17
	727.397
	750.856
	775.766
	20.502
	755.264
	4.408

	
	July’17
	751.644
	726.897
	761.921
	20.064
	741.857
	14.96

	
	Aug’17
	751.644
	765.985
	793.287
	17.844
	775.443
	9.458

	
	Sept’17
	727.397
	730.617
	768.066
	17.257
	750.809
	20.192

	
	Oct’17
	751.644
	734.68
	758.405
	15.23
	743.175
	8.495

	
	Nov’17
	727.397
	596.681
	610.35
	13.696
	596.654
	-0.027

	WESCO
	April’17
	582.74
	637.3
	689.833
	54.234
	635.599
	-1.701

	
	May’17
	602.164
	626.029
	673.256
	38.953
	634.303
	8.274

	
	June’17
	582.74
	557.308
	595.666
	41.282
	554.384
	-2.924

	
	July’17
	602.164
	577.765
	731.982
	154.21
	577.772
	0.007

	
	Aug’17
	602.164
	622.033
	687.379
	70.539
	616.84
	-5.193

	
	Sept’17
	582.74
	628.342
	841.153
	202.065
	639.088
	10.746

	
	Oct’17
	602.164
	639.382
	918.578
	284.197
	634.381
	-5.001

	
	Nov’17
	582.74
	547.045
	599.301
	56.681
	542.62
	-4.425

	NESCO
	April’17
	466.849
	493.551
	597.753
	108.907
	488.846
	-4.705

	
	May’17
	482.411
	468.854
	578.963
	114.176
	464.787
	-4.067

	
	June’17
	466.849
	432.223
	548.642
	109.141
	439.501
	7.278

	
	July’17
	482.411
	446.662
	556.119
	102.767
	453.352
	6.69

	
	Aug’17
	482.411
	494.041
	595.207
	100.708
	494.499
	0.458

	
	Sept’17
	466.849
	475.21
	589.343
	103.64
	485.703
	10.493

	
	Oct’17
	482.411
	458.363
	575.413
	93.521
	481.892
	23.529

	
	Nov’17
	466.849
	425.376
	528.499
	104.689
	423.81
	-1.566

	SOUTHCO
	April’17
	289.315
	303.102
	305.398
	0.651
	304.747
	1.645

	
	May’17
	298.959
	308.789
	314.808
	0.213
	314.595
	5.806

	
	June’17
	289.315
	279.684
	276.185
	0.433
	275.752
	-3.932

	
	July’17
	298.959
	294.376
	294.742
	0.629
	294.113
	-0.263

	
	Aug’17
	298.959
	310.404
	307.768
	0.391
	307.377
	-3.027

	
	Sept’17
	289.315
	294.522
	292.885
	0.074
	292.811
	-1.711

	
	Oct’17
	298.959
	290.344
	292.58
	0.052
	292.528
	2.184

	
	Nov’17
	289.315
	267.085
	265.471
	0.08045
	265.391
	-1.694


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
Members may please discuss.

(F) Energy Generation / Import up to the month of Novemer’17 
Figures in MU  
	Month
	Thermal (TTPS+IB)
	OHPC

& MKD
	CGP Support
	IPP Support
	Renewable
	ISGS
	Total

	Apr’17
	514.91
	581.71
	323.53
	349.53
	17.70
	705.86
	2493.24

	May’17
	543.19
	647.85
	296.06
	212.84
	10.45
	823.85
	2534.95

	June’17
	548.07
	610.00
	358.88
	203.70
	10.17
	537.95
	2268.75

	July’17
	554.18
	688.13
	190.09
	140.71
	10.46
	853.89
	2437.46

	Aug’17
	442.30
	746.49
	281.20
	167.14
	10.06
	853.01
	2500.20

	Sept’17
	363.01
	731.72
	189.82
	173.94
	9.45
	1091.74
	2565.69

	Oct’17
	453.38
	572.67
	155.32
	152.27
	35.85
	1311.67
	2655.33

	Nov’17
	433.21
	263.48
	209.28
	79.27
	9.31
	1121.06
	2115.61

	Total
	4285.51
	5105.58
	2213.48
	1558.67
	122.76
	8420.06
	21686.61


(G)  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of November’17 are as detailed:
	Month
	Total Generation
	Odisha Drawal
	AP Drawal 

	
	MU
	MW
	MU
	MW
	MU
	MW

	April’17
	65.960
	91.61
	32.320
	44.88
	30.950
	42.98

	May’17
	65.532
	88.08
	29.078
	39.08
	33.832
	45.47

	June’17
	45.678
	63.44
	19.509
	27.10
	24.105
	33.48

	July’17
	33.211
	44.63
	15.056
	20.24
	16.232
	21.81

	Aug’17
	51.798
	69.62
	24.448
	32.86
	25.220
	33.90

	Sept’17
	39.018
	54.19
	18.135
	25.18
	19.070
	26.49

	Oct’17
	34.353
	46.17
	16.510
	22.19
	16.164
	21.72

	Nov’17
	25.176
	34.97
	8.700
	12.08
	14.885
	20.67

	TOTAL
	370.726
	
	163.756
	
	180.458
	


In the 114th PSOC meeting it was deliberated that 132/ 33 kV Podagada sub-station is going to be commissioned soon after which matching load on Machhakund system is likely to be increased by 2 – 3 MW.
In the 115th PSOC meeting, O&M stated that Machhakund drawal shall be increased after commissioning of Podagada S/S by 15th December. 

On commissioning of a new S/S, 33 kV feeder loads are to be shifted to these S/Ss. It is noticed that the Discoms are dismantling the old lines. All Discoms were advised not to dismantle those lines so that flexibility of power supply will be maintained in contingency conditions.

CGM (Const) may update the progress
(H) Under Frequency Relay operation in OPTCL System during the month of November’17.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of November’17.
(I) Status of Open Access applications up to the month of November’2017
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’17
	21
	71
	0
	29
	121
	20
	71
	0
	28
	119
	2

	2
	May’17
	12
	31
	0
	32
	75
	12
	29
	0
	25
	66
	9

	3
	June’17
	23
	56
	0
	58
	137
	23
	56
	0
	40
	119
	18

	4
	July’17
	20
	85
	0
	36
	141
	20
	85
	0
	26
	131
	10

	5
	Aug’17
	9
	113
	0
	37
	159
	7
	110
	0
	31
	148
	11

	6
	Sept’17
	17
	140
	0
	52
	209
	15
	140
	0
	41
	196
	13

	7
	Oct’17
	17
	112
	0
	35
	164
	16
	112
	0
	32
	160
	4

	8
	Nov’17
	17
	51
	0
	39
	107
	15
	51
	0
	32
	98
	9

	
	Total
	136
	659
	0
	318
	1113
	128
	654
	0
	255
	1037
	76


PART C – Issues discussed in the 140th OCC meeting of ERPC on 19.12.2017
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting held on 29.04.16 at New Delhi, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format. 
The latest status as updated by OPTCL is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	Amount

Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	3
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	10.05.15
	10.05.17
	162.5 Cr.


	25.16 Cr.
	Total contract awarded for

Rs. 51.35 Cr




In the 113th PSOC meeting CGM (O&M) stated that that the DPR for installation of reactor has been sent to NLDC for PSDF funding as per the suggestion given by ERLDC during a joint study. CPC has been requested to take necessary action for tendering the 400 kV Bus reactor to be installed at Meramundali S/S.
In the 114th PSOC meeting CGM (O&M) stated that the automation of 7 nos of 220kV sub-stations needs to be incorporated for PSDF funding. A proposal in this regard is under process to be placed before BoD for approval. 

In the 115th PSOC meeting, GM (O&M) stated that the approved amount has been scaled down. The actual amount will be intimated to ERPC. Further, proposal for installation of 400 kV reactors at Meramundali S/S has been discussed and finalized in the meeting conducted by NLDC. After approval by the Appraisal committee, the same will be included for funding through PSDF.
In the 140th ERPC meeting, Member Secretary advised to furnish revised target date along with the details of work.
CGM (O&M) may please deliberate.
C.2: Persistent over drawl by West Bengal and Odisha
Odisha overdrawl pattern was also deliberated in 139th OCC. SLDC, Odisha informed that the over drawl was mainly due to forced outage of units at GMR and Vedanta units. GMR Unit – 3 of

350 MW which was out since 15-11-2017 on coal shortage, synchronized on 29-11-17 at 00:26 Hrs. Vedanta all units except Unit – 2 were also in service from 29-11-17 onward. Vedanta U-2 was out for maintenance work from 28-Jun-2017. However, even after synchronization of above units there is no reduction in Odhsa overdrawal.
West Bengal and Odisha are also advised to maximize their internal generation and increase their power purchase quantum in STOA/Power Exchange or from any other source to maintain their drawal as per schedule. In case of repetitive non-compliance of ERLDC instruction to curtail overdrawal during real time operation continues in future, ERLDC will have no other option but to approach appropriate commission with respect to erring entities.

In view of the above, Gridco is requested to explore import of power from any other sources to meet the State’s demand and to avoid appearance before the CERC.

Gridco may please deliberate.

C.3: PPA details for the years 2017-18 to 2019-20
CEA vide mail dated 21st November 2017 informed that it has been decided to estimate the demand and availability of power (energy and peak), initially for the year 2017-18 and subsequently for the years 2018-19 and 2019-20. In this regard, PPA details for the years 2017- 18 to 2019-20 are required as per the format available in the ERPC agenda.
All the constituents furnish the data as per the format to CEA by email: rk.jena@gov.in.

       GRIDCO / GMR / VL / OPGC / TTPS may deliberate.

C.4: Data for preparation Load Generation Balance Report (LGBR) of ER for the year 2018-19
As per the IEGC, RPC Secretariat is responsible for finalization of the Annual Load Generation Balance Report (LGBR) for Peak as well as Off-peak scenarios and the annual outage plan for the respective region. Vedanta / GMR / OPGC are requested to furnish their realistic generation programme for FY 2018-19.


Vedanta / GMR / OPGC may deliberate.

C.5: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 115th PSOC meeting the status has been updated as follows:

	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by June’18. 220 kV Sadeipali-Bolangir(PG) portion of the line is expected by Feb’18. 

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Line is expected by Dec’2017

Keonjhar S/S(220/33 kV) by February’18.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	March 2018 

	b.


	LILO of one circuit of Atri-Puri (Samangara) 220 kV D/C line at Pandiabil (PG). 
	Atri – Pandibili 220 kV one ckt charged on 19.05.17

Pandiabili – Samangara 220 kV one ckt. charged on 20.05.17. LILO of 2nd ckt is ready and will be charged after getting approval from ERLDC. 


In the 113th PSOC meeting AGM (Construction) stated that 2nd ckt of 220 kV Atri-Samangara line will be made LILO at Pandiabili. 
In the 115th PSOC meeting, CGM (Const) stated that NESCO may initiate for 33 kV connectivity with 220/33 kV S/S Keonjhar S/S on priority basis to draw power. 
CGM (Const.) may please deliberate.
C.6: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In the 107th PSOC meeting, CGM (IT) informed that “Crisis management plan” work is awarded to M/s Digital Age Strategies Pvt. Ltd. The said firm has completed the study of Servers and Firewalls at SLDC, Bhubaneswar and back-up SLDC at Meramundali. Presently the data centers of SLDC and GRIDCO are being audited for IT security vulnerability assessment.

SLDC is requested to nominate one officer for attending the Cyber Security training to be held at Bengaluru during 11th to 15th April’2017. Nominations from GRIDCO and OPTCL have since been received. Top management awareness-cum Seminar on the subject shall be organized subsequently.

In the 115th PSOC meeting, IT stated that the report has been furnished by Telecom. Tendering for ‘Auditor certification’ has been finalized. Work order will be placed soon.  
CGM (IT) / Telecom may please deliberate.
C.7: Certification through BIS as per IS 18001:2007 to all generating / transmission units.
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In the 110th PSOC meeting CGM (O&M) stated that BIS office at Bhubaneswar was contacted in this regard. It was decided that OPTCL shall nominate its officers to take training. After completion of training they will conduct audit and certify.
In the 111th PSOC meeting CGM (O&M) stated that 22 nos of officers are nominated from Chandaka, Mendhasal, Atri, Kesura, Bidanasi & Cuttack S/Ss to undergo training. Awareness training shall be started from 1st week of August’17. After receiving the price offer, order will be placed. 

In the 113th PSOC meeting CGM (O&M) stated that certification for 6 Nos of S/Ss will be done by December’2017.
In the 115th PSOC meeting GM (O&M) stated that 2nd phase training has been completed. Modality for 6 Nos of S/Ss will be prepared by December’2017.
CGM (O&M) may please update the status.
C.8: Updating of GT and ICT Tap position of all EHV transformers

All the generation, transmission and distribution utilities have been requested to go through Annexure-B19 of the 140th OCC agenda of ERPC related to last updated information related to GT/ICT/ATRs available at ERLDC and update the capacity, number, tap details, make (Company name) and other information including addition of new transformers, wherever felt necessary.
CGM (O&M) may please update the status.
C.9: Checklist for submission of updated data for Protection Database

The network data in Protection Database needs to be updated on regular basis on account of commissioning of new elements in the CTU as well as STU networks. Accordingly, a checklist has been prepared which is indicated below.

All the constituents are requested to submit the checklist on monthly bases in every OCC/PCC meetings.

In 139th OCC, all the constituents were advised to submit the data to ERPC vide mail (mserpcpower@nic.in) as per the checklist for last three months.

[image: image7.emf]
CGM (O&M) may please note.
C.10: Status of Disturbance Recorder, Stand alone Event Logger and Time Synchronization equipment.

The status of DR/EL and GPS as updated in previous OCCs is given below. Constituents are also requested to furnish their list of new DR/EL which are not included in the list.

[image: image8.emf]
[image: image9.emf]
[image: image10.emf]
[image: image11.emf]
CGM (O&M) / OHPC may please deliberate.
C.11: Status of Emergency Restoration System (ERS Towers) for Eastern Region constituents

CEA vide letter dated 21.07.2017 requested to send the status of state-wise availability of ERS towers and requirement of ERS towers.

In 136th OCC, MS, ERPC informed that CEA vide letter dated 21.07.2017 has sought the latest status on ERS. Therefore, OCC advised all constituents to send the updated status to ERPC secretariat vide mail (mserpc-power@nic.in).

Latest status is given below.

The present status of ERS towers in OPTCL system is as follows:

 220 kV ERS towers: 42 nos located at Mancheswar, Chatrapur & Budhipadar

 400 kV ERS towers: 2 nos located at Mancheswar.

 12 nos. of new 400 kV ERS towers have been recieved.

Another, 16 nos of 400 kV towers accompanied with 6 sets of T&P are required which is under process
CGM (O&M) / OHPC may please deliberate.
C.12: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************
The DPR for ADMS has already been approved by BoD, OPTCL. SLDC shall submit the proposal for funding by PSDF for ADMS to O&M wing of OPTCL for further action.
In the 108th PSOC meeting, SLDC stated that filling of format for PSDF and floating of tender is under process. The DPR will be sent to ERPC. CGM (Telecom) stated that SLDC may contact the consultant of PSDF for filling the format. The proposal has already been sent to NLDC to include for funding through PSDF.
In the 115th PSOC meeting, SLDC stated that EoI document is being prepared by CPC. GM (O&M) stated that the item has not been listed in PSDF. SLDC may investigate and resend the proposal.
SLDC may please deliberate.
C.13: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2017-18 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2017
	Conducted on 30th May 2017
	Last week of January 2018
	

	3
	Rengali
	2nd week of June 2017
	Conducted on 29.06.17
	Last week of November 2017
	Conducted on 30.11.17

	4
	U. Indravati
	3rd week of June 2017
	2nd week of July-2017
	2nd week of February 2018
	

	6
	Balimela
	3rd week of October  2017
	
	1st week of March 2018
	

	9
	Burla
	Last week of June 2017
	Can be conducted after synchronization of #2
	Last week of February 2018
	


OHPC / SLDC may please deliberate.
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of Oct’17:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	1
	-0.027
	0.004

	2
	WESCO
	0
	-4.425
	0.808

	3
	NESCO
	1
	-1.566
	0.368

	4
	SOUTHCO
	0
	-1.694
	0.634

	
	Total
	2
	-7.712
	


It is noticed that all utilities had under drawn during the month.
SLDC/ Discoms may please deliberate.
D.2: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl. No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220/132 kV, 100 MVA, Auto- 1 at Duburi
	Main tank severely damaged
	March-2018

	2
	220/132kV, 100MVA  Auto-2  at Bhadrak
	Fire hazard on 31.05.2017
	March-2018


CGM (O&M) may update the progress.

D.3: Communication issues 
The status of data communication from CGPs as deliberated in the last meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s IFFCO, Paradeep
	Outdoor commissioning work completed. RTU was locally tested. CVT already replaced. Data will be integrated after restoration of OPGW between New Duburi & Paradeep.

	2
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	3
	M/s Rohit Ferrotech
	PLCC established and inspection by Telecom Engineers completed.  Database has already been prepared by OPTCL.    

	4
	VISA
	CB & Status data are not available

	5
	Paradeep
	Duburi-Paradeep Line shut down required for drawing OPGW. After which data can be displayed. Dec’2017

	6
	GMR
	GMR on line data is available at SLDC but not available directly to ERLDC. GMR agreed to lay OPGW for data communication to ERLDC

	7
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 113th PSOC meeting GCC was requested to examine for filing a case before the OERC against the CGP / Industry, those who failed to comply establishment of communication facility as the matter has been delayed considerably. 
In the 19th SCADA O&M meeting of ER held at ERLDC, Kolkata on 07th April 2017 ERLDC informed that scheduling of GMR is being done at ERLDC so data must be reported to ERLDC directly from GMR. ERLDC requested OPTCL to take up the matter with GMR so that data & voice should be available directly to ERLDC. OPTCL agreed for the same.
In the 114th PSOC meeting GMR agreed to lay OPGW for data communication to ERLDC directly. GCC stated that case will be filed against the defaulting CGP / Industry within a week.

GCC has requested CGM (Telecom) to furnish the updated status of the defaulting CGP / Industry to file a case before OERC. In the 115th PSOC meeting, GCC intimated that they will file a case before the OERC soon.
CGM (Telecom) / GCC / GMR / RT&C may deliberate the status.
D.4: Web based drawal / generation scheduling.

In the 111th PSOC meeting it was decided that from 1st August 2017 the schedule submitted through web portal will be considered. The web based schedule will be implemented for TTPS and Ib TPS from 1st September’2017. 
At present all State thermal generating stations including IPPs & CGPs are furnishing their schedule through web portal except IbTPS. Provisions for acceptance of backing down schedule for past block are not kept in the software. IT has already been intimated about this issue. Provision for automatic extraction of Power Exchange schedule for incorporation in the schedule of respective Generator / CGP may be kept in the software.
In the 115th PSOC meeting OPGC stated that IbTPS has started scheduling through web portal. IT may explore to resolve the problems identified by SLDC.
SLDC / IT may update. 
D.5: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

The work for Automatic Meter Reading (AMR) for all the interface points is in progress. 

It was deliberated that from 1st March onwards the AMR shall be made “Go live”. Data will be available after one hour lapses of time.

In the 112th PSOC meeting DGM (IT) stated that TCS has complied with the discrepancies in August data. 679 Nos meter data have been collected during this month. Further, 750 Nos meter data will be available by next month. It was also decided that on 1st day of the month, SLDC will download the meter data and TCS will collect data on 2nd day and complete by evening of the day. On the 3rd day, SLDC and TCS will analyze the mismatch of data, if any. Further, a meeting may be convened by GRIDCO with all the DISCOMs to discuss acceptance of meter data through Text file.
In the 113th PSOC meeting IT stated that data from 690 Nos of meters have received during last month. It was decided that the data received by 2nd working day of the month shall be considered as final. It was further decided that the script shall be stopped on the 1st working day to enable for meter data collection by SLDC. 
In the 114th PSOC meeting IT stated that data from 640 no of sub-stations have been received on 2nd day of October. On 4th day data from some sub-stations was received. Data from remote sub-stations could not be collected due to communication network problem. Further, he stated that data from such sub-stations has to be collected manually each month. TCS has agreed to incorporate the billing software of secure meter. SLDC suggested to provide the AMR data to DISCOMs for monitoring of their real time drawal may be after lapses of 15 to 30 minutes time.
In the 115th PSOC meeting, revised deliberation of IT is as given below.

Total Number of meters integrated with AMI:
840 (Including 6 Power Houses)

Complete data available for Oct-17:

756
Out of 756 Nos of meters for which complete data is available, PRNs for testing could not be generated for 64 Nos of meters where meter power off event was observed. As per the given logic by SLDC, PRNs are generated for meters when complete data is available for whole month (96 blocks of data daily). Due to meter power off 96 daily blocks were not available for 64 meters and hence PRN was not generated.

As this is a genuine case and cannot be avoided, TCS has been advised to revisit the logic of PRN generation to include those meters or provide some alternative arrangement.
Regarding providing real time data to DISCOMs, IT stated that out of 840 total meters in AMI 600+ meters are old APEX type having very low baud rate which provide data at very slower rate. Needless to mention here that the meters are not polled one to one basis and are connected over a daisy chain resulting in sizable latency. Hence, real-time data publishing with the existing technology is not feasible.
The same can be attempted with minimal delay when the meters are replaced with modern meters having higher baud rate.

SLDC / IT may update the status.
D.6: Software for Deviation charge billing.

Hon’ble OERC may notify “Intra State Deviation settlement and related matters” Regulation at any time. For implementation of the regulation, required software for Deviation Charge billing need to be developed and tested. CGM (IT) may take necessary steps for development of the software.

As decided a committee has been constituted for development of the software in house. The work is in progress. 
In the 115th PSOC meeting, IT stated that the software is expected to be completed by end of Dec’17.
CGM (IT) / SLDC may please deliberate.
D.7.DISCOM Issues

CESU

1. Wide mismatch of drawal display through SCADA with actual meter data. It is requested to provide AMR data for realistic forecast.
2. To provide main & check meter reading of all APEX meters to check the accuracy of meters and also to provide the initial & final meter reading of all grid input points in the BSP bill to compare with the input given by all Circle Managers.
3. Construction of new 220/33kV grid at Chhendipada, 132/33kV grid at Parjanga & Khurda.
4. Connectivity of Ransingpur sub-station with Argul for stand by supply for Ransinghpur from which AIIMs is availing power supply.
. 
CESU may deliberate.
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by March’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by March’2018.

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	March’18

	4
	400/220 kV, 2x315 MVA Lapanga S/S
	June’18

	5
	220/33 kV, 2x20 MVA Baliguda S/S
	December’17

	6
	220/33 kV, 2x20 MVA Kalimela S/S
	June’18

	7
	220/33 kV, 2x20 MVA Kasipur S/S
	December’17

	8
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	February’18

	9
	220/33 kV, 2x20 MVA Narasinghpur S/S
	March’18

	10
	220/132 /33 kV, 2x100 MVA Aska S/S
	June’18

	11
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	January’18

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	December’18

	13
	220/132/33 kV Jayapatana S/S(320 MVA)
	December’18

	14
	220/132 kV Pratapassan S/S(320 MVA)
	March’18

	15
	220/132 kV Kesinga S/S (320 MVA)
	March’18

	16
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	March’18

	17
	132/33 kV Ghense S/S
	March’18

	18
	132/33 kV Dhenkikote S/S 
	January’18

	19
	132/33 kV Betanati S/S
	March’18

	20
	132/33 kV Kantabanji S/S
	January’18 (Line charged)

	21
	132/33 kV Podagada S/S
	December’17

	22
	132/33 kV Muniguda S/S
	December’17

	23
	132/33 kV R.Udyagiri S/S
	March’18

	24
	132/33 kV Chikiti S/S
	March’18

	25
	132/33 kV Athagarh S/S
	February’18

	26
	132/33 kV Tirtol S/S
	January’18 (Bus charged)


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. 

CGM (Construction) / DISCOMs may deliberate the status.
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators, the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the last meeting, O&M stated that IB TPS has placed requisition for 6 Nos of Apex meters. SLDC stated that for replacement of all meters including generators, 10 nos of meters will be required. IBTPS may place their requisition for 10 Nos. of meters.

In the 113th PSOC meeting O&M has agreed to install 4 Nos meters as check meter in 220 kV Ib-Budhipadar line.

In the 114th PSOC meeting O & M stated that the energy meters have already been released. IbTPS was advised to co-ordinate with Budhipadar sub-station for installation of meters.
In the 115th PSOC meeting, it was deliberated that the energy meters are yet to be installed. O&M was requested to explore the installation process.
OPTCL / IB TPS may deliberate    
E.3: Declaration of stand-by Energy Meter 
OPTCL should declare a meter as “Standby Meter” for Generators & EHT consumers for the purpose of energy accounting in case of failure of main & check meter. As per Section 2 (v) of Central Electricity Authority (Installation and Operation of Meters) Regulations, 2006, ‘Standby Meter’ means a meter connected to CT and VT, other than those used for main meter and check meter and shall be used for accounting and billing of electricity in case of failure of both main meter and check meter. The standby meter must be a ABT compliance meter.
Further, due to frequent problems noticed in the CVTs, it is suggested to replace the CVT by IVT for metering purpose. In the 114th PSOC meeting it was suggested that OPTCL may notify the stand by meters.

In the 115th PSOC meeting, it was decided that a separate meeting will be convened by GRIDCO with OPTCL (O&M) and SLDC to finalize the issue.

OPTCL may update the status.
E.4: Replacement of defective meters  at Renewable sources.
It is noticed that the energy meter installed at the following renewable sources are showing “power off” mostly during night time resulting non-recording of energy imported by the renewable projects.

1. Jay Iron & Steel, Bamra

2. MGM Green Energy Ltd., Chandpur
3. Molisati Vinimay Pvt. Ltd., Barkot
4. Rajratan Energy Holding Pvt. Ltd., Bolangir

5. Abacus Holdings Pvt. Ltd., Sonepur

6. Alex Green Energy Pvt. Ltd., Patnagarh
In the 114th PSOC meeting it was suggested to investigate the issue by GRIDCO & DISCOMs 

GRIDCO / DISCOMs may deliberate.
E.5: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same. Another meeting was proposed to be convened in the month of August’17 to finalize the mechanism of data communication. In the 113th PSOC meeting, it was decided that GRIDCO will take follow up action with all the RE generators to provide real time generation data to SLDC. ERLDC has reminded again to intimate the status.   

A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.
Telecom / GRIDCO may deliberate the status.
E.6: Major Events in the month of November’17
400kV Jhasuguda-Vedanta (Sterlite) DC charged for the first time as follows:

a. Ckt 1: 18:27Hrs of 06/11/17

b. Ckt 2: 18:53Hrs of 06/11/17
2) 500MVA ICT II at Pandiabili charged for the first time at 15:46Hrs of 17/11/17. Earlier it was charged on 12/07/16 but failed on 21/09/16 due to internal fault. It was replaced and first time charged at 15:46Hrs of 17/11/17
E.7: Important Grid Incidences during the month of November’17.
On 21.11.17 at 22:20 Hrs, 220/132kV, 160MVA AT-2 at Budhipadar sub-station tripped on differential protection due to bursting of 220kV B phase CT. All feeders emanating from 220kV Bus-I (Vedanta ckt-I, AAL ckt.-II, IbTPS ckt.- I & III, Korba ckt.-III) & AT-I tripped on bus-bar protection along with bus coupler breaker.  
E.8: Outage of major transmission Elements during the month of November’17. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration
Dt/time
	Reason

	1
	220 kV New Duburi-Balasore Ckt
	03.11.17

12:40
	04.11.17

13:27
	‘R’ ph. Insulator damaged at Loc. No-429

	2
	132 kV Chplima-Katapalli Ckt-II
	04.11.17

10:10
	07.11.17

16:39
	‘B’ ph LA punctured at Chiplima

	3
	220 kV Theruvali-Indravati Ckt.-IV
	16.11.17

21:44
	19.11.17

15:49
	

	4
	132 kV Budhipadar-Sundergarh Ckt.-II
	20.11.17

15:07
	21.11.17

12:23
	‘Y’ ph conductor snapped at Loc. No-91.

	5
	220/132kV 160 MVA AT-II at Budhipadar
	21.11.17

22:20
	22.11.17

19:19
	220kV side ‘B’ ph. CT burnt.


C.G.M. (O&M) may please deliberate.
E.9:  Review of Outage Program of State Generators / Transmission elements for the month of Jan’18:
Tentative Outage programme for State Generators for the month of January’2018 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 3
# 5

# 6
	01.01.18 to 31.01.18
25.10.16 to continue

16.10.15 to continue
	Annual Maintenance

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 2
# 3
	01.01.18 to 25.01.18
15.10.15 to continue
	Annual Maintenance

Under R,M & U

	3
	Balimela
	# 1
# 2

# 7
	05.08.16 to continue
01.11.17 to continue

12.10.17 to 31.01.18
	Under R,M & U
Programming for R&M

Governor problem 

	4
	Rengali
	# 5
# 4
	21.03.17 to 15.01.18
16.01.18 to 15.02.18
	Hoist gate problem
Annual Maintenance

	5
	Upper Kolab
	# 2
	28.05.17 to 30.04.18
	Upstream leakage & intake gate Problem

	6
	Upper Indravati
	# 3
	01.01.18 to 31.01.18
	Annual Maintenance


OHPC / SLDC may deliberate. 
E.10: Generation Program for the month of January’18.
Generation schedule for the month of January’18 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.12.16
	Reservoir Level as on 01.12.17
	MDDL
	High Flood    Reservoir Level

	
	Jan’18
(1st fortnight)
	Jan’18
(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	30
	30
	629.23 ft 
	 628.04 ft
	590 ft.
	630 ft.

	HPS-II, Chiplima
	20
	20
	-
	-
	-
	-

	Balimela
	80
	80
	1506.70 ft 
	1483.80 ft
	1440 ft.
	1516 ft.

	Rengali
	20
	20
	122.90 mt

1.78mt mtr mt
	122.99 mt mt
	109.72mtr 
	123.5 mtr.

	U.Kolab
	50
	50
	856.34 mt mt
	853.97 mt
	844 mtr 
	858 mtr.

	U. Indravati
	150
	150
	638.90 mt
	636.11 mt mt
	625mtr 
	642 mtr

	MKD (O/D)
	20
	20
	2744.80 ft 
	2748.80 ft
	2685 ft.
	2750 ft.

	TOTAL
	370
	370
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

OHPC / SLDC may deliberate & Members may discuss. 
E.11: Anticipated power generation and demand for the month of January’2018.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	800
	1000

	2
	WESCO
	800
	1050

	3
	NESCO
	550
	750

	4
	SOUTHCO
	400
	500

	6
	Total Discom
	2550
	3300

	
	System Loss & others
	150
	250

	
	Total Demand
	2700
	3550

	Availability
	
	

	1
	Hydro
	370
	1050

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	350
	350

	4
	ISGS share (including OA)
	1050
	1200

	5
	CGP support (OA)
	200
	200

	6
	Total availability
	2720
	3550

	7
	Surplus / Deficit
	20
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (117th) PSOC meeting.
PAGE  

