                                                                                                                  
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image1.png]PTC




Agenda

for

117th Power System Operational Coordination Meeting

Date: 27.01.2018
Venue: PTC, Chandaka, Bhubaneswar 
Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 117th PSOC Meeting to be held on 27.01.2018 at PTC, Chandaka, Bhubaneswar
Item no. 1: Confirmation of the minutes of the 116th PSOC Meeting held on 27.12.2017
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2016/217 (47) dated 11.01.2018 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   : Grid Performance for the month of December’2017
C.1: Status of projects funded under PSDF scheme

C.2: Persistence overdrawal by West Bengal & Odisha

C.3: PPA details for the year 2017-18 to 2019-20

C.4: 220kV Interconnecting line of OPTCL with 400/ 220kV Bolangir PG, Keonjhar & Pandiabil s/s

C.5: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

C.6: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.
C.7: Status of disturbance recorder, stand alone event logger & time synchronization equipment

C.8: Implementation of Automatic Demand Management Scheme
C.9: Mock Black start exercise in Eastern Region 
C.10: Training on “Optimum calculation of transfer capability (ATC, TTC and TRM)” by International Consultant
C.11: Less recording by Joda end energy meter of Joda _Ramchandrapur line.

C.12: Methodology for Submitting the Status of New Transmission Elements / Generating Units to be commissioned within the State
C.13: Non-functioning of bus coupler breaker at Indravati PH switchyard – Other observation of Protection audit team

D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Prolonged outage of transmission elements and tentative revival dates
D.3: Communication issues 
D.4: Web based drawal / generation scheduling.

D.5: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.6: Software for Deviation charge billing.
D.7: Rectification / Replacement of Defective Meters at different interface points.

D.8: DISCOM Issues 
E.1: Commissioning status of New Transmission elements. 

E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
E.3: Declaration of standby energy meter
E.4: Replacement of defective meters at renewable sources.
E.5: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
E.6: Major Events in the month of December’17

E.7: Important grid incidences during the month of December’17.
E.8: Outage of major transmission Elements during the month December’17. (above 10 hrs).
E.9: Review of Outage Program of State Generators for the month of February’2018
E.10: Generation Program for the month of February’2018.
E.11: Anticipated power generation and demand for the month of February’2018.
F.1:  Date and Venue of the next (118th) PSOC meeting
PART B: GRID PERFORMANCE
Review of Grid Performance for the month of December’17.

(A) Frequency:

Hourly frequency variation for the month of December’17.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	Oct’17
	0.00
	0.02
	10.69
	76.19
	13.10
	49.98

	Nov’17
	0.00
	0.05
	13.74
	72.83
	13.38
	49.98

	Dec’17
	0.00
	0.00
	11.84
	72.78
	15.37
	49.98


Maximum & Minimum frequency during the month of December’17.
	Month
	Freq (Hz)
	Date
	Time

	Nov’17
	Maximum – 50.12
	26.11.17
	21:45 Hrs

	
	Minimum – 49.70
	07.11.17
	06:30 Hrs

	Dec’17
	Maximum –50.18
	18.12.17
	2:00 Hrs

	
	Minimum – 49.75
	14.12.17
	9:15 Hrs


Members may please discuss.

(B) Grid Demand up to the month of December’17
	 Month
	Maximum Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	April’17
	88.91
	27.04.17
	2493
	3463
	4299
	26.04.17
	24:00
	2466
	03.04.17
	07:00

	May’17
	88.13
	23.05.17
	2534
	3406
	4281
	04.05.17
	24:00
	2553
	06.05.17
	23:00

	June’17
	82.72
	03.06.17
	2269
	3151
	4009
	04.06.17
	24:00
	2091
	15.06.17
	18:00

	July’17
	86.54
	06.07.17
	2437
	3276
	4233
	05.07.17
	20:00
	2596
	23.07.17
	14:00

	Aug’17
	85.74
	26.08.17
	2500
	3360
	4269
	26.08.17
	24:00
	2647
	17.08.17
	16:00

	Sept’17
	93.49
	16.09.17
	2566
	3567
	4375
	26.09.17
	21:00
	2523
	12.09.17
	17:00

	Oct’17
	91.78
	13.10.17
	2655
	3569
	4491
	23.10.17
	20:00
	2763
	20.10.17
	06:00

	Nov’17
	79.46
	28.11.17
	2116
	2938
	4158
	01.11.17
	19:00
	2231
	24.11.17
	15:00

	Dec’17
	77.95
	28.12.17
	2171
	2919
	4230
	27.12.17
	21:00
	2057
	09.12.17
	04:00

	Dec’16
	70.06
	01.12.15
	2026
	2723
	3813
	01.12.15
	19:00
	2042
	16.12.15
	15:00


(C) Voltage Profile of 220 kV Buses in OPTCL system for the month of: December’17
	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Balasore
	236.30
	9
	03:45
	223.89
	19
	17:45

	2
	Barkote
	235.84
	2
	02:00
	228.45
	30
	18:15

	3
	Bhadrak
	239.02
	9
	02:30
	223.43
	2
	17:30

	4
	Bhanjanagar
	238.27
	10
	01:00
	224.70
	29
	16:15

	5
	Bidanasi
	237.92
	28
	03:00
	225.85
	19
	09:00

	6
	Bolangir
	229.09
	4
	02:00
	213.61
	29
	18:30

	7
	Budhipadar
	231.91
	18
	04:15
	214.83
	24
	16:00

	8
	Chandaka
	234.69
	4
	02:45
	222.50
	15
	17:30

	9
	Cuttack
	
	
	
	
	
	

	10
	Duburi(O)
	238.73
	9
	02:30
	229.84
	30
	18:00

	11
	Duburi (N)
	227.82
	9
	02:15
	219.39
	29
	18:30

	12
	Jayanagar
	240.52
	20
	21:30
	219.56
	29
	16:15

	13
	Joda
	238.67
	21
	14:00
	225.28
	29
	17:45

	14
	Katapalli
	231.11
	2
	02:00
	219.62
	29
	18:45

	15
	Lapanga
	
	
	
	
	
	

	16
	Laxmipur
	239.88
	8
	21:00
	218.81
	29
	16:15

	17
	Mendhasal
	236.01
	4
	03:00
	205.82
	31
	10:00

	18
	Meramundali
	232.67
	2
	02:15
	226.72
	29
	17:45

	19
	Narendrapur
	239.25
	19
	11:30
	205.88
	19
	17:30

	20
	Nayagarh
	235.21
	4
	14:45
	221.81
	16
	17:30

	21
	Paradeep
	236.88
	9
	02:30
	221.93
	27
	18:30

	22
	Tarkera
	243.17
	6
	10:30
	227.07
	30
	18:15

	23
	Theruvali
	234.51
	8
	21:00
	212.34
	29
	16:15


The maximum Voltage of 243.17 kV occurred at Tarkera 220 kV bus, while Mendhasal 220 kV bus has experienced the minimum Voltage of 205.82 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Meramundali  and New Duburi bus during the month of December 2017 is shown below.
In the 116th PSOC meeting, it was decided that SLDC shall monitor the VAR injection by JSPL & BSL on real time basis and issue instruction to absorb VAr at high voltage condition failing which one ckt. of the above industries shall be disconnected from both the ends. JSPL requested to review the matter of isolation and assured to absorb VAr as per the instruction of SLDC.

[image: image2.emf]200

205

210

215

220

225

230

235

240

245

250

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF 220 KV JAYANAGAR BUS

For December 2017


[image: image3.emf]200

205

210

215

220

225

230

235

240

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF 220 kV NARENDRAPUR BUS

FOR DECEMBER 2017


[image: image4.emf]405

406

407

408

409

410

411

412

413

414

415

416

417

418

419

420

421

422

423

424

425

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF 400 kV MERAMUNDALI BUS

For December 2017


[image: image5.emf]405

406

407

408

409

410

411

412

413

414

415

416

417

418

419

420

421

422

423

424

425

426

427

428

429

430

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF 400kV  NEW DUBURI BUS

For December 2017


Members may discuss.
(D) Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of Dec-17
[image: image6.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  DECEMBER'2017

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

80.12 21 17:45 11.36 7 15:30

80.08 21 17:45 10.08 20 13:15

81.08 21 17:45 5.08 20 8:15

1x100 47.72 22 18:45 12.88 27 5:00

1x160 85.24 22 18:45 19.16 22 13:45

1x160 121.64 18 18:30 8.84 20 8:00

1x160 91.36 13 18:00 11.24 19 2:30

1x160

1x100 39.04 19 12:30 6.52 19 12:45

1x100 24.08 23 18:00 6.00 20 3:15

2x160 126.44 31.00 18:30 17.80 8 14:00

133.64 31.00 18:30 18.80 8 14:00

88.88 8 8:15 21.36 20 9:00

93.00 20 11:00 39.36 31 13:30

1x100 38.80 12 17:45 6.64 18 15:45

1x160 68.40 12 17:45 20.96 21 2:30

1x100 42.60 12 17:45 12.92 21 2:30

1x160 65.96 12 17:45 19.84 21 2:30

CUTTACK 1x160

Under shut down

61.24 14 17:45 8.20 20 14:15

50.76 31 19:00 7.84 20 14:00

1x160 78.60 24 19:30 25.76 15 14:30

1x160 129.32 27 10:00 25.64 15 14:30

57.56 30 19:00 11.08 21 8:30

58.68 27 12:30 12.56 22 14:00

58.52 27 12:15 12.88 22 14:00

1x100 33.28 8 8:00 4.88 19 21:00

1x100 29.40 15 17:30 4.72 19 21:00

1x160

1x160

70.04 19 17:45 6.68 26 1:00

36.96 18 18:15 6.56 26 1:00

2x100

2x160 97.00 21 18:00 25.48 2 2:30

96.56 21 18:00 25.56 2 2:30

1x100 55.76 21 18:00 14.24 2 2:30

1x160 90.16 3 17:45 16.48 9 2:45

1x100 66.04 21 12:30 9.84 9 13:00

1x50

4x100  67.76 14 9:00 20.72 27 14:15

69.08 14 9:00 8.36 6 10:30

58.68 20 10:00 14.96 14 8:30

58.68 20 10:00 10.48 19 10:00

2x100 86.40 27 17:45 18.40 13 11:30

81.68 27 17:45 17.96 13 11:30

1x160  58.00 22 13:00 1.00 5 21:00

1x160 58.00 22 13:00 1.00 5 21:00

2x160

1x100

KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & Katapali 

area load.}



DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, Jajpur 

Road, Kalarangi, Jajpur Town}

Mendhasal 

{ Part area load of Khurda S/S}

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }

JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]



"*" - Alternate P/S from Kuchei.



BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), MCL, 

Sundergarh,Brajarajnagar, Rajgangpur}

2x160 

BHADRAK 220/132 KV

{Bhadrak area load, Bhadrak(T),Soro,  

FACOR (I), Dhamra Port}

LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 

BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

SAMANGARA                                          

{ 

Puri, Nimapara & Konark}

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, Digapahandi, 

Mohana.}

THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

Rayagada & Paralakhemundi 

can be fed from Machhkund 

system.

ATRI                                                    

 {

Banki, 

Khurda, Chandpur & Argul}

Supported by Burla & Chipilima 

power.

PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

BIDANASI 220/132 KV

{Bidanasi, Khurda }

3x100 

3x100 

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}

3x160 



BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

Drawal details

Maximum Minimum


(E) DISCOM Drawal up to the month of December’17
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	April’17
	727.397
	760.945
	789.421
	17.199
	772.222
	11.277

	
	May’17
	751.644
	839.125
	871.775
	20.892
	850.883
	11.758

	
	June’17
	727.397
	750.856
	775.766
	20.502
	755.264
	4.408

	
	July’17
	751.644
	726.897
	761.921
	20.064
	741.857
	14.96

	
	Aug’17
	751.644
	765.985
	793.287
	17.844
	775.443
	9.458

	
	Sept’17
	727.397
	730.617
	768.066
	17.257
	750.809
	20.192

	
	Oct’17
	751.644
	734.68
	758.405
	15.23
	743.175
	8.495

	
	Nov’17
	727.397
	596.681
	610.35
	13.696
	596.654
	-0.027

	
	Dec’17
	751.644
	555.67
	584.501
	20.324
	564.177
	8.507

	WESCO
	April’17
	582.74
	637.3
	689.833
	54.234
	635.599
	-1.701

	
	May’17
	602.164
	626.029
	673.256
	38.953
	634.303
	8.274

	
	June’17
	582.74
	557.308
	595.666
	41.282
	554.384
	-2.924

	
	July’17
	602.164
	577.765
	731.982
	154.21
	577.772
	0.007

	
	Aug’17
	602.164
	622.033
	687.379
	70.539
	616.84
	-5.193

	
	Sept’17
	582.74
	628.342
	841.153
	202.065
	639.088
	10.746

	
	Oct’17
	602.164
	639.382
	918.578
	284.197
	634.381
	-5.001

	
	Nov’17
	582.74
	547.045
	599.301
	56.681
	542.62
	-4.425

	
	Dec’17
	602.164
	579.696
	709.064
	126.074
	582.99
	3.294

	NESCO
	April’17
	466.849
	493.551
	597.753
	108.907
	488.846
	-4.705

	
	May’17
	482.411
	468.854
	578.963
	114.176
	464.787
	-4.067

	
	June’17
	466.849
	432.223
	548.642
	109.141
	439.501
	7.278

	
	July’17
	482.411
	446.662
	556.119
	102.767
	453.352
	6.69

	
	Aug’17
	482.411
	494.041
	595.207
	100.708
	494.499
	0.458

	
	Sept’17
	466.849
	475.21
	589.343
	103.64
	485.703
	10.493

	
	Oct’17
	482.411
	458.363
	576.631
	93.521
	483.11
	24.747

	
	Nov’17
	466.849
	425.376
	528.517
	104.689
	423.828
	-1.548

	
	Dec’17
	482.411
	416.019
	508.591
	95.552
	413.039
	-2.98

	SOUTHCO
	April’17
	289.315
	303.102
	305.398
	0.651
	304.747
	1.645

	
	May’17
	298.959
	308.789
	314.808
	0.213
	314.595
	5.806

	
	June’17
	289.315
	279.684
	276.185
	0.433
	275.752
	-3.932

	
	July’17
	298.959
	294.376
	294.742
	0.629
	294.113
	-0.263

	
	Aug’17
	298.959
	310.404
	307.768
	0.391
	307.377
	-3.027

	
	Sept’17
	289.315
	294.522
	292.885
	0.074
	292.811
	-1.711

	
	Oct’17
	298.959
	290.344
	292.58
	0.052
	292.528
	2.184

	
	Nov’17
	289.315
	267.085
	265.471
	0.08045
	265.391
	-1.694

	
	Dec’17
	298.959
	271.068
	270.844
	0.265
	270.579
	-0.489


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
Members may please discuss.

(F) Energy Generation / Import up to the month of Decemer’17 
Figures in MU  
	Month
	Thermal (TTPS+IB)
	OHPC

& MKD
	CGP Support
	IPP Support
	Renewable
	ISGS
	Total

	Apr’17
	514.91
	581.71
	323.53
	349.53
	17.70
	705.86
	2493.24

	May’17
	543.19
	647.85
	296.06
	212.84
	10.45
	823.85
	2534.95

	June’17
	548.07
	610.00
	358.88
	203.70
	10.17
	537.95
	2268.75

	July’17
	554.18
	688.13
	190.09
	140.71
	10.46
	853.89
	2437.46

	Aug’17
	442.30
	746.49
	281.20
	167.14
	10.06
	853.01
	2500.20

	Sept’17
	363.01
	731.72
	189.82
	173.94
	9.45
	1091.74
	2565.69

	Oct’17
	453.38
	572.67
	155.32
	152.27
	35.85
	1311.67
	2655.33

	Nov’17
	433.21
	263.48
	209.28
	79.27
	9.31
	1121.06
	2115.61

	Dec’17
	554.44
	189.28
	223.23
	122.73
	10.44
	1061.73
	2171.41

	Total
	4839.95
	5294.86
	2436.71
	1681.40
	133.20
	9401.79
	23858.02


(G)  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of December’17 are as detailed:
	Month
	Total Generation
	Odisha Drawal
	AP Drawal 

	
	MU
	MW
	MU
	MW
	MU
	MW

	April’17
	65.960
	91.61
	32.320
	44.88
	30.950
	42.98

	May’17
	65.532
	88.08
	29.078
	39.08
	33.832
	45.47

	June’17
	45.678
	63.44
	19.509
	27.10
	24.105
	33.48

	July’17
	33.211
	44.63
	15.056
	20.24
	16.232
	21.81

	Aug’17
	51.798
	69.62
	24.448
	32.86
	25.220
	33.90

	Sept’17
	39.018
	54.19
	18.135
	25.18
	19.070
	26.49

	Oct’17
	34.353
	46.17
	16.510
	22.19
	16.164
	21.72

	Nov’17
	25.176
	34.97
	8.700
	12.08
	14.885
	20.67

	Dec’17
	38.400
	51.612
	18.613
	25.017
	17.893
	24.049

	TOTAL
	409.126
	
	182.369
	
	198.351
	


In the 115th PSOC meeting, O&M stated that Machhakund drawal shall be increased after commissioning of Podagada S/S by 15th December. 

CGM (Const) may update the progress
(H) Under Frequency Relay operation in OPTCL System during the month of December’17.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of December’17.
(I) Status of Open Access applications up to the month of December’2017
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’17
	21
	71
	0
	29
	121
	20
	71
	0
	28
	119
	2

	2
	May’17
	12
	31
	0
	32
	75
	12
	29
	0
	25
	66
	9

	3
	June’17
	23
	56
	0
	58
	137
	23
	56
	0
	40
	119
	18

	4
	July’17
	20
	85
	0
	36
	141
	20
	85
	0
	26
	131
	10

	5
	Aug’17
	9
	113
	0
	37
	159
	7
	110
	0
	31
	148
	11

	6
	Sept’17
	17
	140
	0
	52
	209
	15
	140
	0
	41
	196
	13

	7
	Oct’17
	17
	112
	0
	35
	164
	16
	112
	0
	32
	160
	4

	8
	Nov’17
	17
	51
	0
	39
	107
	15
	51
	0
	32
	98
	9

	9
	Dec’17
	34
	124
	0
	40
	198
	33
	124
	0
	35
	192
	6

	
	Total
	170
	783
	0
	358
	1311
	161
	778
	0
	290
	1229
	82


PART C – Issues discussed in the 141st  OCC meeting of ERPC on 18.01.2018
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	10.05.15
	10.05.17
	162.5 Cr.


	25.16 Cr.
	Total contract awarded for

Rs. 51.35 Cr



	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	
	22.35 Cr.
	
	Tendering under process


In the 116th PSOC meeting, OPTCL stated that they are linking another project for funding through PSDF and the target date will be changed. The revised target date for completion will be intimated to ERPC. Further, technical specification for 400 kV bus reactors at Meramundali S/S is yet to be prepared. It was suggested that CPC may expedite the same.

CGM (O&M) / OHPC may please deliberate.
C.2: Persistent over drawl by West Bengal and Odisha
In 140th OCC, over drawl pattern of West Bengal and Odisha was deliberated in detail. Some improvement in West Bengal and Odisha Drawl pattern has been observed during December and up to 7th January-2018. West Bengal average over drawl quantum was reduced to 1 MU during above mentioned period where as for Odisha over drawl quantum is around 2 MU per day.

In view of above, still there is some scope to maintain drawl as per schedule during morning and evening peak hour to avoid such quantum over drawl.
In view of the above, Gridco is requested to explore import of power from any other sources to meet the State’s demand and to avoid appearance before the CERC.
In the 116th PSOC meeting, GRIDCO stated that they are take necessary action for procurement of power from other sources to meet the State’s requirement.
Gridco may please deliberate.

C.3: PPA details for the years 2017-18 to 2019-20
CEA vide mail dated 21st November 2017 informed that it has been decided to estimate the demand and availability of power (energy and peak), initially for the year 2017-18 and subsequently for the years 2018-19 and 2019-20. In this regard, PPA details for the years 2017- 18 to 2019-20 are required as per the format available in the ERPC agenda.
All the constituents furnish the data as per the format to CEA by email: rk.jena@gov.in.
In the 116th PSOC meeting, GRIDCO stated that they shall furnish the required data.

       GRIDCO / GMR / VL / OPGC / TTPS may deliberate.

C.4: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 115th PSOC meeting the status has been updated as follows:

	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by June’18. 220 kV Sadeipali-Bolangir(PG) portion of the line is expected by Feb’18. 

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Keonjhar S/S (220/33 kV) by March’18.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	March 2018 


In the 116th PSOC meeting, NESCO intimated that they are ready to draw power from the proposed 220/33 kV S/S Keonjhar S/S.

CGM (Const.) may please deliberate.
C.5: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In the 107th PSOC meeting, CGM (IT) informed that “Crisis management plan” work is awarded to M/s Digital Age Strategies Pvt. Ltd. The said firm has completed the study of Servers and Firewalls at SLDC, Bhubaneswar and back-up SLDC at Meramundali. Presently the data centers of SLDC and GRIDCO are being audited for IT security vulnerability assessment.

In the 116th PSOC meeting, IT stated that audit has been completed and recommended for “ISO 270001 certificate”. Certificate will be received by the end of February’2018.
CGM (IT) / Telecom may please deliberate.
C.6: Certification through BIS as per IS 18001:2007 to all generating / transmission units.
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In the 111th PSOC meeting CGM (O&M) stated that 22 nos of officers are nominated from Chandaka, Mendhasal, Atri, Kesura, Bidanasi & Cuttack S/Ss to undergo training. Awareness training shall be started from 1st week of August’17. After receiving the price offer, order will be placed. 

In the 113th PSOC meeting CGM (O&M) stated that certification for 6 Nos of S/Ss will be done by December’2017.
In the 116th PSOC meeting, CGM (O&M) stated that draft modality has been prepared. Order for Mendhasal S/S will be issued as a pilot project.
CGM (O&M) may please update the status.
C.7: Status of Disturbance Recorder, Stand alone Event Logger and Time Synchronization equipment.

The status of DR/EL and GPS as updated in previous OCCs is given below. Constituents are also requested to furnish their list of new DR/EL which are not included in the list.

[image: image7.emf]
[image: image8.emf]
[image: image9.emf]
[image: image10.emf]
In the 116th PSOC meeting, CGM (O&M) stated that EL at Meramundali sub-station for 220kV side has been installed and EL for Mendhasal sub-station has been included in the automation project. OHPC stated that DR of Indravati PH has been rectified.
CGM (O&M) / OHPC may please deliberate.
C.8: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************

The latest status along with proposed logic as follows:
[image: image11.emf]
[image: image12.emf]
In the 115th PSOC meeting, SLDC stated that EoI document is being prepared by CPC. GM (O&M) stated that the item has not been listed in PSDF. SLDC may investigate and resend the proposal.

In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
SLDC may please deliberate.
C.9: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2017-18 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2017
	Conducted on 30th May 2017
	Last week of January 2018
	Conducted on 09.01.18

	3
	Rengali
	2nd week of June 2017
	Conducted on 29.06.17
	Last week of November 2017
	Conducted on 30.11.17

	4
	U. Indravati
	3rd week of June 2017
	2nd week of July-2017
	2nd week of February 2018
	

	6
	Balimela
	3rd week of October  2017
	
	1st week of March 2018
	

	9
	Burla
	Last week of June 2017
	Can be conducted after synchronization of #2
	Last week of February 2018
	To be conducted on 29th Jan’18


The black start exercise of Upper Indravati P.H. which was scheduled to be carried out on 09.01.2018 at 11:00Hrs could not be carried out due to transmission line problem and will be performed later.

OHPC / SLDC may please deliberate.
C.10: Training on “Optimum calculation of transfer capability (ATC, TTC and TRM)” by International Consultant

CEA vide mail dated 21st December 2017 informed that M/S Powertech Labs Inc. (PLI) Canada is providing consultancy services in India. As per the contract 3 days training is arranged at ERPC, Kolkata from 19th to 21st February 2018. The training will be held at the ERPC conference Hall, Kolkata. The training programme covers the following topics:

· Examination and recommendation of methodology for optimum calculation of transfer capability (TTC/ATC/TRM) in the planning and the operational horizons

· Calculation of transfer capability (TTC/ATC/TRM) for entire country

Constituents may nominate members preferably dealing with Transmission Planning and Grid Operation.
Sr. G.M. (CP) / CGM (O&M) / SLDC to deliberate.

C.11: Less recording by Joda end energy meter of Joda _Ramchandrapur line.
Meter No NP-5937- A installed at Joda end of 220 Ramchandarpur is recording 10 % to 15 % less as compared to Ramchandarpur end since 06.12.2017. Subsequently ERLDC vide mail dated 14.12.17 (with a copy to PGCIL) requested OPTCL to check CT/PT connection to the said meter. However the problem is still persisting and GRIDCO accounting is done with Ramchandarpur end meter.

CGM (O&M) to deliberate.

C.12: Methodology for Submitting the Status of New Transmission Elements / Generating Units to be commissioned within the State

For clear visibility of the Eastern Region networks and better system operation, all the new transmission elements (ISTS & STU links) need to be updated regularly. The commissioning of new transmission elements of ISTS lines has been processed and updated by RLDC whereas commissioning of STU lines has been processed by SLDCs. However, commissioning status of new STU lines of states has not been updated to ERLDC and ERPC regularly. Sometime SLDCs used to submit the status of their new commissioning of elements during OCC meeting. To regularize the process following methodology need to be adopted:

1. Transmission elements/ Generating units expected to be commissioned during next month need to be submitted to ERLDC/ERPC in every OCC.

2. Detail parameters of new transmission element before commissioning need to be shared with RLDC.

3. Detail date and time of synchronization need to be updated on real time to ERLDC after commissioning of any new Transmission element/Generating unit.

4. SLDC SCADA team needs to configure the new element in their SCADA and share the same to ERLDC SCADA for network update.

5. List of the new transmission elements/ generating units commissioned during last month need to inform RLDC/RPC within 7th day of the current month, so that same to be updated in OCC.
It was deliberated in the OCC meeting of ERPC that the information should be sent by email in the following id:

1. erldcam@gmail.com
2. ftcer@posoco.in
3. mserpc-power@nic.in
Members may discuss.

C.13: Non-functioning of bus coupler breaker at Indravati PH switchyard – Other observation of Protection audit team
On 04.01.2018 3rd party protection audit party of ERPC visited the switchyard of UIHEP. The following observations were made by the team.
1. 220kV bus coupler breaker is not operating since 2013.
2. ICT tie breaker is not in service.
3. Digital PLCC panel is installed which is yet to be commissioned.
PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of Dec’17:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	8.507
	1.530

	2
	WESCO
	0
	3.294
	0.568

	3
	NESCO
	1
	-2.980
	0.716

	4
	SOUTHCO
	0
	-0.489
	0.180

	
	Total
	1
	8.332
	


It is noticed that CESU & WESCO had overdrawn during the month.
SLDC/ Discoms may please deliberate.
D.2: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl. No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220/132 kV, 100 MVA, Auto- 1 at Duburi
	Main tank severely damaged
	March-2018

	2
	220/132kV, 100MVA  Auto-2  at Bhadrak
	Fire hazard on 31.05.2017
	March-2018


CGM (O&M) may update the progress.

D.3: Communication issues 
The status of data communication from CGPs as deliberated in the last meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s IFFCO, Paradeep
	Outdoor commissioning work completed. RTU was locally tested. CVT already replaced. Data will be integrated after restoration of OPGW between New Duburi & Paradeep.

	2
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	3
	M/s Rohit Ferrotech
	PLCC established and inspection by Telecom Engineers completed.  Database has already been prepared by OPTCL.    

	4
	VISA
	New RTU installed

	5
	Paradeep
	Duburi-Paradeep Line shutdown arranged for drawing OPGW after which data can be displayed. To be completed by January 2018.

	6
	GMR
	GMR on line data is available at SLDC but not available directly to ERLDC. GMR entrusted the work on Powergrid.

	7
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 116th PSOC meeting, GCC stated that they will file a case against NINL & IRE before the OERC soon.
CGM (Telecom) / GCC / GMR / RT&C may deliberate the status.
D.4: Web based drawal / generation scheduling.

In the 111th PSOC meeting it was decided that from 1st August 2017 the schedule submitted through web portal will be considered. The web based schedule will be implemented for TTPS and Ib TPS from 1st September’2017. 
At present all State thermal generating stations including IPPs & CGPs are furnishing their schedule through web portal except IbTPS. Provisions for acceptance of backing down schedule for past block are not kept in the software. IT has already been intimated about this issue. Provision for automatic extraction of Power Exchange schedule for incorporation in the schedule of respective Generator / CGP may be kept in the software.
In the 115th PSOC meeting OPGC stated that IbTPS has started scheduling through web portal. IT may explore to resolve the problems identified by SLDC.
SLDC / IT may update. 
D.5: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

Members may discuss.
D.6: Software for Deviation charge billing.

Hon’ble OERC may notify “Intra State Deviation settlement and related matters” Regulation at any time. For implementation of the regulation, required software for Deviation Charge billing need to be developed and tested. CGM (IT) may take necessary steps for development of the software.

As decided a committee has been constituted for development of the software in house. The work is in progress. 
In the 115th PSOC meeting, IT stated that the software is expected to be completed by end of Dec’17.
In the 116th PSOC meeting, IT stated that the software is completed except calculation portion, which will be done as per the draft Regulation of OERC.

CGM (IT) / SLDC may please deliberate.
D.7: Rectification / Replacement of Defective Meters at different interface points.

A list of defective meters indicating the defects is tabled as under 
[image: image13.emf]DEFECTIVE METERS LIST

WESCO

SL NO. SUBSTATION METERING POINT MAIN CHECK REMARK

1  Bamra  Bamra Traction Feeder 132kV OPT00949 OPT01295 Active Current of one phase is negative, while the respective 

other phase current is positive. The resultant active current, is 

reduced resulting less W imp energy recorded.

2  Bamra Solar  Joy Iron Steel Ltd(Solar) XD595254 XD595255 Meter power off frequently.

3  Barapalli  Trf1-40MVA 132/33kV OPT00025 DATA COULD NOT DOWNLOADED SINCE A LONG

4  Barapalli  Trf2-20MVA 132/33kV OPT00029 OPT00032 Current in L3 become reversed frequently,showing erronous 

reading

5  Barkote SOLAR  Molisati Solar 11kV ORBP7958 ORBP7959 Meter power off frequently.

6  Bhalulata  Bhalulata Traction Feeder 132kV OPT01269 OPT00957 Active Current of one phase is negative, while the respective 

other phase current is positive. The resultant active current, is 

reduced resulting less W imp energy recorded.

7 Budhipadar Basundhara Fdr-II APM03739 APM03767 PT connection to meter need to be changed from Bus PT to line 

PT

8  Brajarajnagar  Trf2-12.5MVA 132/11kV APM02463 Meter burnt since Sept'16 needs to be changed

9  Chandiposh  Chandiposh Traction 220kV OPT01214 OPT01153 Active Current of one phase is negative, while the respective 

other phase current is positive. The resultant active current, is 

reduced resulting less W imp energy recorded.

10 Chhend  Nuagaon Traction Feeder 132kV OPT00972 OPT00966 Active Current of one phase is negative, while the respective 

other phase current is positive. The resultant active current, is 

reduced resulting less W imp energy recorded.

11  Katapali  FRP Feeder 132kV FRP_MAIN1 ORBP7511 OPTCL meter need to be installed.

12  Lapanga  Rengali Traction 132KV OPT01948 OPT01949 Active Current of one phase is negative, while the respective 

other phase current is positive. The resultant active current, is 

reduced resulting less W imp energy recorded.

13  Padmapur  Trf1-20MVA 132/33kV OPT00970 OPT00925 DATA COULD NOT DOWNLOADED SINCE INSTALLATION

14 Patnagarh ALEX Solar Pvt. Ltd. OPT00652 OPT00659 Meter power off frequently.

15  Rajgangpur  Traction Feeder-1 132kV APM03807 APM03825 Showinlg less reading in import than actual and more 

reading in export than actual.

Presently WESCO meter has been considered for 

billing,but it is not processed in ERP.It is to be manually 

added.

Need meter change urgently.

16  Rourkela  Traction Trf-12.5MVA 132/25kV OPT01009 OPT01347 Active Current of one phase is negative, while the respective 

other phase current is positive. The resultant active current, is 

reduced resulting less W imp energy recorded.

17 Sadeipali REHPL(Solar) 11kV OPT00796 OPT00731 Meter power off frequently.

18  Sonepur Solar  ABACUS HOLDINGS Solar ORBP7956 ORBP7957 Meter power off frequently.

CESU

1 Chandpur MGM SOLAR ORBP8178 ORBP8179 Meter power off frequently.

2 Kharagprasad Traction Feeder 132kV APM03744 APM03757 Active Current of one phase is negative, while the respective 

other phase current is positive. The resultant active current, is 

reduced resulting less W imp energy recorded.

3 Khurda Kaipadar Traction Feeder 132kV OPT00778 Defective since installation.

4 Paradeep PPL Feeder-I OPT00895 OPT00658 Energy recorded in export even if the ckt is isolated condition 

from PPL end.

NESCO

1 Karanjia TRF-III APM02365 Check meter showing improper voltage.The phase voltage 

varies from 12kV to 19kV,where as main meter (APM02331) 

showing correct voltage.

2 Polasponga Traction Feeder 132kV APM12622 APM12623 Active Current of one phase is negative, while the respective 

other phase current is positive. The resultant active current, is 

reduced resulting less W imp energy recorded.

SOUTHCO

1 Rayagada Traction Feeder 132kV OPT00740 OPT00714 Active Current of one phase is negative, while the respective 

other phase current is positive. The resultant active current, is 

reduced resulting less W imp energy recorded.

2 Umerkote Trf2-20MVA 132/33kV OPT00680 DATA COULD NOT DOWNLOADED SINCE INSTALLATION


OPTCL may take necessary action for checking CT / PT and early replacement of these meters wherever required.
CGM (O&M) may please deliberate.
D.8.DISCOM Issues

CESU

1. Connectivity of Ransingpur sub-station with Argul for stand by supply for Ransinghpur (connected to Chandaka S/S) from which AIIMs is availing power supply.
2. Construction of new 132/33 kV S/S at Parajang, Khurda Ind. Estate & Kantilo.
3. Bay extension at Angul S/S.
4. Mismatch of drawal display with actual meter data.
5. Providing main and check meter data to CESU.
SOUTHCO
1. Interruption of power supply to Rambha Traction sub-station during November-2017 occurred 3 times (26minutes) thereby causing serious disruption of passenger trains & loosing reliability surcharge.
2. Installation of Apex meter at 33kV Mukhiguda feeder at Tentuhkhunti Grid by OPTCL for accounting & deduction of WESCO drawal from SOUTHCO Energy account.
. CESU / SOUTHCO may deliberate.
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by March’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by March’2018.

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	March’18

	4
	400/220 kV, 2x315 MVA Lapanga S/S
	June’18

	5
	220/33 kV, 2x20 MVA Baliguda S/S
	December’18

	6
	220/33 kV, 2x20 MVA Kalimela S/S
	June’18

	7
	220/33 kV, 2x20 MVA Kasipur S/S
	March’18

	8
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	March’18

	9
	220/33 kV, 2x20 MVA Narasinghpur S/S
	March’18

	10
	220/132 /33 kV, 2x100 MVA Aska S/S
	June’18

	11
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	January’18

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	December’18

	13
	220/132/33 kV Jayapatana S/S(320 MVA)
	December’18

	14
	220/132 kV Pratapsasan S/S(320 MVA)
	March’19

	15
	220/132 kV Kesinga S/S (320 MVA)
	June’18

	16
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	March’18

	17
	132/33 kV Ghense S/S
	March’18

	18
	132/33 kV Dhenkikote S/S 
	January’18

	19
	132/33 kV Betanati S/S
	March’18

	20
	132/33 kV Kantabanji S/S
	January’18 

	21
	132/33 kV Podagada S/S
	December’17

	22
	132/33 kV Muniguda S/S
	Charged

	23
	132/33 kV R.Udyagiri S/S
	March’18

	24
	132/33 kV Chikiti S/S
	March’18

	25
	132/33 kV Athagarh S/S
	February’18

	26
	132/33 kV Tirtol S/S
	January’18 (Bus charged)


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. 

CGM (Construction) / DISCOMs may deliberate the status.
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators, the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the 116th PSOC meeting, it was decided that CGM (O&M), OPTCL may direct the E & MR Division, Burla to take up the work.
OPTCL / IB TPS may deliberate    
E.3: Declaration of stand-by Energy Meter 
OPTCL should declare a meter as “Standby Meter” for Generators & EHT consumers for the purpose of energy accounting in case of failure of main & check meter. As per Section 2 (v) of Central Electricity Authority (Installation and Operation of Meters) Regulations, 2006, ‘Standby Meter’ means a meter connected to CT and VT, other than those used for main meter and check meter and shall be used for accounting and billing of electricity in case of failure of both main meter and check meter. The standby meter must be a ABT compliance meter.
Further, due to frequent problems noticed in the CVTs, it is suggested to replace the CVT by IVT for metering purpose. In the 114th PSOC meeting it was suggested that OPTCL may notify the stand by meters.

In the 116th PSOC meeting, it was decided that a separate meeting is to be convened by GRIDCO with OPTCL (O&M) and SLDC to finalise the issue.

.

OPTCL may update the status.
E.4: Replacement of defective meters  at Renewable sources.
It is noticed that the energy meter installed at the following renewable sources are showing “power off” mostly during night time resulting non-recording of energy imported by the renewable projects.

1. Jay Iron & Steel, Bamra

2. MGM Green Energy Ltd., Chandpur
3. Molisati Vinimay Pvt. Ltd., Barkot
4. Rajratan Energy Holding Pvt. Ltd., Bolangir

5. Abacus Holdings Pvt. Ltd., Sonepur

6. Alex Green Energy Pvt. Ltd., Patnagarh
In the 116th PSOC meeting GRIDCO stated that letter has been issued to the solar power producers in this regard. Discoms are requested to intimate the status in the next meeting.
GRIDCO / DISCOMs may deliberate.
E.5: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same. Another meeting was proposed to be convened in the month of August’17 to finalize the mechanism of data communication. In the 113th PSOC meeting, it was decided that GRIDCO will take follow up action with all the RE generators to provide real time generation data to SLDC. ERLDC has reminded again to intimate the status.   

A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.
In the 116th PSOC meeting, CGM (Telecom) stated that the solar projects need to pay the SCADA integration charges for display of the data through SCADA.
Telecom / GRIDCO may deliberate the status.
E.6: Major Events in the month of December’17
19/12/2017: 220 kV Samagara – Atri ckt.- II made LILO at Pandiabili.

27/12/2017: 20MVA, 132/33kV 2nd transformer commissioned at Mania.
E.7: Important Grid Incidences during the month of December’17.
No important grid incidence during the month of December 2018.

E.8: Outage of major transmission Elements during the month of December’17. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration

Dt/time
	Reason

	1
	132 kV Katapalli-ChiplimaCkt-II
	08.12.17

08:16
	13.12.17

13:54
	‘Y’ ph. 132 kV CT burst at Chiplima switchyard

	2
	220 kV Bhanjanagar-MendhasalCkt
	13.12.17

12:42
	15.12.17

19:42
	‘R’ ph jumper snapped at Loc. No-87

	3
	220 kV Tarkera-RengaliCkt-II
	14.12.17

15:14
	15.12.17

14:08
	Insulator damaged at Loc. No-2.

	4
	132 kV Kendrapara-ParadeepCkt-I
	14.12.17

16:58
	16.12.17

16:28
	‘R’ ph conductor snapped between Loc. No-216 to 223 and ‘R’ ph jumper snapped at Loc. No-306.

	5
	220 kV Balasore-Baripada PG Ckt-II
	18.12.17

19:47
	20.12.17

00:40
	‘Y’ ph Conductor snapped at Loc. No-48

	6
	132 kV Meramundali-ChainpalCkt-II
	23.12.17

06:23
	24.12.17

17:05
	Line tripped due to fog

	7
	132 kV Meramundali-ChainpalCkt-II
	25.12.17

04:13
	26.12.17

17:26
	Line tripped due to fog


C.G.M. (O&M) may please deliberate.

E.9:  Review of Outage Program of State Generators / Transmission elements for the month of Feb’18:
Tentative Outage programme for State Generators for the month of February’2018 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 4
# 5

# 6
	02.02.18 to 28.02.18
25.10.16 to continue

16.10.15 to continue
	Annual Maintenance

Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to continue
	Under R,M & U

	3
	Balimela
	# 1
# 2

# 7
	05.08.16 to continue
01.11.17 to continue

12.10.17 to 31.01.18
	Under R,M & U
Programming for R&M

Governor problem 

	4
	Rengali
	# 5
# 4

# 2
	21.03.17 to 31.01.18
01.02.18 to 28.02.18

16.02.18 to 15.06.18
	Hoist gate problem
Annual Maintenance

Programming for Capital Maintenance

	5
	Upper Kolab
	# 2
	28.05.17 to 30.04.18
	Upstream leakage & intake gate Problem

	6
	Upper Indravati
	# 3
	08.02.18 to 07.03.18
	Annual Maintenance


OHPC / SLDC may deliberate. 
E.10: Generation Program for the month of February’18.
Generation schedule for the month of February’18 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.01.17
	Reservoir Level as on 01.01.18
	MDDL
	High Flood    Reservoir Level

	
	Feb’18
(1st fortnight)
	Feb’18
(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	40
	40
	628.17 ft 
	 626.85 ft
	590 ft.
	630 ft.

	HPS-II, Chiplima
	30
	30
	-
	-
	-
	-

	Balimela
	90
	90
	1503.90 ft 
	1479.00 ft
	1440 ft.
	1516 ft.

	Rengali
	30
	30
	122.52 mt

1.78mt mtr mt
	122.66 mt mt
	109.72mtr 
	123.5 mtr.

	U.Kolab
	60
	60
	856.39 mt mt
	853.78 mt
	844 mtr 
	858 mtr.

	U. Indravati
	200
	200
	639.00 mt
	635.92 mt mt
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2740.50 ft 
	2747.40 ft
	2685 ft.
	2750 ft.

	TOTAL
	480
	480
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

OHPC / SLDC may deliberate & Members may discuss. 
E.11: Anticipated power generation and demand for the month of February’2018.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	800
	1000

	2
	WESCO
	800
	1050

	3
	NESCO
	550
	750

	4
	SOUTHCO
	400
	500

	6
	Total Discom
	2550
	3300

	
	System Loss & others
	150
	250

	
	Total Demand
	2700
	3550

	Availability
	
	

	1
	Hydro
	370
	1050

	2
	State Thermal
	750
	750

	3
	IPP, small hydro &RE
	350
	350

	4
	ISGS share (including OA)
	1050
	1200

	5
	CGP support (OA)
	200
	200

	6
	Total availability
	2720
	3550

	7
	Surplus / Deficit
	20
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (118th) PSOC meeting.
PAGE  

