                                                                                                                  
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image1.png]PTC




Agenda

for

119th Power System Operational Coordination Meeting

Date: 23.03.2018
Venue: PTC, Chandaka, Bhubaneswar 
Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 119th PSOC Meeting to be held on 23.03.2018 at PTC, Chandaka, Bhubaneswar
Item no. 1: Confirmation of the minutes of the 118th PSOC Meeting held on 26.02.2018
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2017/893 (47) dated 17.03.2018 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   : Grid Performance for the month of February’2018
C.1: Status of projects funded under PSDF scheme

C.2: PPA details for the year 2017-18 to 2019-20
C.3: 220kV Interconnecting line of OPTCL with 400/ 220kV Bolangir PG, Keonjhar & Pandiabil s/s

C.4: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

C.5: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.

C.6: Status of Disturbance Recorder, stand alone Event Logger & time synchronization equipment

C.7: Implementation of Automatic Demand Management Scheme
C.8: Mock Black start exercise in Eastern Region 

C.9:Non-functioning of bus coupler breaker at Indravati PH switchyard – Other observation of Protection audit team

C.10: Status of UFRs healthiness installed in Eastern Region

C.11: Approval of outage procedure and Submission of outage request to ERLDC as per procedure.
C.12: Islanding Scheme for GMR & IbTPS.

C.13: Accounting of Tertiary Loading Arrangement at PGCIL Grid S/Ss in ER.
D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Prolonged outage of transmission elements and tentative revival dates

D.3: Communication issues 
D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.5: Software for Deviation charge billing.
D.6: DISCOM Issues 
D.7: Rectification / Replacement of Defective Meters at different interface points.

E.1: Commissioning status of New Transmission elements. 

E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
E.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.

E.4: Planned outage of 400 kV transmission elements and Inter-State tie lines.

E.5: Disturbance at Tarkera Grid S/S- Interruption of power supply to RSP-Agenda by RSP
E.6: Major Events in the month of February’18
E.7: Important grid incidences during the month of February’18.

E.8: Outage of major transmission Elements during the month February’18. (above 10 hrs).
E.9: Review of Outage Program of State Generators for the month of April’2018
E.10: Generation Program for the month of April’2018.
E.11: Anticipated power generation and demand for the month of April’2018.

F.1:  Date and Venue of the next (120th) PSOC meeting
PART B: GRID PERFORMANCE
Review of Grid Performance for the month of February’18.

(A) Frequency:

Hourly frequency variation for the month of February’18.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	Dec’17
	0.00
	0.00
	11.84
	72.78
	15.37
	49.98

	Jan’18
	0.00
	0.01
	8.94
	76.51
	14.55
	49.99

	Feb’18
	0.00
	0.00
	7.09
	78.50
	14.41
	49.99


Maximum & Minimum frequency during the month of February’18.
	Month
	Freq (Hz)
	Date
	Time

	Jan’18
	Maximum –50.16
	31.01.18
	21:45 Hrs

	
	Minimum – 49.74
	01.01.18
	07:15 Hrs

	Feb’18
	Maximum –50.12
	16.02.18
	13:00 Hrs

	
	Minimum – 49.78
	23.02.18
	06:30 Hrs


Members may please discuss.

(B) Grid Demand up to the month of February’18
	 Month
	Max. Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	April’17
	88.91
	27.04.17
	2493
	3463
	4299
	26.04.17
	24:00
	2466
	03.04.17
	07:00

	May’17
	88.13
	23.05.17
	2534
	3406
	4281
	04.05.17
	24:00
	2553
	06.05.17
	23:00

	June’17
	82.72
	03.06.17
	2269
	3151
	4009
	04.06.17
	24:00
	2091
	15.06.17
	18:00

	July’17
	86.54
	06.07.17
	2437
	3276
	4233
	05.07.17
	20:00
	2596
	23.07.17
	14:00

	Aug’17
	85.74
	26.08.17
	2500
	3360
	4269
	26.08.17
	24:00
	2647
	17.08.17
	16:00

	Sept’17
	93.49
	16.09.17
	2566
	3567
	4375
	26.09.17
	21:00
	2523
	12.09.17
	17:00

	Oct’17
	91.78
	13.10.17
	2655
	3569
	4491
	23.10.17
	20:00
	2763
	20.10.17
	06:00

	Nov’17
	79.46
	28.11.17
	2116
	2938
	4158
	01.11.17
	19:00
	2231
	24.11.17
	15:00

	Dec’17
	77.95
	28.12.17
	2171
	2919
	4230
	27.12.17
	21:00
	2057
	09.12.17
	04:00

	Jan’18
	84.87
	29.01.18
	2311
	3107
	4251
	28.01.18
	20:00
	2244
	04.01.18
	04:00

	Feb’18
	83.37
	21.02.18
	2194
	3265
	4211
	12.02.18
	20:00
	2241
	16.02.18
	15:00

	Feb’17
	76.22
	25.02.17
	1970
	2932
	3845
	23.02.17
	20:00
	2305
	04.02.17
	15:00


(C) Voltage Profile of 220 kV Buses in OPTCL system for the month of: February’18
	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Atri
	232.49
	05
	2:00
	220.43
	23
	18:15

	2
	Balasore
	232.78
	01
	3:15
	215.63
	23
	09:00

	3
	Barkote
	233.88
	05
	2:00
	224.22
	10
	11:30

	4
	Bhadrak
	235.26
	03
	2:00
	220.08
	23
	18:45

	5
	Bhanjanagar
	236.24
	05
	3:15
	222.04
	02
	18:00

	6
	Bidanasi
	237.63
	05
	3:15
	222.68
	19
	19:00

	7
	Bolangir
	231.63
	11
	21:15
	208.36
	02
	18:00

	8
	Budhipadar
	232.95
	11
	21:15
	221.09
	02
	17:15

	9
	Chandaka
	232.78
	05
	02:00
	220.02
	23
	18:15

	10
	Cuttack
	234.97
	05
	03:15
	220.25
	19
	19:00

	11
	Duburi(O)
	236.65
	05
	02:00
	227.30
	23
	18:45

	12
	Duburi (N)
	225.97
	05
	02:00
	216.21
	23
	18:45

	13
	Jayanagar
	238.50
	05
	03:15
	221.64
	04
	16:30

	14
	Joda
	232.03
	17
	03:30
	220.71
	27
	19:00

	15
	Katapalli
	235.90
	01
	15:15
	213.28
	06
	08:00

	16
	Lapanga
	234.51
	11
	21:15
	217.14
	01
	15:00

	17
	Laxmipur
	237.69
	01
	01:15
	220.77
	10
	14:30

	18
	Mendhasal
	234.22
	05
	02:00
	221.52
	23
	18:15

	19
	Meramundali
	230.36
	05
	03:15
	222.74
	26
	18:15

	20
	Narendrapur
	231.91
	21
	14:00
	213.67
	01
	12:30

	21
	Nayagarh
	233.36
	05
	02:00
	220.19
	02
	18:00

	22
	Paradeep
	233.01
	05
	02:00
	216.67
	28
	19:45

	23
	Tarkera
	233.99
	12
	02:30
	227.47
	17
	19:15

	24
	Theruvali
	232.49
	01
	01:30
	211.42
	10
	14:45


The maximum Voltage of 238.50 kV occurred at Jayanagar 220 kV bus, while Bolangir 220 kV bus has experienced the minimum Voltage of 208.36 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Meramundali  and New Duburi bus during the month of January 2018 is shown below.
[image: image2.emf]200

205

210

215

220

225

230

235

240

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

NARENDRAPUR  220 kV VOLTAGE PROFILE

FEBRUARY 2018


[image: image3.emf]200

205

210

215

220

225

230

235

240

245

250

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

JAYANAGAR 220 VOLTAGE PROFILE

FEBRUARY 2018


[image: image4.emf]400

401

402

403

404

405

406

407

408

409

410

411

412

413

414

415

416

417

418

419

420

421

422

423

424

425

0:001:002:003:004:005:006:007:008:009:0010:0011:0012:0013:0014:0015:0016:0017:0018:0019:0020:0021:0022:0023:00

Voltage In kV

Time In Hrs

MERAMUNDALI 400 kV VOLTAGE PROFILE

FEBRUARY 2018


[image: image5.emf]405

406

407

408

409

410

411

412

413

414

415

416

417

418

419

420

421

422

423

424

425

426

427

428

429

430

0:000:451:302:153:003:454:305:156:006:457:308:159:009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

NEW DUBURI 400 kV VOLTAGE PROFILE

FEBRUARY 2018


Members may discuss.
(D) Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of Feb-18
[image: image6.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  FEBRUARY'2018

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

68.72 28 19:45 9.24 3 8:15

68.56 28 19:45 5.28 3 8:15

69.28 28 19:45 4.88 3 8:15

1x100 62.64 3 11:15 6.24 1 14:30

1x160 85.64 28 19:45 11.72 1 14:30

YET TO BE COMMISSIONED

1x160 96.36 23 8:45 8.32 22 8:45

1x160 83.04 22 9:00 11.56 23 8:45

1x160 59.40 19 19:00 11.68 22 14:00

1x100 45.12 24 11:45 8.40 22 14:00

1x100 41.92 19 19:00 9.24 20 8:00

2x160 130.72 4 18:45 24.12 11 20:00

138.08 4 18:45 25.80 11 20:00

117.68 1 14:45 15.88 16 10:15

117.04 1 14:45 15.76 16 10:15

1x100 Under shut down

1x160 89.64 27 19:00 27.44 3 3:30

1x100 61.12 28 8:00 16.92 3 3:30

1x160 95.16 28 8:00 26.16 3 3:30

CUTTACK 1x160

59.96

16 19:15 8.00 23 13:45

Under shut down

81.40 2 9:30 11.04 23 14:30

61.72 4 19:00 10.52 23 14:30

1x160 87.52 24 18:45 27.64 16 17:00

1x160 87.64 24 18:45 27.60 16 17:00

59.92 22 20:00 23.00 14 16:45

52.52 22 19:45 23.44 14 16:45

52.60 22 19:45 23.72 14 16:45

1x100 32.60 6 18:15 6.84 4 22:00

1x100 32.76 6 18:15 7.28 4 22:00

1x160 49.04 6 18:15 11.04 4 22:00

1x160 93.72 5 15:45 7.44 1 15:00

93.72 5 15:45 7.44 1 15:00

40.24 16 18:30 5.96 7 3:45

39.36 16 18:30 5.96 7 3:45

38.60 16 18:30 5.92 7 4:30

2x100 20.40 10 9:00 7.20 11 12:00

32.40 10 9:00 7.80 11 12:00

2x160 89.12 28 18:45 4.48 1 12:30

100.32 1 17:15 8.72 3 1:15

1x100 51.32 28 18:45 13.98 21 13:30

1x160 99.80 27 19:45 30.88 8 16:15

1x100 60.80 27 19:45 18.64 8 16:15

1x50

4x100  52.76 19 19:15 9.96 25 21:15

54.08 19 19:15 12.72 25 21:15

52.84 19 19:15 11.20 25 21:15

52.64 19 19:15 11.80 25 21:15

2x100 84.92 27 19:00 18.84 8 14:00

80.04 26 20:15 18.24 8 14:00

1x160  63.00 10 13:00 0.00 22 21:00

1x160 63.00 10 13:00 0.00 22 21:00

2x160 42.72 19 18:45 13.48 3 3:30

42.76 19 18:45 13.44 3 3:30

1x100

KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & Katapali 

area load.}



DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, Jajpur 

Road, Kalarangi, Jajpur Town}

Mendhasal 

{ Part area load of Khurda S/S}

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }

JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]



"*" - Alternate P/S from Kuchei.



BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), MCL, 

Sundergarh,Brajarajnagar, Rajgangpur}

2x160 

BHADRAK 220/132 KV

{Bhadrak area load, Bhadrak(T),Soro,  

FACOR (I), Dhamra Port}

LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 

BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

SAMANGARA                                          

{ 

Puri, Nimapara & Konark}

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, Digapahandi, 

Mohana.}

THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

Rayagada & Paralakhemundi 

can be fed from Machhkund 

system.

ATRI                                                    

 {

Banki, 

Khurda, Chandpur & Argul}

Supported by Burla & Chipilima 

power.

PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

BIDANASI 220/132 KV

{Bidanasi, Khurda }

3x100 

3x100 

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}

3x160 



BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

Drawal details

Maximum Minimum


(E) DISCOM Drawal up to the month of February’18
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	April’17
	727.397
	760.945
	789.421
	17.199
	772.222
	11.277

	
	May’17
	751.644
	839.125
	871.775
	20.892
	850.883
	11.758

	
	June’17
	727.397
	750.856
	775.766
	20.502
	755.264
	4.408

	
	July’17
	751.644
	726.897
	761.921
	20.064
	741.857
	14.96

	
	Aug’17
	751.644
	765.985
	793.287
	17.844
	775.443
	9.458

	
	Sept’17
	727.397
	730.617
	768.066
	17.257
	750.809
	20.192

	
	Oct’17
	751.644
	734.68
	758.409
	15.23
	743.179
	8.499

	
	Nov’17
	727.397
	596.681
	610.336
	13.696
	596.64
	-0.041

	
	Dec’17
	751.644
	555.67
	584.551
	20.324
	564.227
	8.557

	
	Jan’18
	751.644
	570.873
	593.97
	20.482
	573.488
	2.615

	
	Feb’18
	678.904
	578.615
	592.019
	17.464
	574.555
	-4.06

	WESCO
	April’17
	582.74
	637.3
	692.208
	54.234
	637.974
	0.674

	
	May’17
	602.164
	626.029
	675.458
	38.953
	636.505
	10.476

	
	June’17
	582.74
	557.308
	597.211
	41.282
	555.929
	-1.379

	
	July’17
	602.164
	577.765
	734.199
	154.21
	579.989
	2.224

	
	Aug’17
	602.164
	622.033
	689.155
	70.539
	618.616
	-3.417

	
	Sept’17
	582.74
	628.342
	843.984
	202.065
	641.919
	13.577

	
	Oct’17
	602.164
	639.382
	922.703
	284.197
	638.506
	-0.876

	
	Nov’17
	582.74
	547.045
	601.11
	56.681
	544.429
	-2.616

	
	Dec’17
	602.164
	579.696
	709.064
	126.074
	582.99
	3.294

	
	Jan’18
	602.164
	605.119
	790.905
	190.803
	600.102
	-5.017

	
	Feb’18
	543.89
	557.519
	785.651
	232.094
	553.557
	-3.962

	NESCO
	April’17
	466.849
	493.551
	597.753
	108.907
	488.846
	-4.705

	
	May’17
	482.411
	468.854
	578.963
	114.176
	464.787
	-4.067

	
	June’17
	466.849
	432.223
	548.642
	109.141
	439.501
	7.278

	
	July’17
	482.411
	446.662
	556.119
	102.767
	453.352
	6.69

	
	Aug’17
	482.411
	494.041
	595.207
	100.708
	494.499
	0.458

	
	Sept’17
	466.849
	475.21
	589.343
	103.64
	485.703
	10.493

	
	Oct’17
	482.411
	458.363
	577.417
	93.521
	483.896
	25.533

	
	Nov’17
	466.849
	425.376
	528.517
	104.689
	423.828
	-1.548

	
	Dec’17
	482.411
	416.019
	510.678
	95.552
	415.126
	-0.893

	
	Jan’18
	482.411
	426.851
	529.108
	103.001
	426.107
	-0.7444

	
	Feb’18
	435.726
	407.243
	485.227
	80.556
	404.671
	-2.572

	SOUTHCO
	April’17
	289.315
	303.102
	305.398
	0.651
	304.747
	1.645

	
	May’17
	298.959
	308.789
	314.808
	0.213
	314.595
	5.806

	
	June’17
	289.315
	279.684
	276.185
	0.433
	275.752
	-3.932

	
	July’17
	298.959
	294.376
	294.742
	0.629
	294.113
	-0.263

	
	Aug’17
	298.959
	310.404
	307.768
	0.391
	307.377
	-3.027

	
	Sept’17
	289.315
	294.522
	292.885
	0.074
	292.811
	-1.711

	
	Oct’17
	298.959
	290.344
	292.58
	0.052
	292.528
	2.184

	
	Nov’17
	289.315
	267.085
	265.471
	0.0805
	265.3906
	-1.694

	
	Dec’17
	298.959
	271.068
	270.844
	0.265
	270.579
	-0.489

	
	Jan’18
	298.959
	281.023
	281.141
	0.025
	281.116
	0.093

	
	Feb’18
	270.027
	262.415
	263.204
	0
	263.204
	0.789


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
Members may please discuss.

(F) Energy Generation / Import up to the month of February’18
Figures in MU  
	Month
	Thermal (TTPS+IB)
	OHPC

& MKD
	CGP Support
	IPP Support
	Renewable
	ISGS
	Total

	Apr’17
	514.91
	581.71
	323.53
	349.53
	17.70
	705.86
	2493.24

	May’17
	543.19
	647.85
	296.06
	212.84
	10.45
	823.85
	2534.95

	June’17
	548.07
	610.00
	358.88
	203.70
	10.17
	537.95
	2268.75

	July’17
	554.18
	688.13
	190.09
	140.71
	10.46
	853.89
	2437.46

	Aug’17
	442.30
	746.49
	281.20
	167.14
	10.06
	853.01
	2500.20

	Sept’17
	363.01
	731.72
	189.82
	173.94
	9.45
	1091.74
	2565.69

	Oct’17
	453.38
	572.67
	155.32
	152.27
	35.85
	1311.67
	2655.33

	Nov’17
	433.21
	263.48
	209.28
	79.27
	9.31
	1121.06
	2115.61

	Dec’17
	554.44
	189.28
	223.23
	122.73
	10.44
	1061.73
	2171.41

	Jan’18
	545.32
	236.10
	360.28
	301.68
	9.93
	858.09
	2311.40

	Feb’18
	515.05
	270.16
	247.77
	156.54
	9.34
	994.90
	2193.76

	Total
	5467.06
	5537.59
	2835.46
	2060.35
	143.16
	10213.75
	26247.80


(G)  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of February’18 are as detailed:
	Month
	Total Generation
	Odisha Drawal
	AP Drawal 

	
	MU
	MW
	MU
	MW
	MU
	MW

	April’17
	65.960
	91.61
	32.320
	44.88
	30.950
	42.98

	May’17
	65.532
	88.08
	29.078
	39.08
	33.832
	45.47

	June’17
	45.678
	63.44
	19.509
	27.10
	24.105
	33.48

	July’17
	33.211
	44.63
	15.056
	20.24
	16.232
	21.81

	Aug’17
	51.798
	69.62
	24.448
	32.86
	25.220
	33.90

	Sept’17
	39.018
	54.19
	18.135
	25.18
	19.070
	26.49

	Oct’17
	34.353
	46.17
	16.510
	22.19
	16.164
	21.72

	Nov’17
	25.176
	34.97
	8.700
	12.08
	14.885
	20.67

	Dec’17
	38.400
	51.612
	18.613
	25.017
	17.893
	24.049

	Jan’18
	 38.901                                                                  
	52.286                 
	19.620
	26.371
	17.395
	23.380

	Feb’18
	34.547
	51.409
	17.431
	25.938
	15.467
	23.016

	TOTAL
	482.574
	
	219.420
	
	231.213
	


In the 118th PSOC meeting, O&M stated that Machhakund drawal shall be increased after drawal of power from Podagada S/S by SOUTHCO. 

SOUTHCO may deliberate.
(H) Under Frequency Relay operation in OPTCL System during the month of February’18.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of February’18.
(I) Status of Open Access applications up to the month of February’2018
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’17
	21
	71
	0
	29
	121
	20
	71
	0
	28
	119
	2

	2
	May’17
	12
	31
	0
	32
	75
	12
	29
	0
	25
	66
	9

	3
	June’17
	23
	56
	0
	58
	137
	23
	56
	0
	40
	119
	18

	4
	July’17
	20
	85
	0
	36
	141
	20
	85
	0
	26
	131
	10

	5
	Aug’17
	9
	113
	0
	37
	159
	7
	110
	0
	31
	148
	11

	6
	Sept’17
	17
	140
	0
	52
	209
	15
	140
	0
	41
	196
	13

	7
	Oct’17
	17
	112
	0
	35
	164
	16
	112
	0
	32
	160
	4

	8
	Nov’17
	17
	51
	0
	39
	107
	15
	51
	0
	32
	98
	9

	9
	Dec’17
	34
	124
	0
	40
	198
	33
	124
	0
	35
	192
	6

	10
	Jan’18
	16
	84
	0
	35
	135
	16
	84
	0
	32
	132
	3

	11
	Feb’18
	27
	81
	0
	32
	140
	24
	80
	0
	29
	133
	7

	
	Total
	213
	948
	0
	425
	1586
	201
	942
	0
	351
	1494
	92


PART C – Issues to be discussed in the 143rd  OCC meeting of ERPC on 26.03.2018
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	10.05.15
	10.05.17
	162.5 Cr.


	25.16 Cr.
	Total contract awarded for

Rs. 51.35 Cr



	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-

Jan 19

Burla-Nov

2018,

Chiplima

Dec 2018
	22.35 Cr.
	
	Tendering under process


In the 116th PSOC meeting, OPTCL stated that they are linking another project for funding through PSDF and the target date will be changed. The revised target date for completion will be intimated to ERPC. Further, technical specification for 400 kV bus reactors at Meramundali S/S is yet to be prepared. It was suggested that CPC may expedite the same.

In the 117th PSOC meeting, O&M deliberated that 400 kV bus Reactor for Meramundali S/S shall be procured after getting sanction by PSDF. 

In the 118th PSOC meeting, SLDC stated that ADMS for SLDC is to be incorporated as PSDF funding item. O&M shall intimate ERPC the revised target date.
CGM (O&M) / OHPC / SLDC may please update the status.
C.2: PPA details for the years 2017-18 to 2019-20
CEA vide mail dated 21st November 2017 informed that it has been decided to estimate the demand and availability of power (energy and peak), initially for the year 2017-18 and subsequently for the years 2018-19 and 2019-20. In this regard, PPA details for the years 2017- 18 to 2019-20 are required as per the format available in the ERPC agenda.
All the constituents furnish the data as per the format to CEA by email: rk.jena@gov.in.
In the 117th PSOC meeting, CGM (PP) stated that GRIDCO is preparing the details of PPA made by them. GMR was requested to forward the required data.

In the 118th PSOC meeting, CGM (PP) stated that GRIDCO will forward the required information to ERPC by the end of February’2018.
GRIDCO / GMR / OPGC / may deliberate.

C.3: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 118th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by June’18. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by June’18. 

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Keonjhar S/S (220/33 kV) by March’18.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	March 2018 


CGM (Const.) may please deliberate.
C.4: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In the 107th PSOC meeting, CGM (IT) informed that “Crisis management plan” work is awarded to M/s Digital Age Strategies Pvt. Ltd. The said firm has completed the study of Servers and Firewalls at SLDC, Bhubaneswar and back-up SLDC at Meramundali. Presently the data centers of SLDC and GRIDCO are being audited for IT security vulnerability assessment.

In the 117th PSOC meeting, CGM (IT) stated that audit has been completed and “ISO 270001 certificate”. Certificate has been issued conditionally for one year. In case OPTCL fails to fulfill the conditions, the period may not be extended. However, the audit report is yet to be received by IT.

In the 118th PSOC meeting, CGM (IT) stated that certificate is expected by end of February’2018.
CGM (IT) / Telecom may please deliberate.
C.5: Certification through BIS as per IS 18001:2007 to all generating / transmission units.
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In the 111th PSOC meeting CGM (O&M) stated that 22 nos of officers are nominated from Chandaka, Mendhasal, Atri, Kesura, Bidanasi & Cuttack S/Ss to undergo training. Awareness training shall be started from 1st week of August’17. After receiving the price offer, order will be placed. 

In the 113th PSOC meeting CGM (O&M) stated that certification for 6 Nos of S/Ss will be done by December’2017.
In the 116th PSOC meeting, CGM (O&M) stated that draft modality has been prepared. Order for Mendhasal S/S will be issued as a pilot project.
In the 117th PSOC meeting CGM (O&M) stated that draft project report for Mendhasal S/S has been submitted to BIS. The report will be approved in the meeting to be conducted by them.

In the 118th PSOC meeting, O&M stated that the report has already been submitted. Approval is yet to be received.
CGM (O&M) may please update the status.
C.6: Status of Disturbance Recorder, Stand alone Event Logger and Time Synchronization equipment.

The status of DR/EL and GPS as updated in previous OCCs is given below. Constituents are also requested to furnish their list of new DR/EL which are not included in the list.

[image: image7.emf]
[image: image8.emf]
[image: image9.emf]
[image: image10.emf]
In the 118th PSOC meeting O&M stated that 400 kV side EL at Mendhasal shall be replaced. Further, Order has been placed for automation of Mendhasal S/S, which is expected to be completed by end of May’2018. Proposal for including DR for Indravati is yet to be sent.
CGM (O&M) / OHPC may please deliberate.
C.7: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************

The latest status along with proposed logic as follows:
[image: image11.emf]
[image: image12.emf]
In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 117th PSOC meeting it was decided that SLDC shall process for tendering.

In the 118th PSOC meeting, SLDC stated that the tender specification is expected to be received from CPC by 1st week of March’2018. After receiving the same SLDC will process for tendering
SLDC may please deliberate.
C.8: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2017-18 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2017
	Conducted on 30th May 2017
	Last week of January 2018
	Conducted on 09.01.18

	3
	Rengali
	2nd week of June 2017
	Conducted on 29.06.17
	Last week of November 2017
	Conducted on 30.11.17

	4
	U. Indravati
	3rd week of June 2017
	2nd week of July-2017
	2nd week of February 2018
	Conducted on
09.03.2018

	6
	Balimela
	3rd week of October  2017
	Conducted on 09.01.18
	1st week of March 2018
	Conducted on
09.03.2018

	9
	Burla
	Last week of June 2017
	Can be conducted after synchronization of #2
	Last week of February 2018
	Conducted on 29th Jan’18


The black start exercise of Upper Indravati P.H. which was scheduled to be carried out on 09.01.2018 at 11:00Hrs could not be carried out due to transmission line problem and will be performed later.

OHPC / SLDC may please deliberate.
C.9: Non-functioning of bus coupler breaker at Indravati PH switchyard – Other observation of Protection audit team
On 04.01.2018 3rd party protection audit party of ERPC visited the switchyard of UIHEP. The following observations were made by the team.
1. 220kV bus coupler breaker is not operating since 2013.
2. ICT tie breaker is not in service.
3. Digital PLCC panel is installed which is yet to be commissioned.
In the 117th PSOC meeting it was decided that OHPC may take necessary action for compliance of the protection audit report. OHPC may prepare the DPR if required and seek funding through PSDF.  OHPC may coordinate GM (O&M) in this regard. CGM (Telecom) stated that communication system has been approved by NLDC for PSDF funding.

In the 118th PSOC meeting, OHPC stated that rectifications of equipments at Indravati switchyard been included for PSDF funding. Work will be completed by January’2019.
OHPC may deliberate.
C.10: Status of UFRs healthiness installed in Eastern Region

UFR Healthiness Certification for the month of January, 2018 has been received from CESC, WBSETCL, DVC, JUSNL, OPTCL and BSPTCL.

OCC advised OPTCL to change 33kV Laxmipur feeder with suitable feeder of desired load.

In the 118th PSOC meeting, it was decided that SOUTHCO shall identify other feeders having equivalent quantum of load in place of Laxmipur feeder load and submit to O&M for necessary action.

CGM (O&M) / SOUTHCO may please deliberate.

C.11: Approval of outage procedure and Submission of outage request to ERLDC as per procedure.

The procedure for transmission element outage was approved in 87th ERPC meeting. After this some minor modifications in the approved procedure was also done. As per the procedure following need to be adhered by the outage indenting parties while applying OCC approved transmission element outages to ERLDC for approval:

1. Request for outages which are approved by OCC must be sent by the indenting agency of the transmission asset at least 3 days in advance to respective RLDC by 10:00 hours. (For example, if an outage is to be availed on say 10th day of the month, the indenting agency would forward such requests to the concerned RLDC on or before 7th day of the month by 1000 hours.)

2. In case the request for transmission element outage is not received within the timeline prescribed above, it will be assumed that the indenting agency is not availing the outage. However, indenting agency is duty bound to inform ERLDC at least 3 days in advance, if it is not availing the OCC approved outage.

Since last few months it was observed that some of the indenting agencies were deviating from submission dates corresponding to their OCC approval date while submitting their request, which causes a lot of inconvenience to coordinate with multiple agencies and also to carry out system study before approve the outage request. In some cases, indenting agencies were also not intimated ERLDC/ERPC in advance for cancellation of any outage approved in OCC.

Detail outage procedure as on date is updated in ERLDC website.

In the 118th PSOC meeting, it was decided that SLDC & O&M shall examine the outage procedure and forward their comments to ERLDC.

CGM (O&M) / SLDC may please deliberate.

C.12:  Islanding scheme for GMR & IbTPS

In the 118th PSOC meeting CGM (Telecom) stated that Telecom has suggested for laying of optical fibre to implement islanding scheme for IbTPS, which is yet to be done by them. GMR IPP has no islanding scheme at present. Also it was decided that GMR should develop an islanding scheme for their State connected unit.

IbTPS/ GMR / CGM (Telecom) may please deliberate the status

C.13: Accounting of Tertiary Loading Arrangement at PGCIL Grid S/Ss in ER

As per the decision in the 35th CCM meeting of ERPC held on 02.08.2017 “Accounting of Tertiary Loading Arrangement at PGCIL Grid S/Ss in ER” and subsequent ratification in 36th TCC & ERPC meeting held on 13th & 14th September 2017, it was decided that the drawal of auxiliary power from tertiary winding of different Powergrid S/Ss would be treated as State drawal for inter-regional accounting. Powergrid and States would make back to back commercial arrangements for this power.
Accordingly from the following Powergrid S/S auxiliary consumption has been added in Gridco’s drawal from 23.10.2017.

1.Angul(PG), 2. Sundargarh (PG), 3. Pandiabili (PG), 4. Bolangir (PG), 5. Baripada (PG), 6. Jaipur (PG), 7. Keonjhar (PG) and 8. Rengali (PG). For Rourkela (PG) the tertiary drawal has been added from 05.02.2018.

Till date no back to back arrangement has been made between Gridco and Powergrid to account the energy consumption ( 2.60146 MU) which has been added the State’s transmission loss. This has also been intimated to Gridco by SLDC vide letter No. 831 (4) dated 08.03.2018. 
GRIDCO may please deliberate.

PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non compliance of drawal schedule messages issued to Discoms during the month of Feb’18:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	-4.06
	0.701

	2
	WESCO
	0
	-3.962
	0.710

	3
	NESCO
	0
	-2.572
	0.631

	4
	SOUTHCO
	0
	0.789
	0.300

	
	Total
	0
	-9.805
	


It is noticed that only SOUTHCO had overdrawn marginally during the month.
SLDC/ Discoms may please deliberate.
D.2: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl. No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220/132 kV, 100 MVA, Auto- 1 at Duburi
	Main tank severely damaged
	March-2018

	2
	220/132kV, 100MVA  Auto-2  at Bhadrak
	Fire hazard on 31.05.2017
	March-2018

	3
	220/132 kV, 100 MVA Auto-1 at Chandaka
	Oil filtration since 05.02.2018 
	


CGM (O&M) may update the progress.

D.3: Communication issues 
The status of data communication from CGPs as deliberated in the last meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	3
	M/s Rohit Ferrotech
	PLCC established and inspection by Telecom Engineers completed.  Database has already been prepared by OPTCL.    

	4
	VISA
	New RTU installed. Testing to be done.

	5
	Paradeep
	Duburi-Paradeep Line shutdown arranged for drawing OPGW after which data can be displayed. To be completed by January 2018.

	6
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 118th PSOC meeting, GCC stated that a case will be filed against NINL, IRE & Rohit Ferrotech for non compliance of the data communication provision.

GMR Issue
	GMR on line data is available at SLDC but not available directly to ERLDC. GMR entrusted the work on Powergrid.


CGM (Telecom) / GCC / GMR / RT&C may deliberate the status.
D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
O&M may deliberate.
D.5: Software for Deviation charge billing.

Hon’ble OERC may notify “Intra State Deviation settlement and related matters” Regulation at any time. For implementation of the regulation, required software for Deviation Charge billing need to be developed and tested. CGM (IT) may take necessary steps for development of the software.

As decided a committee has been constituted for development of the software in house. The work is in progress. 
In the 117th PSOC meeting IT stated that the software will be ready within a week time.
In the 118th PSOC meeting IT stated that the format is being revised after changing of schedule.

CGM (IT) / SLDC may please deliberate.
D.6.DISCOM Issues

CESU

1. Connectivity of Ransingpur sub-station with Argul for stand by supply for Ransinghpur (connected to Chandaka S/S) from which AIIMs is availing power supply.
2. Wide mismatch of actual drawal and SCADA display data to the tune of +115 MW to -117 MW.
CESU may deliberate
D.7: Rectification / Replacement of Defective Meters at different interface points.

A list of defective meters indicating the defects has been placed in the 116th PSOC meeting wherein OPTCL was requested to take necessary action for checking CT / PT and early replacement of these meters wherever required. O&M proposed to convene a meeting to discuss the issue. The meeting is yet to be convened.

O&M may deliberate the status
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by March’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by March’2018.

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	March’18

	4
	400/220 kV, 2x315 MVA Lapanga S/S
	June’18

	5
	220/33 kV, 2x20 MVA Baliguda S/S
	December’18

	6
	220/33 kV, 2x20 MVA Kalimela S/S
	June’18

	7
	220/33 kV, 2x20 MVA Kasipur S/S
	March’18

	8
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	March’18

	9
	220/33 kV, 2x20 MVA Narasinghpur S/S
	March’18

	10
	220/132 /33 kV, 2x100 MVA Aska S/S
	June’18

	11
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	March’18

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	December’18

	13
	220/132/33 kV Jayapatana S/S(320 MVA)
	December’18

	14
	220/132 kV Pratapsasan S/S(320 MVA)
	March’19

	15
	220/132 kV Kesinga S/S (320 MVA)
	June’18

	16
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	March’18

	17
	132/33 kV Ghense S/S
	March’18

	18
	132/33 kV Dhenkikote S/S 
	Charged on 24.02.2018

	19
	132/33 kV Betanati S/S
	March’18

	20
	132/33 kV Kantabanji S/S
	Charged on 28.02.18 

	21
	132/33 kV R.Udyagiri S/S
	March’18

	22
	132/33 kV Chikiti S/S
	March’18

	23
	132/33 kV Athagarh S/S
	March’18


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. 
CGM (Construction) / DISCOMs may deliberate the status.
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators, the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the 117th PSOC meeting, it was decided that CGM (O&M), OPTCL may direct the E & MR Division, Burla to take up the work.

In the 118th PSOC meeting Sr. G.M, EHT (O&M) Zone-II assured to install the meters soon.

OPTCL / IB TPS may deliberate the status.    
E.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same. Another meeting was proposed to be convened in the month of August’17 to finalize the mechanism of data communication. In the 113th PSOC meeting, it was decided that GRIDCO will take follow up action with all the RE generators to provide real time generation data to SLDC. ERLDC has reminded again to intimate the status.   

A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.
In the 116th PSOC meeting, CGM (Telecom) stated that the solar projects need to pay the SCADA integration charges for display of the data through SCADA.
In the 117th PSOC meeting CGM (Telecom) stated that for pilot project the integration charges may not be required. The Agencies may be asked to proceed with their project.

In the 118th PSOC meeting GRIDCO state that MoM has already been made for 2 Nos. pilot projects and work will be started soon.
Telecom / GRIDCO may deliberate the status.
E.4: Planned outage of 400 kV transmission elements and Inter-State tie lines.
As decided in the OCC meeting that the consolidated planned outage program for all 400 kV lines and Inter-State tie lines shall have be submitted to ERPC for approval in the monthly OCC meeting. The has also been indicated in the procedure at item No C.11 above. CGM (O&M) may please intimate all the GM in charge of (O&M) Circles to prepare the monthly outage programe if any and forward to SLDC for including in the OCC agenda of the State.

CGM (O&M) 
E.5: Disturbance at Tarkera Grid S/S- Interruption of power supply to RSP-Agenda by RSP
On 12th March, 2018, 22:39 Hrs: Tarkera Grid s/s - Auto Tr-4 'R' Phase new 220kV CT of GE make failed within 5 Hrs of commissioning leading to very heavy voltage dip, Islanding of our Power Plants & their unitstripping due to load collapsing.

This was a repettion of new CT failure at Tarkera Grid. On 14-Nov-17 also, Auto Tr-2, R Ph new CT had failed at 00:07 Hrs. leading to wide spread power failure & related disturbance.

In both the incidences, RSP lost almost 14 Hrs worth of production apart from shock to equipments.

E.6: Major Events in the month of February’18
09.02.18: Podagada 132/33 kV, 1x12.5 S/S charged

24.02.18: Dhenkikote 132/33 kV, 1x20 MVA kV S/S charged with radial feeder from Karanjia.

28.02.18: Kantabanji 132/33 kV, 1x40 MVA S/S & Traction feeder idle charged with radial feeder from Kharior.

E.7: Important Grid Incidences during the month of February’18.
On 09.02.2018 at 17:31 hrs  400 kV Meramundali-DuburiCkt-II tripped  at Meramundali on dist-4.8 km, ‘R’ ph to E/F, IR-32.14 kA, On field visit it was found that ‘R’ ph LA burst and fire caught in 400 kV switchyard. 400 kV Meramundali-GMR Ckt tripped at Meramundali on O/C and E/F. At 17:46 hrs it was observed that 50 MVA reactor of 400 kV Meramundali-Vedanta Ckt-I caught fire.

E.8: Outage of major transmission Elements during the month of February’18. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration
Dt/time
	Reason

	1
	132 kV Budhipadar-Lapanga Ckt
	01.01.18

15:30
	02.01.18

12:35
	‘Y’ phJumper snapped at Loc. No-135.


C.G.M. (O&M) may please deliberate.

E.9:  Review of Outage Program of State Generators / Transmission elements for the month of Apr’18:
Tentative Outage programme for State Generators for the month of April’2018 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 2
# 5

# 6
	09.02.18 to 30.04.18
25.10.16 to continue

16.10.15 to continue
	Shaft seal problem
Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
	15.10.15 to continue
	Under R,M & U

	3
	Balimela
	# 1

# 2

# 7
	05.08.16 to continue

20.11.17 to continue

19.03.18 to 18.04.18
	Under R,M & U

Programming for R&M

Governor problem/Breaker replacement 

	4
	Rengali
	# 4
	02.04.18 to 20.05.18
	Annual Maintenance & new DVR erection

	5
	Upper Kolab
	# 2
	28.05.17 to continue
	Upstream leakage & intake gate Problem


OHPC / SLDC may deliberate. 
E.10: Generation Program for the month of April’18.
Generation schedule for the month of April’18 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.03.17
	Reservoir Level as on 01.03.18
	MDDL
	High Flood    Reservoir Level

	
	Apr’18
(1st fortnight)
	Apr’18
(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	45
	45
	622.04 ft 
	 620.97 ft
	590 ft.
	630 ft.

	HPS-II, Chiplima
	35
	35
	-
	-
	-
	-

	Balimela
	240
	240
	1496.40 ft 
	1458.70 ft
	1440 ft.
	1516 ft.

	Rengali
	120
	120
	121.74 mt

1.78mt mtr mt
	121.64 mt mt
	109.72mtr 
	123.5 mtr.

	U.Kolab
	60
	60
	854.88 mt mt
	852.00 mt
	844 mtr 
	858 mtr.

	U. Indravati
	250
	250
	636.88 mt
	634.06 mt mt
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2729.45 ft 
	2744.20 ft
	2685 ft.
	2750 ft.

	TOTAL
	780
	780
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

OHPC / SLDC may deliberate & Members may discuss. 
E.11: Anticipated power generation and demand for the month of Apr’2018.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1100
	1280

	2
	WESCO
	1100
	1250

	3
	NESCO
	750
	900

	4
	SOUTHCO
	450
	550

	6
	Total Discom
	3400
	3980

	
	System Loss & others
	170
	220

	
	Total Demand
	3570
	4200

	Availability
	
	

	1
	Hydro
	800
	1350

	2
	State Thermal
	770
	770

	3
	IPP, small hydro &RE
	650
	650

	4
	ISGS share (including OA)
	1100
	1200

	5
	CGP support (OA)
	250
	250

	6
	Total availability
	3570
	4220

	7
	Surplus / Deficit
	0
	20


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (120th) PSOC meeting.
PAGE  

