                                                                                                                  
Odisha Power Transmission Corporation Ltd.

Bhubaneswar.

[image: image1.png]PTC




Agenda

for

120th Power System Operational Coordination Meeting

Date: 28.04.2018
Venue: PTC, Chandaka, Bhubaneswar 
Odisha Power Transmission Corporation Ltd. Bhubaneswar.
Agenda for 120th PSOC Meeting to be held on 28.04.2018 at PTC, Chandaka, Bhubaneswar
Item no. 1: Confirmation of the minutes of the 119th PSOC Meeting held on 23.03.2018
The minutes of meeting was circulated vide letter No. SGM (PS)-Pl-15/2017/991 (47) dated 30.03.2018 to all the members and also uploaded in the SLDC website. Members may offer their comments. If there is no comment, the minutes of the meeting may please be confirmed.

PART A

(List of items to be discussed for which the details are given in the subsequent parts)
B   : Grid Performance for the month of March’2018
C.1: Status of projects funded under PSDF scheme

C.2: Accounting of State drawal from sub-station ofPGCIL / ISTS Licensee in ER
C.3: Improved telecom infrastructure for cyber security

C.4: Commissioning of breaker at 400/220 kV Indravati (OHPC) S/s

C.5: Controlling over drawal of states by disconnection of radial feeders.

C.6: 220kV Interconnecting line of OPTCL with 400/ 220kV Bolangir PG, Keonjhar & Pandiabil s/s

C.7: Schedule for reactive capability test

C.8: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

C.9: Certification through BIS as per IS 18001:2007 to all generating/ transmission units.

C.10: Status of Disturbance Recorder, stand alone Event Logger & time synchronization equipment

C.11: Implementation of Automatic Demand Management Scheme
C.12: Mock Black start exercise in Eastern Region 

C.13: Implementation of Islanding Scheme.

D.1: Non-compliance of drawal schedule by DISCOMs

D.2: Prolonged outage of transmission elements and tentative revival dates

D.3: Communication issues 
D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

D.5: Web based drawal / generation scheduling 
D.6: Software for Deviation charge billing.
D.7: DISCOM Issues 
D.8: Rectification / Replacement of Defective Meters at different interface points.

E.1: Commissioning status of New Transmission elements. 

E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
E.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.

E.4: Major Events in the month of February’18
E.5: Important grid incidences during the month of February’18.

E.6: Outage of major transmission Elements during the month February’18. (above 10 hrs).
E.7: Review of Outage Program of State Generators for the month of April’2018
E.8: Generation Program for the month of April’2018.
E.9: Anticipated power generation and demand for the month of April’2018.

F.1:  Date and Venue of the next (121st) PSOC meeting
PART B: GRID PERFORMANCE
Review of Grid Performance for the month of March’18.

A. Frequency:

Hourly frequency variation for the month of March’18.
	Month
	% of time frequency remained
	Average

	
	<49.00
	49.00-49.70
	49.70-49.90
	49.90-50.05
	>50.05
	

	Jan’18
	0.00
	0.01
	8.94
	76.51
	14.55
	49.99

	Feb’18
	0.00
	0.00
	7.09
	78.50
	14.41
	49.99

	Mar’18
	0.00
	0.00
	9.39
	78.69
	11.92
	49.98


Maximum & Minimum frequency during the month of March’18.
	Month
	Freq (Hz)
	Date
	Time

	Feb’18
	Maximum –50.12
	16.02.18
	13:00 Hrs

	
	Minimum – 49.78
	23.02.18
	06:30 Hrs

	March’18
	Maximum –50.11
	31.03.18
	07:00 Hrs

	
	Minimum – 49.78
	26.03.18
	15:15 Hrs


Members may please discuss.

B. Grid Demand up to the month of March’18
	 Month
	Max. Consumption
	Demand
	Maximum Demand
	Minimum Demand

	
	MU
	Date
	MU
	Avg. (MW)
	MW
	Date
	Time 
	MW
	Date
	Time 

	April’17
	88.91
	27.04.17
	2493
	3463
	4299
	26.04.17
	24:00
	2466
	03.04.17
	07:00

	May’17
	88.13
	23.05.17
	2534
	3406
	4281
	04.05.17
	24:00
	2553
	06.05.17
	23:00

	June’17
	82.72
	03.06.17
	2269
	3151
	4009
	04.06.17
	24:00
	2091
	15.06.17
	18:00

	July’17
	86.54
	06.07.17
	2437
	3276
	4233
	05.07.17
	20:00
	2596
	23.07.17
	14:00

	Aug’17
	85.74
	26.08.17
	2500
	3360
	4269
	26.08.17
	24:00
	2647
	17.08.17
	16:00

	Sept’17
	93.49
	16.09.17
	2566
	3567
	4375
	26.09.17
	21:00
	2523
	12.09.17
	17:00

	Oct’17
	91.78
	13.10.17
	2655
	3569
	4491
	23.10.17
	20:00
	2763
	20.10.17
	06:00

	Nov’17
	79.46
	28.11.17
	2116
	2938
	4158
	01.11.17
	19:00
	2231
	24.11.17
	15:00

	Dec’17
	77.95
	28.12.17
	2171
	2919
	4230
	27.12.17
	21:00
	2057
	09.12.17
	04:00

	Jan’18
	84.87
	29.01.18
	2311
	3107
	4251
	28.01.18
	20:00
	2244
	04.01.18
	04:00

	Feb’18
	83.37
	21.02.18
	2194
	3265
	4211
	12.02.18
	20:00
	2241
	16.02.18
	15:00

	Mar’18
	94.20
	29.03.18
	2595
	3487
	4515
	29.03.18
	20:00
	2606
	02.03.18
	15:00

	Mar’17
	83.52
	28.03.17
	2361
	3173
	4064
	29.03.17
	21:00
	2301
	11.03.17
	04:00


C. Voltage Profile of 220 kV Buses in OPTCL system for the month of: March’18
	Sl. No
	S/s Name
	Maximum
	Minimum

	
	
	kV
	Day
	Time
	kV
	Day
	Time

	1
	Atri
	228.51
	17
	3:15
	206.22
	21
	18:45

	2
	Balasore
	230.59
	31
	17:30
	208.65
	28
	19:00

	3
	Barkote
	232.26
	2
	14:45
	223.83
	21
	18:45

	4
	Bhadrak
	232.67
	1
	4:30
	200.39
	28
	19:15

	5
	Bhanjanagar
	231.97
	17
	3:15
	212.29
	21
	18:45

	6
	Bidanasi
	233.47
	2
	15:00
	215.06
	21
	15:30

	7
	Bolangir
	225.28
	16
	16:00
	210.38
	21
	18:30

	8
	Budhipadar
	232.43
	13
	14:30
	220.66
	24
	19:15

	9
	Chandaka
	229.20
	17
	3:15
	206.34
	21
	18:30

	10
	Cuttack
	230.93
	2
	15:00
	212.11
	21
	15:30

	11
	Duburi(O)
	233.99
	1
	13:45
	219.62
	21
	19:00

	12
	Duburi (N)
	222.79
	1
	13:45
	209.92
	28
	18:45

	13
	Jayanagar
	236.53
	17
	3:15
	218.17
	10
	15:30

	14
	Joda
	232.20
	2
	13:30
	218.17
	29
	20:45

	15
	Katapalli
	227.07
	16
	14:30
	218.12
	26
	19:00

	16
	Lapanga
	229.72
	3
	3:45
	223.02
	26
	19:00

	17
	Laxmipur
	237.51
	31
	18:00
	217.54
	10
	15:30

	18
	Mendhasal
	230.41
	17
	3:45
	207.84
	21
	18:45

	19
	Meramundali
	228.62
	2
	14:00
	220.83
	21
	18:45

	20
	Narendrapur
	228.85
	17
	3:15
	200.39
	21
	18:45

	21
	Nayagarh
	229.43
	17
	3:15
	207.96
	21
	18:45

	22
	Paradeep
	227.70
	2
	3:30
	208.01
	21
	19:00

	23
	Tarkera
	233.65
	2
	14:45
	223.43
	21
	18:45

	24
	Theruvali
	237.17
	31
	18:00
	217.71
	23
	13:15


The maximum Voltage of 237.51 kV occurred at Laxmipur 220 kV bus, while Narendrapur & Bhadrak 220 kV bus has experienced the minimum Voltage of 200.39 kV. The 220 kV Voltage profile of Jayanagar and Narendrapur and 400 kV Voltage profile of Meramundali  and New Duburi bus during the month of January 2018 is shown below.
[image: image2.emf]200

205

210

215

220

225

230

235

240

00:00 00:45 01:30 02:15 03:00 03:45 04:30 05:15 06:00 06:45 07:30 08:15 09:00 09:45 10:30 11:15 12:00 12:45 13:30 14:15 15:00 15:45 16:30 17:15 18:00 18:45 19:30 20:15 21:00 21:45 22:30 23:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NARENDRAPUR 220 kV BUS

FOR MARCH 2018


[image: image3.emf]200

205

210

215

220

225

230

235

240

245

250

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF  JAYANAGAR 220 kV BUS 

FOR MARCH 2018


[image: image4.emf]390

395

400

405

410

415

420

425

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF MERAMUNDALI 400 kV BUS FOR 

MARCH 2018


[image: image5.emf]390

395

400

405

410

415

420

425

430

00:0000:4501:3002:1503:0003:4504:3005:1506:0006:4507:3008:1509:0009:4510:3011:1512:0012:4513:3014:1515:0015:4516:3017:1518:0018:4519:3020:1521:0021:4522:3023:15

Voltage In kV

Time In Hrs

VOLTAGE PROFILE OF NEW DUBURI 400 kV BUS 

FOR MARCH 2018


Members may discuss.
D. Loading of 220/ 132 kV Auto at  220 kV S/Ss in OPTCL system for the month of Mar’18
[image: image6.emf]AUTO TRANSFORMER LOADING FOR THE MONTH OF  MARCH'2018

Name of the 220 kV Sub-Station Capacity REMARKS

( Feeding Sub-stations/Feeders )

MVA MW Day Time MW Day Time

109.40 28 21:00 44.32 18 09:15

90.36 20 12:50 44.12 18 09:15

109.92 28 21:00 44.68 18 09:15

1x100 54.72 23 18:30 8.48 24 17:45

1x160 97.72 23 18:30 7.12 1 04:30

YET TO BE COMMISSIONED

1x160 79.84 1 17:45 27.40 8 10:00

1x160 70.56 1 17:45 24.08 8 10:00

1x160 40.56 5 18:45 6.52 5 05:00

1x100 29.08 5 18:45 4.36 5 05:00

1x100 23.60 28 08:45 3.76 29 01:30

2x160 131.84 18 19:00 38.20 11 13:00

139.52 18 19:00 40.32 11 13:00

100.08 30 13:30 35.64 14 09:00

91.60 22 19:30 17.88 9 10:15

1x100 69.32 28 15:45 26.40 24 00:00

1x160 123.72 23 19:15 18.36 28 12:15

1x100 76.88 23 19:15 18.36 28 12:15

1x160 115.32 28 15:45 15.08 23 12:15

CUTTACK 1x160

59.80

20 12:00 13.76 6 09:30

Under shut down

61.60 22 18:15 6.56 28 08:30

58.76 22 18:15 6.32 28 08:30

1x160 129.36 26 09:30 19.76 31 18:45

1x160 81.00 5 19:15 19.92 31 18:45

54.88 24 19:15 28.04 21 14:00

54.92 24 19:15 28.36 21 14:00

54.96 24 19:15 28.60 21 14:00

1x100 29.32 9 16:45 3.72 10 23:45

1x100 29.40 9 16:45 3.68 10 23:45

1x160 44.00 9 16:45 5.64 10 23:45

1x160 61.20 22 18:45 28.40 16 05:30

60.96 22 18:45 28.28 16 05:30

38.72 1 18:45 5.52 12 17:15

38.12 1 18:45 5.56 12 17:15

37.00 1 18:45 4.88 12 17:15

2x100 25.20 30 15:15 7.80 28 12:00

43.20 29 09:15 11.40 2 12:00

2x160 102.84 27 20:15 31.32 1 14:30

102.56 27 19:15 31.32 1 14:30

1x100 59.04 27 20:15 17.76 1 14:30

1x160 105.92 27 20:45 13.44 1 06:30

1x100 64.60 27 10:48 8.36 1 06:30

1x50

4x100  63.08 13 06:15 4.24 23 10:15

64.36 12 17:15 11.40 16 05:00

63.16 13 06:15 10.72 16 05:00

55.40 23 10:15 11.28 16 05:00

2x100 85.96 4 19:00 38.44 22 10:30

81.12 4 19:00 36.72 22 10:30

1x160  110.00 25 13:00 1.00 17 21:00

1x160 110.00 25 13:00 1.00 17 21:00

2x160 47.84 19 18:00 3.16 20 07:45

47.96 19 18:00 3.20 20 07:45

1x100

KATAPALI 220/132 KV

{Chipilima,Bargarh, ACC,Sonepur & 

Katapali area load.}



DUBURI 220/132 KV 

{Duburi, Bamnipal(I), BRPL, MESCO, 

Jajpur Road, Kalarangi, Jajpur Town}

Mendhasal { Part area load of Khurda S/S}

MERAMUNDALI 220/132 kV

{Meramundali Traction, Dhenkanal, 

Navchrome(I), Hind Metal, Aarti,BRG}

3x100



CHANDAKA 220/132 KV

{ Chandaka, Bhubaneswar, Nimapada, 

Ransinghpur, Puri,Kesura, Kaipadar Tr. }

JAYANAGAR 220/132 KV.

[Damanjodi(NALCO), Traction S/Ss,

Tentulikhunti, Sunabeda, Jayanagar]



"*" - Alternate P/S from 

Kuchei.



BUDHIPADAR 220/132 KV

{ Jharsuguda, Jharsuguda Tr, Cemco(I), 

MCL, Sundergarh,Brajarajnagar, 

Rajgangpur}

2x160 

BHADRAK 220/132 KV

{Bhadrak area load, Bhadrak(T),Soro,  

FACOR (I), Dhamra Port}

LAPANGA                                             

{Kuchinda, Aryan Viraj, Shyam Metallics}

TARKERA 220/132 KV

[ Rourkela, Rourkela Tr.,RSP(I), Chhend , 

Adhunik Metal,  Rajgangpur, OCL(I), 

Rajgangpur Tr.] 

BOLANGIR (SADAIPALLI)  220/132 KV

{ Bolangir, Patnagarh, Sonepur, Saintala, 

Khariar, Barpalli }

SAMANGARA                                          

{ Puri, Nimapara & Konark}

NARENDRAPUR 220/132KV

{ Narendrapur, NarendrapurTr, Berhampur, 

Chhatrapur, Ganjam, Balugaon, 

Digapahandi, Mohana.}

THERUVALLI 220/132 KV.

{Theruvali, IMFAL(I), JK(I), Junagarh, 

Kesinga,Powmex(I), Rayagada, }

Rayagada & Paralakhemundi 

can be fed from Machhkund 

system.

ATRI                                                     

{Banki, Khurda, Chandpur & Argul}

Supported by Burla & 

Chipilima power.

PARDEEP 220/132 KV

{ Paradeep, Kendrapada, Pattamundai, 

Chandikhol, Cuttack, Jagatsinghpur, 

Phulnakhara}



TTPS  220/132 KV

{ Chainpal, FCI (I), Angul, MCL Nandira(I), 

Rairakhole,Boinda,Kamakhyanagar,

Kalarangi,Nuapatna, Choudwar } 



JODA 220/132 KV

{ Joda,Tensa, FAP(I), Bolani(I), Nalda 

Tr.,Polasponga, *Rairangpur, Bhalulata 

traction}

BIDANASI 220/132 KV

{Bidanasi, Khurda }

3x100 

3x100 

BHANJANAGAR 220/132 KV

{ Bhanjanagar, Aska, Phulbani, Ganjam, 

Chatrapur}

3x160 



BALASORE 220/132 KV

{ Balasore, Birla Tyre(I), Ispat Alloy(I), 

Jaleswar, Jaleswar(T)}

Drawal details

Maximum Minimum


E. DISCOM Drawal up to the month of March’18
	Name of DISCOM
 
	Month


	Approved Energy Drawal Prorated for the month (MU)
	Scheduled Energy (MU)
	Actual Energy Drawal 
( MU)
	Open Access Import Schedule
(MU)
	Net Energy Drawal 
( MU)
	Overdraw (MU) 

	
	
	1
	2
	3
	4
	5=(3-4)
	6=(5-2)

	CESU
	April’17
	727.397
	760.945
	789.421
	17.199
	772.222
	11.277

	
	May’17
	751.644
	839.125
	871.775
	20.892
	850.883
	11.758

	
	June’17
	727.397
	750.856
	775.766
	20.502
	755.264
	4.408

	
	July’17
	751.644
	726.897
	761.921
	20.064
	741.857
	14.96

	
	Aug’17
	751.644
	765.985
	793.287
	17.844
	775.443
	9.458

	
	Sept’17
	727.397
	730.617
	768.066
	17.257
	750.809
	20.192

	
	Oct’17
	751.644
	734.68
	758.409
	15.23
	743.179
	8.499

	
	Nov’17
	727.397
	596.681
	610.336
	13.696
	596.64
	-0.041

	
	Dec’17
	751.644
	555.67
	584.551
	20.324
	564.227
	8.557

	
	Jan’18
	751.644
	570.873
	593.97
	20.482
	573.488
	2.615

	
	Feb’18
	678.904
	578.615
	593.582
	17.464
	576.118
	-2.497

	
	Mar’18
	751.644
	776.413
	790.308
	22.080
	768.228
	-8.185

	WESCO
	April’17
	582.74
	637.3
	692.208
	54.234
	637.974
	0.674

	
	May’17
	602.164
	626.029
	675.458
	38.953
	636.505
	10.476

	
	June’17
	582.74
	557.308
	597.211
	41.282
	555.929
	-1.379

	
	July’17
	602.164
	577.765
	734.199
	154.21
	579.989
	2.224

	
	Aug’17
	602.164
	622.033
	689.155
	70.539
	618.616
	-3.417

	
	Sept’17
	582.74
	628.342
	843.984
	202.065
	641.919
	13.577

	
	Oct’17
	602.164
	639.382
	922.703
	284.197
	638.506
	-0.876

	
	Nov’17
	582.74
	547.045
	601.11
	56.681
	544.429
	-2.616

	
	Dec’17
	602.164
	579.696
	709.064
	126.074
	582.99
	3.294

	
	Jan’18
	602.164
	605.119
	790.905
	190.803
	600.102
	-5.017

	
	Feb’18
	543.89
	557.519
	785.650
	265.990
	519.66
	-37.859

	
	Mar’18
	602.164
	647.520
	790.512
	184.908
	605.604
	-41.916

	NESCO
	April’17
	466.849
	493.551
	597.753
	108.907
	488.846
	-4.705

	
	May’17
	482.411
	468.854
	578.963
	114.176
	464.787
	-4.067

	
	June’17
	466.849
	432.223
	548.642
	109.141
	439.501
	7.278

	
	July’17
	482.411
	446.662
	556.119
	102.767
	453.352
	6.69

	
	Aug’17
	482.411
	494.041
	595.207
	100.708
	494.499
	0.458

	
	Sept’17
	466.849
	475.21
	589.343
	103.64
	485.703
	10.493

	
	Oct’17
	482.411
	458.363
	577.417
	93.521
	483.896
	25.533

	
	Nov’17
	466.849
	425.376
	528.517
	104.689
	423.828
	-1.548

	
	Dec’17
	482.411
	416.019
	510.678
	95.552
	415.126
	-0.893

	
	Jan’18
	482.411
	426.851
	529.108
	103.001
	426.107
	-0.744

	
	Feb’18
	435.726
	407.243
	487.587
	80.556
	407.031
	-0.212

	
	Mar’18
	482.411
	482.741
	583.541
	101.714
	481.827
	-0.914

	SOUTHCO
	April’17
	289.315
	303.102
	305.398
	0.651
	304.747
	1.645

	
	May’17
	298.959
	308.789
	314.808
	0.213
	314.595
	5.806

	
	June’17
	289.315
	279.684
	276.185
	0.433
	275.752
	-3.932

	
	July’17
	298.959
	294.376
	294.742
	0.629
	294.113
	-0.263

	
	Aug’17
	298.959
	310.404
	307.768
	0.391
	307.377
	-3.027

	
	Sept’17
	289.315
	294.522
	292.885
	0.074
	292.811
	-1.711

	
	Oct’17
	298.959
	290.344
	292.58
	0.052
	292.528
	2.184

	
	Nov’17
	289.315
	267.085
	265.471
	0.081
	265.391
	-1.694

	
	Dec’17
	298.959
	271.068
	270.844
	0.265
	270.579
	-0.489

	
	Jan’18
	298.959
	281.023
	281.141
	0.025
	281.116
	0.093

	
	Feb’18
	270.027
	262.415
	263.204
	0
	263.204
	0.789

	
	Mar’18
	298.959
	325.302
	326.177
	0
	326.177
	0.875


The figures are as per EBC data. Energy drawal by SOUTHCO are excluding of energy consumed by NALCO at Damanjodi and IMFA at Theruvali. 
Members may please discuss.
F. Energy Generation / Import up to the month of March’18
Figures in MU  

[image: image7.emf]OHPC

& MKD

Apr’17

514.91 581.71 323.53 349.53 17.70 705.86 2493.24

May’17

543.19 647.85 296.06 212.84 10.45 823.85 2534.24

June’17

548.07 610.00 358.88 203.70 10.17 537.95 2268.77

July’17

554.18 688.13 190.09 140.71 10.46 853.89 2437.46

Aug’17

442.30 746.49 281.20 167.14 10.06 853.01 2500.20

Sept’17

363.01 731.72 189.82 173.94 9.45 1091.74 2559.68

Oct’17

453.38 572.67 155.32 152.27 35.85 1311.67 2681.16

Nov’17

433.21 263.48 209.28 79.27 9.31 1121.06 2115.61

Dec’17

554.44 189.28 223.23 122.73 10.44 1061.73 2161.85

Jan’18

545.32 236.10 360.28 301.68 9.93 858.09 2311.40

Feb’18

515.05 270.16 247.77 156.54 9.34 994.90 2193.76

Mar’18

571.04 373.57 318.67 151.62 10.31 1169.34 2594.55

Total

6038.10 5911.16 3154.13 2211.97 153.47 11383.09 28851.92

ISGS Total Month Thermal 

(TTPS+IB)

CGP 

Support

IPP 

Support

Renewable


G.  Drawal of Machhakund Power
The drawal of Machhakund power up to the month of March’18 are as detailed:

[image: image8.emf]MU MW MU MW MU MW

Apr’17

65.96 91.61 32.32 44.89 30.95 42.99

May’17

65.53 88.08 29.08 39.08 33.83 45.47

June’17

45.68 63.44 19.51 27.10 24.11 33.48

July’17

33.21 44.64 15.06 20.24 16.23 21.82

Aug’17

51.80 69.62 24.45 32.86 25.22 33.90

Sept’17

39.02 54.19 18.14 25.19 19.07 26.49

Oct’17

34.35 46.17 16.51 22.19 16.16 21.73

Nov’17

25.18 34.97 8.70 12.08 14.89 20.67

Dec’17

38.40 51.61 18.61 25.02 17.89 24.05

Jan’18

38.90 52.29 19.62 26.37 17.40 23.38

Feb’18

34.55 51.41 17.43 25.94 15.47 23.02

Mar’18

41.53 55.82 20.30 27.29 19.34 26.00

Total

514.10 58.65 239.72 27.35 250.56 28.58

Month Total Generatuion Odisha Drawal AP Drawal


In the 118th PSOC meeting, O&M stated that Machhakund drawal shall be increased after drawal of power from Podagada S/S by SOUTHCO. 

In the 119th PSOC meeting Sr. G.M SLDC stated that there is no matching load available, in case more Nos of Machhakund units synchronized. Southco may explore their takeoff arrangement from newly commissioned Podagada 132/33 kV S/S to increase Machhakund drawal of the State. 

SOUTHCO may deliberate.
H. Under Frequency Relay operation in OPTCL System during the month of March’18.

Since, the frequency had never gone beyond the lowest setting of UFR, there was no UF Relay operation occurred during the month of March’18.
I. Status of Open Access applications up to the month of March’2018
The status of different types of Open Access applications received and disposed by SLDC is as tabled.
	Sl. No
	Month
	No of Applications received
	No of Applications Disposed
	No of App. Rejected

	
	
	Intra-State
	Inter-State
	Total
	Intra-State
	Inter-State
	Total
	

	
	
	
	Bilateral
	PXI
	
	
	Bilateral
	PXI
	
	

	
	
	
	ST
	MT/

LT
	
	
	
	ST
	MT/

LT
	
	
	

	1
	April’17
	21
	71
	0
	29
	121
	20
	71
	0
	28
	119
	2

	2
	May’17
	12
	31
	0
	32
	75
	12
	29
	0
	25
	66
	9

	3
	June’17
	23
	56
	0
	58
	137
	23
	56
	0
	40
	119
	18

	4
	July’17
	20
	85
	0
	36
	141
	20
	85
	0
	26
	131
	10

	5
	Aug’17
	9
	113
	0
	37
	159
	7
	110
	0
	31
	148
	11

	6
	Sept’17
	17
	140
	0
	52
	209
	15
	140
	0
	41
	196
	13

	7
	Oct’17
	17
	112
	0
	35
	164
	16
	112
	0
	32
	160
	4

	8
	Nov’17
	17
	51
	0
	39
	107
	15
	51
	0
	32
	98
	9

	9
	Dec’17
	34
	124
	0
	40
	198
	33
	124
	0
	35
	192
	6

	10
	Jan’18
	16
	84
	0
	35
	135
	16
	84
	0
	32
	132
	3

	11
	Feb’18
	27
	81
	0
	32
	140
	24
	80
	0
	29
	133
	7

	12
	Mar’18
	8
	72
	0
	31
	111
	7
	71
	0
	27
	105
	6

	
	Total
	221
	1020
	0
	456
	1697
	208
	1013
	0
	378
	1599
	98


PART C – Issues discussed in the 144rd  OCC meeting of ERPC held on 19.04.2018
C.1: Status of projects funded under PSDF schemes

In the PSDF review meeting, it was advised to RPCs to monitor the status of all the projects funded by PSDF. Therefore, constituents are requested to update the status of projects which are being funded by PSDF in the desired format.

The latest status as updated by OPTCL / OHPC is as given below:
	Sl No


	Name of

Constituent
	Name of Project
	Date of approval from PSDF
	Target Date of Completion
	PSDF grant
Approved (in Rs.)
	Amount

Drawn till date (in Rs.)
	Status as updated in
129th meeting

	4
	OPTCL
	Renovation & Up-gradation of protection and control systems of Sub-stations in the State of Odisha in order to rectify protection related deficiencies.
	10.05.15
	30.11.18
	162.5 Cr.


	37.79Cr.
	Total contract awarded for

Rs. 51.35 Cr



	7
	
	Implementation of OPGW based reliable communication at 132kV and above substations
	15.11.2017
	
	25.61 Cr
	
	Agreement signed on 03.01.2018

	13
	OHPC
	Renovation & up-gradation of protection & control system of 4 nos. OHPC sub-stations
	
	U.Kolab-

March 19

Balimela-

Feb 2019

U.Indravati-Jan 19

Burla-Nov

2018,

Chiplima

Dec 2018
	22.35 Cr.
	
	Tendering under process

	Projects under process of approval:

	
	OPTCL 
	Installation of 125 MVAR Bus Reactor along with construction of associated bay each at 400kV Grid S/S of Mendhasal, Meramundali & New Duburi for VAR control & stabilisation of system voltage 


	28-08-17
	
	31.94 Cr
	
	Scheme was examined by TSEG. Inputs sought from entity.  OPTCL submitted the relevant information

	Projects recently submitted:

	
	OPTCL 
	Implementation of Automatic Demand Management System (ADMS) in SLDC, Odisha 


	22-12-17
	3.26 Cr
	
	
	

	
	OPTCL 

.
	Protection upgradation and installation of SAS for seven numbers of 220/132/33kV Grid substations (Balasore, Bidanasi, Budhipadar, Katapalli, Narendrapur, New-Bolangir & Paradeep).  
	20.02.2018 
	41.1 Cr
	
	
	


In the 116th PSOC meeting, OPTCL stated that they are linking another project for funding through 
PSDF and the target date will be changed. The revised target date for completion will be intimated to ERPC. Further, technical specification for 400 kV bus reactors at Meramundali S/S is yet to be prepared. It was suggested that CPC may expedite the same.

In the 117th PSOC meeting, O&M deliberated that 400 kV bus Reactor for Meramundali S/S shall be procured after getting sanction by PSDF. 

In the 119th PSOC meeting OHPC stated that the status remained same.
CGM (O&M) / OHPC / SLDC may please update the status.
C.2: Accounting of state drawl from Substation of PGCIL/ISTS Licensee in ER 

 State net drawl from Substation of PGCIL/ISTS Licensee in ER is being computed considering meter installed at feeders on LV side of Transformer due to the fact that for a few ICTs, multiple states used to draw through same ICT. Further, Sub stations where auxiliary requirement is met through tertiary of the IST ICT, States net drawl is computed by adding drawl through feeders after LV side of Transformer and auxiliary consumption through tertiary. Presently with network strengthening and re-configuration in ER, such case of multiple State/entity drawing power from same ICT of PGCIL/ISTS License does not exist anymore.  

As per Clause 7(1) (C) of CEA (Installation and Operation of Meters) Regulations, 2006 & its subsequent amendments, Main Meters for drawl computation through ICT should be installed on HV side of ICT and meters installed on LV side of ICT should be considered as Standby meters. 

In view of the above it is proposed that Sate drawl from PGCIL/ISTS Licensee S/S may be computed by using the meter installed on HV side of ICTs in line with CEA regulation.  

In order to enable ERLDC compute the state drawl through ICTs of PGCIL & other ISTS Licensees in ER as per CEA Regulations, PGCIL is requested to install meters at HV and LV side of ICTs at the stations enclosed at Annexure-B4.  

GRIDCO may please note.  

C.3:  Improved telecom Infrastructure for cyber security 

In 142nd OCC, ERLDC informed that, in line with Enquiry Committee Recommendation, cyber security audit is being conducted on regular basis for SCADA system installed at ERLDC and SLDC as well but cyber security audit for telecom infrastructure installed in Eastern Region is not being carried out.  

OCC advised all the constituents to conduct the cyber security audit on telecom infrastructure installed in Eastern Region. It is further advised that compliance / mitigation of the points observed during the audit should also be completed for improvement of the telecom infrastructure in ER. 

MS, ERPC informed that a presentation on Cyber Security in Power Sector is also planned to be conducted at 37th TCC/ERPC meeting. 

OCC referred the issue to TCC for further deliberation.  

In 37th TCC meeting, it was decided that a workshop would be conducted by CEA at ERPC for further benefit of ER Constituents.  

As suggested by CEA, a format would be circulated among ER constituents for furnishing the information of the their respective systems for discussion in OCC Meeting. The format is enclosed at Annexure-B5. 

OCC advised all the constituents to submit the information to ERPC as per Annexure-B5.  

It was informed that a workshop would be held at ERPC, Kolkata in April 2018 for for further benefit of ER Constituents.  

CGM (Telecom) may discuss.  
C.4: Methodology for Submitting the Status of New Transmission Elements/ Generating Units to be commissioned within the State 

For clear visibility of the Eastern Region networks and better system operation, all the new transmission elements (ISTS & STU links) need to be updated regularly. The commissioning of new transmission elements of ISTS lines has been processed and updated by RLDC whereas commissioning of STU lines has been processed by SLDCs. However, commissioning status of new STU lines of states has not been updated to ERLDC and ERPC regularly. Sometime SLDCs used to submit the status of their new commissioning of elements during OCC meeting. To regularize the process following methodology need to be adopted: 

1.  Transmission elements/ Generating units expected to be commissioned during next month need to be submitted to ERLDC/ERPC in every OCC. 
2.  Detail parameters of new transmission element before commissioning need to be shared with RLDC. 
3.  Detail date and time of synchronization need to be updated on real time to ERLDC after commissioning of any new Transmission element/Generating unit. 
4.  SLDC SCADA team needs to configure the new element in their SCADA and share the same to ERLDC SCADA for network update. 
5.  List of the new transmission elements/ generating units commissioned during  last month need to inform RLDC/RPC within 7th day of the current month, so that same to be updated in OCC. 

In 141st OCC, all the constituents were advised to submit the information within 7th day of the month to following mail ids: 

 erldcam@gmail.com 
 ftcer@posoco.in 
 mserpc-power@nic.in 

To maintain harmonization, all the states and transmission licensees are request to submit the details to ERLDC/ERPC in the following format: 

Monthly commissioning List of Transmission element and generators: Previous Month 

	Sl No
	Element Name
	Owner
	Charging Date
	Charging Time
	Remarks (conductor type/spec/expected load/any other)

	
	
	
	
	
	


Expected commissioning List of Transmission element and generators: Next Month 

	Sl No
	Element Name
	Owner
	Charging Date
	Charging Time
	Remarks (conductor type/spec/expected load/any other)

	
	
	
	
	
	


The matter was deliberated in last OCC meetings, wherein all states and transmission licensees agreed to submit the list of transmissions elements synchronized for the first time during last month within 7th day of the current month to ERLDC through mail. However, in April2018ERLDC received information regarding new elements commissioned in Mar-18 only from West Bengal. Other states and transmission licensees did not submit both List of Transmission element and generators synchronized in the previous Month and List of Transmission element and generators expected to be synchronized during next Month. 
CGM (Constrution) / CGM (O&M) may please note

C.5: Commissioning of breakers at 400/220 kV Indravati (OHPC) S/s 
In 141st OCC, it was explained that 3x105 MVA 400/220 kV ICT-I tie breaker, 220 kV Bus coupler and transfer bus breakers are not in service at 400/220 kV Indravati (OHPC) S/s.
In 142nd OCC, OHPC submitted the action plan as follows:

1. 220kV bus coupler: CB and CT needed to be replaced. They would restore the Bus coupler by August 2018
2. 220 kV Bus tie: CB and CT needed to be replaced. They would restore the Bus tie by November 2018.
3. 400 kV Tie-1 Breaker: CB and CT needed to be replaced. They would restore the 400 kV Tie by January 2019.
OCC opined that the target dates given by OHPC for replacement of CT and Breaker is too long and advised to take serious action to complete the work at the earliest.
OHPC may deliberate.

C.6: Controlling over drawal of states by disconnection of radial feeders -ERLDC 

In accordance with IEGC sections 5.4.2 (c) and 5.4.2 (f), feeders for disconnecting demand of every state in the order of their priority for switching off, were identified in the past. However, with growth of network interconnection and load as well as change of load distribution (if any) during the intervening period, it is felt that the list  needs reviewing.   

All constituents are requested to furnish views regarding their respective identified feeders and indicate the expected load (average and peak) that would be disconnected by switching off the feeders, so that the list can be finalized at the earliest. 

The updated list is as below.  

 
Odisha System 

Priority 
Feeders/ICTs 




Point of Disconnection 

1 
220 kV Rengali(PG)-Rengali(OPTCL) 
220 kV Rengali-PG 

2 
220/132 kV Baripada 160 MVA ICT 
220 kV Baripada-PG 

3 
220 kV Baripada(PG)-Balsore (Odisha) 
220 kV Baripada-PG 

Intra-state Feeders 




Remarks 

132kV Bolangir(New)-Patnagarh S/C 

132kV Chhatrapur – Ganjam S/C 

132kV Bhanjanagar-Phulbani S/C 

132kV Chandaka-Nimapara / Ranasighpur 

132kV Baripada(PG)-Jaleswar/Bhograi 

132kV Jajpur Rd. – Kendrapara D/C 

In 142nd OCC, all constituents were advised to indicate the average and maximum load relief expected on disconnection of the identified intra-state / tie lines. 

In 143rd OCC, OPTCL informed that 132kV Chatrapur-Ganjam S/c line could be deleted from the list. 

OCC advised all the constituents to submit the details of average and maximum load relief expected on disconnection of the identified intra-state / tie lines.  

OPTCL may update.
C.7: 220 kV inter-connecting lines of OPTCL with 400/220 kV Bolangir (PG), Keonjhar & Pandiabil S/s
PGCIL has already commissioned the 2 X 315MVA 400/220kV Bolangir S/s by LILOing of 400 kV Meramandali-Jeypore S/C line and 400/220 kV Keonjhar S/s with an objective of supplying power from ER grid to its adjoining areas in Odisha.
In 119th PSOC meeting the status has been updated as follows:
	Sl. 
	Name of the transmission line
	Completion schedule

	1.
	2 X 315MVA 400/220kV Bolangir S/s

	a.
	LILO of one circuit of Sadeipalli-Kesinga 220 kV D/C line at Bolangir (PG) S/S.
	Construction of 220 kV Sadeipali- Kesinga line has started. Expected by June’18. 220 kV Sadeipali-Bolangir (PG) portion of the line is expected by June’18. 

	2.
	400/220 kV Keonjhar S/S.

	a.
	Keonjhar (PG)-Keonjhar (220/33 kV) 220 kV D/C line
	Keonjhar S/S (220/33 kV) by April’18.

	b.
	Keonjhar (PG)-Turumunga (220/132 kV) 220 kV D/C Line.
	By 2019

	3.
	400/220 kV Pandiabil Grid S/s

	a.
	Pratapsasan(OPTCL)-Pandiabil (PG) 220 kV D/C line
	December 2018 


CGM (Const.) may please deliberate.
C.8: Schedule for reactive capability tests
In last OCC, Members updated the status and informed the schedule as follows

· GMR (Three units)- It was informed that Grid conditions are not supporting for testing of the unit. TCC advised GMR to discuss the issue in 143th OCC meeting scheduled to be held on March 2018.
ERLDC informed that the unit to be tested need not operate at full load. Xxxxxxx The power stations may therefore select the date and period of testing as per their convenience.

GMR may deliberate

C.9: Preparation of crisis management plan for Cyber Security in Power Sector in line with CERT-IN.

The activity of the preparation of Crisis Management Plan for countering the cyber attacks and its implementation including the Mock Drills, audits etc. is being monitored by CEA regularly in line with crisis management plant of Ministry of Power. Power Utilities (including generation, transmission & distribution utilities) of eastern region are to furnish regularly, the updated status to Chief Engineer, Distribution Planning & Development Division, CEA. NTPC communicated their activity of the preparation of Crisis Management Plan for countering the cyber attacks vide letter dated 2nd August, 2013.

In the 107th PSOC meeting, CGM (IT) informed that “Crisis management plan” work is awarded to M/s Digital Age Strategies Pvt. Ltd. The said firm has completed the study of Servers and Firewalls at SLDC, Bhubaneswar and back-up SLDC at Meramundali. Presently the data centers of SLDC and GRIDCO are being audited for IT security vulnerability assessment.

In the 117th PSOC meeting, CGM (IT) stated that audit has been completed and “ISO 270001 certificate”. Certificate has been issued conditionally for one year. In case OPTCL fails to fulfill the conditions, the period may not be extended. However, the audit report is yet to be received by IT.

In the 118th PSOC meeting, CGM (IT) stated that certificate is expected by end of February’2018.
In the 119th PSOC meeting CGM (IT) stated that the Audit report and Certificate is yet to be received.
CGM (IT) / Telecom may please deliberate.
C.10: Certification through BIS as per IS 18001:2007 to all generating / transmission units.
In 84th OCC meeting all constituents were requested to interact with BIS with intimation to ERPC and get certified as per CEA direction.

In the 111th PSOC meeting CGM (O&M) stated that 22 nos of officers are nominated from Chandaka, Mendhasal, Atri, Kesura, Bidanasi & Cuttack S/Ss to undergo training. Awareness training shall be started from 1st week of August’17. After receiving the price offer, order will be placed. 

In the 113th PSOC meeting CGM (O&M) stated that certification for 6 Nos of S/Ss will be done by December’2017.
In the 116th PSOC meeting, CGM (O&M) stated that draft modality has been prepared. Order for Mendhasal S/S will be issued as a pilot project.
In the 117th PSOC meeting CGM (O&M) stated that draft project report for Mendhasal S/S has been submitted to BIS. The report will be approved in the meeting to be conducted by them.

In the 118th PSOC meeting, O&M stated that the report has already been submitted. Approval is yet to be received.
In the 119th PSOC meeting O&M stated that approval is yet to be received.
CGM (O&M) may please update the status.
C.11: Status of Disturbance Recorder, Stand alone Event Logger and Time Synchronization equipment.

The status of DR/EL and GPS as updated in previous OCCs is given below. Constituents are also requested to furnish their list of new DR/EL which are not included in the list.

Availability status of Event Logger, Disturbance Recorder & GPS
	Sl.No
	Sub-Station
	Protection & Control system
	Remarks

	
	
	Availability
	Time Synchronization
	

	
	
	EL
	DR
	GPS
	Relay
	DR
	EL
	

	12
	Indravati
	Yes
	Faulty
	No
	No
	No
	No
	ICT feeders using DR & EL available in numerical relays. 400 kV ICT-II feeder is being maintained by PGCIL.

	
	Meramundali
	Defunct
	Yes
	Yes
	Yes
	Yes
	Yes
	

	
	Mendhasal
	Defunct
	Yes
	Yes
	Yes
	Yes
	No
	EL will be restored by March’2015


In the 118th PSOC meeting O&M stated that 400 kV side EL at Mendhasal shall be replaced. Further, Order has been placed for automation of Mendhasal S/S, which is expected to be completed by end of May’2018. Proposal for including DR for Indravati is yet to be sent.
In the 119th PSOC meeting OHPC stated that EL & DR at Indravati is functioning. PSOC advised OHPC to revise the status in the OCC meeting. 
CGM (O&M) / OHPC may please deliberate.
C.12: Implementation of Automatic Demand Management Scheme

OPTCL vide mail dated 24.02.2016 pointed that Hon’ble CERC vide their order dated 31.12.2015 passed in Sou-motu Petition No.- 5/SM/2014 in the matter of non-compliance of Regulation 5.4.2 (d) of IEGC directed all Respondents (SLDCs) for implantation of ADMS in their respective control area. CERC have allowed dead line till 30.06.2016 to the Respondent for implementation of ADMS. Failing which they will be liable for action under Section 142 of the Act.

   *****************************************************************************

The latest status along with proposed logic as follows:
[image: image9.emf]
[image: image10.emf]
In the 116th PSOC meeting, CGM (O&M) stated that since considerable time has already been lapsed SLDC may prepare the EoI without waiting for CPC.
In the 117th PSOC meeting it was decided that SLDC shall process for tendering.

In the 118th PSOC meeting, SLDC stated that the tender specification is expected to be received from CPC by 1st week of March’2018. After receiving the same SLDC will process for tendering
In the 119th PSOC meeting it was decided that SLDC may prepare the financial specification and get approved from Finance wing of OPTCL without depending on CPC, as the matter is very much delayed. 
SLDC may please deliberate.
C.13: Mock Black start exercises in Eastern Region 
The tentative schedule of black-start exercises for F.Y 2018-19 given by OCC is as follows
	Sl.
	Name of Hydro Station
	Schedule
	Tentative Date
	Schedule
	Tentative Date

	
	
	Test-I
	
	Test-II
	

	1
	Upper Kolab
	Last week of May-2018
	
	Last week of January 2019
	

	3
	Rengali
	2nd week of June 2018
	
	Last week of November 2018
	

	4
	U. Indravati
	3rd week of June 2018
	
	2nd week of February 2019
	

	6
	Balimela
	3rd week of October  2018
	
	1st week of March 2019
	

	9
	Burla
	Last week of June 2018
	
	Last week of February 2019
	


OHPC / SLDC may please deliberate.
C.14: Implementation of Islanding scheme:

Efforts should be made to design islanding scheme based on frequency sensing relays so that in case of imminent grid failure, electrical islands canbe formed. These electrical islands can not only help in maintaining supply to essential services but would also help in faster restoration of grid.

No islanding scheme is available in Odisha, Bihar and Sikkim.

OPTCL has submitted the detail plan of IbTPS islanding scheme

OCC advised OPTCL to give a presentation on CPP islanding scheme esxisting in Odisha with the details of extending power capacity to Odisha during emergencies.

OPTCL may deliberate the status

PART-D – Operational Issues
D.1: Non-compliance of drawal schedule by DISCOMs

Non-compliance of drawal schedule messages issued to D
iscoms during the month of March’18:
	Sl. No
	Name of Discom
	No. of message issued
	Over drawal (MU)
	Deviation (%)

	1
	CESU
	0
	-8.185
	1.05

	2
	WESCO
	0
	-41.916
	6.47

	3
	NESCO
	0
	-0.914
	0.19

	4
	SOUTHCO
	0
	0.875
	0.27

	
	Total
	0
	-50.14
	


It is noticed that CESU & WESCO have under drawn while NESCO & SOUTHCO drawl are as per schedule.
SLDC/ Discoms may please deliberate.
D.2: Prolonged outage of transmission elements and tentative revival dates
The tentative revival dates of transmission elements are updated in the last meeting are as follows:

	  Sl. No
	Name of transmission element
	Reason of outage
	Probable date of revival

	1
	220/132 kV, 100 MVA, Auto- 1 at Duburi
	Main tank severely damaged
	April-2018

	2
	220/132kV, 100MVA  Auto-2  at Bhadrak
	Fire hazard on 31.05.2017
	April-2018


CGM (O&M) may update the progress.

D.3: Communication issues 
The status of data communication from CGPs as deliberated in the last meeting is as follows.

	Sl.
	Name of CGP
	Present status

	1
	M/s NINL, Duburi
	M/s NINL has requested for Scheme, BOQ for PLCC/SCADA, which has been forwarded by OPTCL. No action has been taken by NINL so far. 

	3
	M/s Rohit Ferrotech
	PLCC established and inspection by Telecom Engineers completed.  Database has already been prepared by OPTCL.    

	4
	VISA
	New RTU installed. Testing to be done.

	5
	Paradeep
	Already integrated.

	6
	IRE, Chatrapur
	Data communication system yet to be established by the Plant


In the 117th PSOC meeting, Members opined that GCC should file a case soon against NINL & IRE before the OERC.

In the 118th PSOC meeting, GCC stated that a case will be filed against NINL, IRE & Rohit Ferrotech for non-compliance of the data communication provision.

In the 119th PSOC meeting it was decided that GCC shall file a case against the defaulting CGP/ Consumers before the OERC. SLDC stated that RLDC is not getting the GMR-Meramundali line flow data. CGM (Telecom) has assured to investigate the issue.
GMR Issue
	GMR on line data is available at SLDC but not available directly to ERLDC. GMR entrusted the work on Powergrid.


CGM (Telecom) / GCC / GMR / RT&C may deliberate the status.
D.4: Implementation of Automatic Meter Reading for OPTCL-Discom interface points.

In the 116th PSOC meeting, IT stated that out of 840 nos of meters integrated, around data from 750 nos of meters will be received each month. Data from the remaining 90 meters are to be collected manually.

In the 117th PSOC meeting IT stated that out of 840 nos of meters integrated, data from 717 nos of meters have been extracted for the month of December’17. Data could not be collected from 63 Nos of meters, which were replaced, as the information was received by IT one day before. CGM (O&M) may instruct Secure meters Ltd to inform the replacement of meters to IT immediately. 

In the 118th PSOC meeting, IT stated that out of 840 nos. of meters integrated, data from 754 nos. of meters have been extracted for the month of January’18. The extracted data will be compared with the M cubed meter reading. If found satisfactory, the project will be made go live.
In the 119th PSOC meeting IT stated that Parameters of 16 Nos meters are showing wrong. DLMS data for the newly installed Secure meters are not coming. It was decided that O&M shall discuss the matter with Secure meters to resolve the issue.
O&M may deliberate.
D.5: Web based drawal / generation scheduling.

In the 111th PSOC meeting it was decided that from 1st August 2017 the schedule submitted through web portal will be considered. The web based schedule will be implemented for TTPS and Ib TPS from 1st September’2017. 
At present all State thermal generating stations including IPPs & CGPs are furnishing their schedule through web portal.

The following fetchers need to be incorporated in the software: 

1. Provisions for acceptance of backing down schedule for past block.

2. Provision for automatic extraction of Power Exchange schedule from the worksheet for incorporation in the schedule of respective Generator / CGP.

3. Navigation between different web pages within the portal

4. Report generation in excel format with down loading provision.
SLDC / IT may update. 

D.6: Software for Deviation charge billing.

Hon’ble OERC may notify “Intra State Deviation settlement and related matters” Regulation at any time. For implementation of the regulation, required software for Deviation Charge billing need to be developed and tested. CGM (IT) may take necessary steps for development of the software.

As decided a committee has been constituted for development of the software in house. The work is in progress. 
In the 117th PSOC meeting IT stated that the software will be ready within a week time.
In the 119th PSOC meetring IT stated that modification of program is under process.

CGM (IT) / SLDC may please deliberate.
D.7.DISCOM Issues

CESU

1. Connectivity of Ransingpur sub-station with Argul for stand by supply for Ransinghpur (connected to Chandaka S/S) from Atri Grid S/S in case of power supply fails from Chandaka S/s due to any fault. As AIIMs is availing power supply from Ransingpur S/S.
2. To provide soft copy of Deviation bill to CESU ABT cell in each week.
3. Instant revision of CESU drawal schedule due to irregular drawl of Bhushan Steel Ltd.
4. The discrepancy in BSP bill intimated by CESU is not being considered by GRIDCO.
CESU may deliberate
WESCO
1. Power import by M/s Jyoti Solar and M/S GEDCOL solar is not being deducted from WESCO BSP bill.

2. Time synchronization of main/check meter should have been done with GMT especially for EHT consumers.
WESCO may deliberate
D.8: Rectification / Replacement of Defective Meters at different interface points.

A list of defective meters indicating the defects has been placed in the 116th PSOC meeting wherein OPTCL was requested to take necessary action for checking CT / PT and early replacement of these meters wherever required. O&M proposed to convene a meeting to discuss the issue. The meeting is yet to be convened.

In the 119th PSOC meeting O&M stated that a meeting will be convened with Secure Meters and SLDC to discuss the issue.

O&M may deliberate the status
PART E: OPERATIONAL PLANNING
E.1:  Commissioning status of new Transmission elements. 
The status of commissioning of new transmission elements deliberated in the meeting is as follows:
	   Sl. No
	Transmission element details
	Present Status

	1
	Commissioning of 220 kV Jayanagar-Jeypore 2nd DC line 
	Work has already been started. Expected to be completed by June’18.

	2
	Commissioning of 400 kV Meramundali-Mendhasal 2nd ckt.
	Line is ready and shall be charged after commissioning of 3rd ICT at Mendhasal. Expected by April’2018.

	3
	400/220 kV, 315 MVA 3rd ICT at Mendhasal S/S
	March’18

	4
	400/220 kV, 2x315 MVA Lapanga S/S
	June’18

	5
	220/33 kV, 2x20 MVA Baliguda S/S
	December’18

	6
	220/33 kV, 2x20 MVA Kalimela S/S
	December’18

	7
	220/33 kV, 2x20 MVA Kasipur S/S
	April’18

	8
	220/33 kV, 2x40 MVA Keonjhar GIS S/S
	May’18

	9
	220/33 kV, 2x20 MVA Narasinghpur S/S
	June’18

	10
	220/132 /33 kV, 2x100 MVA Aska S/S
	December’18

	11
	220/132/33 kV, Bargarh (New) S/S (320 MVA)
	Charged during March’18

	12
	220/132/33 kV, Goda Chhak S/S (320 MVA)
	December’18

	13
	220/132/33 kV Jayapatana S/S(320 MVA)
	December’18

	14
	220/132 kV Pratapsasan S/S(320 MVA)
	March’19

	15
	220/132 kV Kesinga S/S (320 MVA)
	June’18

	16
	400 KV IB - Lapanga D/C (SEL, Bhushan & L&T)
	June’18

	17
	132/33 kV Ghense S/S
	Charged during April’18

	18
	132/33 kV Dhenkikote S/S 
	Charged on 24.02.2018

	19
	132/33 kV Betanati S/S
	March’18

	20
	132/33 kV Kantabanji S/S
	Charged on 28.02.18 

	21
	132/33 kV R.Udyagiri S/S
	July’18

	22
	132/33 kV Chikiti S/S
	August’18

	23
	132/33 kV Athagarh S/S
	April’18


The Discoms were requested to take necessary action for availing power supply from those S/Ss and prepare their action plan for takeoff arrangement. WESCO may make necessary takeoff arrangement from the newly commissioned 220/132/33 kV Bargarh S/S.

CGM (Construction) / DISCOMs may deliberate the status.
E.2: Installation of ABT compliance Energy Meter at Ib TPS feeders & Generators / Furnishing of DC
SLDC shall prepare the schedule and Energy Accounting in respect of IbTPS. It is learnt that the Main meter installed by IbTPS feeders is recording 30 minutes reading while Check meter provided by OPTCL is recording 15 minutes reading. Unless ABT compliance Main and Check energy meters installed in IbTPS feeders & Generators, the energy accounting and PAFM cannot be computed. It is requested OPTCL / IbTPS to provide ABT compliance Main and Check meters in all the 220 kV IbTPS feeders & Generators.

In the 117th PSOC meeting, it was decided that CGM (O&M), OPTCL may direct the E & MR Division, Burla to take up the work.

In the 118th PSOC meeting Sr. G.M, EHT (O&M) Zone-II assured to install the meters soon.

In the 119th PSOC meeting CGM (O&M) stated that Ib TPS may deposit the required amount to release meters (for check meter).

OPTCL / IB TPS may deliberate the status.    
E.3: Compliance of CEA Regulations for Grid Connectivity of Renewable Energy Sources.
As per CEA (Technical Standards for connectivity to Grid) Regulations, 2007, dated 21st February 2007, the pertinent clauses 6 (iii) & 6 (iv) (b) of general Connectivity Conditions shall be applicable to all the Generating Projects including the renewable, which are getting connected to the Grid at voltage level of 33kV & above. Subsequently, CEA have notified the CEA (Technical Standards for Connectivity of the Distributed Generation Resources) Regulations 2013 dated 30.09.2013. These Regulations are applicable for “Distributed Generation Resources”, which means A Generating Station feeding electricity into the System at voltage level below 33kV. Needless to mention that these Regulations also cover the renewable projects connected to the Distribution Licensee’s System at voltage level of below 33kV. The letter received from CEA is annexed herewith. 

SLDC has already forwarded the Regulations & a letter received from DoE, Govt. of Odisha to the Distribution Licensees.  

A meeting was convened on 29.07.2017 by Director (Commercial) between all RE Generators, SLDC, GRIDCO, DISCOMS & Telecom to decide the strategy. It was decided that the RE generators shall suggest the mechanism to be adopted for real time data communication to SLDC & Telecom to examine the same. Another meeting was proposed to be convened in the month of August’17 to finalize the mechanism of data communication. In the 113th PSOC meeting, it was decided that GRIDCO will take follow up action with all the RE generators to provide real time generation data to SLDC. ERLDC has reminded again to intimate the status.   

A meeting has been convened by Gridco in this regard with the RE generators, OPTCL, Telecom & SLDC. In the meeting, two nos of agencies presented their data acquisition logic from the RE sources. It was decided that each agency will take up a pilot project for data communication from one RE source to SLDC. On completion of the above project next course of application shall be decided.
In the 116th PSOC meeting, CGM (Telecom) stated that the solar projects need to pay the SCADA integration charges for display of the data through SCADA.
In the 117th PSOC meeting CGM (Telecom) stated that for pilot project the integration charges may not be required. The Agencies may be asked to proceed with their project.

In the 118th PSOC meeting GRIDCO state that MoM has already been made for 2 Nos. pilot projects and work will be started soon.
In the 119th PSOC meeting it was decided that SLDC shall write a letter to Gridco to intimate the status for deliberations in the OCC. Gridco may explore for early completion of the pilot project.

Telecom / GRIDCO may deliberate the status.
E.4: Major Events in the month of March’18
16.03.18: 220/33 kV, 2nd 40 MVA Tfr at Malkangiri charged.
21.03.18: 220 kV Joda-Tata Steel bay and line charged at Joda end.

21.03.18: 220 kV Bus of Bargarh (New) 220/132 kV S/S charged at 20:11 Hrs. 220/132 kV, 100 MVA Auto charged at 20:18 Hrs.

E.5: Important Grid Incidences during the month of March’18.
On 13.03.2018 at 19:30 hrs  400 kV Meramundali-Vedanta Ckt-I tripped  on both sides (at Meramundali - on dist-27.4 km, ‘B’ ph to E/F, IB-35.46 kA and at Vedanta -Zone-I, dist-221.9 km, ‘B’ ph to E/F, 1.6 kA).  400/220 kV, 315 MVA ICT-I &II at Meramundali tripped on both sides. (On 400 kV side on- O/C )
E.6: Outage of major transmission Elements during the month of March’18. (above 10 hrs).
	Sl No
	Transmission lines
	Tripping Dt/time
	Restoration
Dt/time
	Reason

	1
	400 kV Meramundali-Vedanta Ckt-I
	13.03.18

19:30
	14.03.18

17:51
	‘B’ ph LA burst at Meramundali.

	2 
	132 kV OCL-Salipur Ckt
	21.03.18

05:57
	21.03.18

17:49
	‘R’ ph  insulator damaged at Loc. No-79.


C.G.M. (O&M) may please deliberate.

E.7:  Review of Outage Program of State Generators / Transmission elements for the month of May’18:
Tentative Outage programme for State Generators for the month of May’2018 are as follows:
	Sl.
	Station
	Unit
	Period
	Remarks

	1
	Burla
	# 1
# 5

# 6
	14.03.18 to 20.05.18
25.10.16 to continue

16.10.15 to continue
	Shaft seal leakage
Under R,M & U

Under R, M & U

	2
	Chiplima
	# 3
# 1
	15.10.15 to continue
02.05.18 to 26.05.18
	Under R,M & U
Annual Maintenance

	3
	Balimela
	# 1

# 2
	05.08.16 to continue

20.11.17 to continue
	Under R,M & U

Programming for R&M

	4
	Upper Kolab
	# 2
	28.05.17 to continue
	Upstream leakage & intake gate Problem


OHPC / SLDC may deliberate. 
E.8: Generation Program for the month of May’18.
Generation schedule for the month of May’18 furnished by OHPC are given below. 

	Name of Hydro Gen. Station               
	Generation Program (MW)
	Reservoir Level as on 01.04.17
	Reservoir Level as on 01.04.18
	MDDL
	High Flood    Reservoir Level

	
	Apr’18
(1st fortnight)
	Apr’18
(2nd fortnight)
	
	
	
	

	HPS-I, Burla
	30
	30
	617.45 ft 
	 616.52 ft
	590 ft.
	630 ft.

	HPS-II, Chiplima
	20
	20
	-
	-
	-
	-

	Balimela
	220
	220
	1485.90 ft 
	1456.50 ft
	1440 ft.
	1516 ft.

	Rengali
	120
	120
	121.04 mtr

	119.66 mtr
	109.72mtr 
	123.5 mtr.

	U.Kolab
	60
	60
	853.32 mtr mt
	850.72 mtr
	844 mtr 
	858 mtr.

	U. Indravati
	250
	250
	635.00 mtr
	632.61 mrt mt
	625mtr 
	642 mtr

	MKD (O/D)
	30
	30
	2722.90 ft 
	2736.30 ft
	2685 ft.
	2750 ft.

	TOTAL
	730
	730
	
	
	
	


Generation schedule may change depending on inflow & availability of machine.

OHPC / SLDC may deliberate & Members may discuss. 
E.9: Anticipated power generation and demand for the month of May’2018.
	Sl. No
	Discom
	Average
	Peak

	1
	CESU
	1100
	1450

	2
	WESCO
	1100
	1450

	3
	NESCO
	800
	1000

	4
	SOUTHCO
	450
	550

	6
	Total Discom
	3450
	4350

	
	System Loss & others
	170
	220

	
	Total Demand
	3570
	4370

	Availability
	
	

	1
	Hydro
	730  
	1350

	2
	State Thermal
	770
	770

	3
	IPP, small hydro &RE
	650
	650

	4
	ISGS share (including OA)
	1120
	1300

	5
	CGP support (OA)
	300
	300

	6
	Total availability
	3570
	4370

	7
	Surplus / Deficit
	0
	0


Members may discuss.
PART F: OTHER ISSUES
F.1:  Date and Venue of the next (121th) PSOC meeting.
PAGE  

Sheet1

						Month		Thermal (TTPS+IB)		OHPC		CGP Support		IPP Support		Renewable		ISGS		Total

										& MKD

						Apr’17		514.91		581.71		323.53		349.53		17.70		705.86		2493.24

						May’17		543.19		647.85		296.06		212.84		10.45		823.85		2534.24

						June’17		548.07		610.00		358.88		203.70		10.17		537.95		2268.77

						July’17		554.18		688.13		190.09		140.71		10.46		853.89		2437.46

						Aug’17		442.30		746.49		281.20		167.14		10.06		853.01		2500.20

						Sept’17		363.01		731.72		189.82		173.94		9.45		1091.74		2559.68

						Oct’17		453.38		572.67		155.32		152.27		35.85		1311.67		2681.16

						Nov’17		433.21		263.48		209.28		79.27		9.31		1121.06		2115.61

						Dec’17		554.44		189.28		223.23		122.73		10.44		1061.73		2161.85

						Jan’18		545.32		236.10		360.28		301.68		9.93		858.09		2311.40

						Feb’18		515.05		270.16		247.77		156.54		9.34		994.90		2193.76

						Mar’18		571.04		373.57		318.67		151.62		10.31		1169.34		2594.55

						Total		6038.10		5911.16		3154.13		2211.97		153.47		11383.09		28851.92





Sheet2





Sheet3






Sheet1

						Month		Total Generatuion				Odisha Drawal				AP Drawal

								MU		MW		MU		MW		MU		MW

						Apr’17		65.96		91.61		32.32		44.89		30.95		42.99

						May’17		65.53		88.08		29.08		39.08		33.83		45.47

						June’17		45.68		63.44		19.51		27.10		24.11		33.48

						July’17		33.21		44.64		15.06		20.24		16.23		21.82

						Aug’17		51.80		69.62		24.45		32.86		25.22		33.90

						Sept’17		39.02		54.19		18.14		25.19		19.07		26.49

						Oct’17		34.35		46.17		16.51		22.19		16.16		21.73

						Nov’17		25.18		34.97		8.70		12.08		14.89		20.67

						Dec’17		38.40		51.61		18.61		25.02		17.89		24.05

						Jan’18		38.90		52.29		19.62		26.37		17.40		23.38

						Feb’18		34.55		51.41		17.43		25.94		15.47		23.02

						Mar’18		41.53		55.82		20.30		27.29		19.34		26.00

						Total		514.10		58.65		239.72		27.35		250.56		28.58







Sheet2





Sheet3






